## Public Non-CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901760 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD April 6, 2009 that BPA would no longer function as CKPD's TOP on and the notice was effective immediately. As a result of BPA's decision, CKPD had to register as a TOP and report itself as noncompliant with this NERC Standard. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of its TOP registration and the time of its registration, CKPD was unable to provide adequate and reliable telecommunications facilities for the exchange of interconnection and operating information, in violation of this Standard. | COM-001-1 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to provide adequate and reliable telecommunications facilities for the exchange of interconnection and operating information, the interim risk to the BPS was abated because the basic lines of communications (voice and data) with the Reliability Coordinator and BPA were still in place while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD identified telecommunication resources used to communicate with its TOPs and BA (BPA). CKPD communicates with the Reliability Coordinator (RC) through BPA. CKPD provided evidence of its completion in a document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901761 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ( "BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP on and the notice was effective immediately. As a result of BPA's decision, CKPD had to register as a TOP and report itself as noncompliant with this Standard. In its Self-Report, CKPD stated that the requirements of the Standard were new and unexpected obligations for CKPD as a result of its TOP registration and the time of its registration, CKPD did not manage, alarm, test and/or actively monitor vital telecommunications facilities, in violation of this Standard. | COM-001-1 | R2 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to manage, alarm, test and/or actively monitor vital telecommunications facilities, the interim risk to the BPS was abated because the basic lines of communications (voice and data) with the RC and BPA were still in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD developed procedures and guidance for alarming and testing its vital communications in its document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901762 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of its TOP registration. WECC determined that at the time of its registration, CKPD failed to have written operating instructions and procedures to enable its continued operation during the loss of telecommunication facilities, in violation of this Standard. | COM-001-1 | R5 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to have written procedures in place to operate without such communication facilities, the risk to the BPS was abated because the basic lines of communications (voice and data) were in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD developed a written plan to address system operation with loss of vital communications in its document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901763 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. As a result of BPA's decision, at the time of its registration, CKPD failed to have communications (voice and data links) with the appropriate RCs, BAs and TOPs, in violation of this Standard. | COM-002-2 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to have communications (voice and data links) with the appropriate RCs, BAs and TOPs, the risk to the BPS was abated because the basic lines of communications (voice and data) with the RC and BPA were still in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided documentation of its voice and data links with its TOP and BA, set forth in a document titled Clark Public Utilities Telecommunications Facilities Adequacy and Reliability, dated July 31, 2009. | 2009-09-18 | 2009-12-15 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901790 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to develop, maintain, and implement a set of plans to mitigate operating emergencies, load shedding and system restoration, in violation of this Standard. | EOP-001-0 | R3 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. In addition, all of the requirements of this Standard were elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements between the two entities would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the CKPD Emergency Operator Plans and Operator Controlled Manual Load Shedding Plan, dated January 26, 2010, that addressed insufficient generating capacity (at a level appropriate to a non-BA), for mitigating operating emergencies on the transmission system and for load shedding. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901791 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. At the time of its registration, CKPD had failed to have emergency plans to enable it to mitigate operating emergencies, including communications protocols and a list of controlling actions to resolve the emergency, in violation of this standard. | EOP-001-0 | R4 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided documentation of emergency plans that will enable it to mitigate operating emergencies. The CKPD Emergency Operator Plans and Operator Controlled Manual Load Shedding Plan, dated January 26, 2010, that addresses communications protocols, load reduction, tasks to be coordinated, and staffing levels. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901792 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | EOP-001-0 | R5 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the CKPD Emergency Operator Plans and Operator Manual Load Shedding Plan, dated January 26, 2010, that includes an “Additional Emergency Condition Considerations” section and also includes Attachment 1-EOP-001-0. The plan adopted the elements of Attachment 1 as a list of additional elements to be considered as potential responses during any emergency condition. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901793 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to review and update its emergency plan, and to provide a copy of its updated emergency plans to its RC and neighboring TOPs and BAs, in violation of this Standard. | EOP-001-0 | R6 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of the emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions, incorporate them into its own plan, and share the results with appropriate BAs and TOPs. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its Emergency Operator Plans (1/26/10), Operator Manual Load Shedding Plan (1/26/10), and System Restoration Plan(1/1/10). These emergency plans include provisions for annual reviews and updates, if appropriate. CKPD stated it will annually review and update each emergency plan and provide a copy of its updated emergency plans to its RC, TOP and BA. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901794 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate its emergency plans with neighboring TOPs and BAs as appropriate, in violation of this Standard. | EOP-001-0 | R7 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of the emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that plans developed and coordinated by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions, incorporate them into its own plan, and coordinate the results with appropriate BAs and TOPs. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its Emergency Operator Plans and Operator Manual Load Shedding Plan, dated January 26, 2010, to show that it has coordinated with its neighboring BAs and TOPs. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901684 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, in violation of this Standard. | EOP-005-1 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WE#CC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901685 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to develop restoration plans with a priority of restoring the integrity of the Interconnection, in violation of this Standard. | EOP-005-1 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Also, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center and CKPD could call on BPA for emergency response and system restoration in the interim if an emergency event occurred. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. The restoration plan includes a priority for restoring the integrity of the Interconnection. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901686 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate its restoration plans with the Generator Owners and Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities, in violation of this Standard. | EOP-005-1 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of this Standard and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. The restoration plan includes a procedure for coordination with BPA and PacifiCorp West. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901687 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to periodically test its telecommunication facilities needed to implement the restoration plan, in violation of this Standard. | EOP-005-1 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. In addition, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. CKPD confirmed that its Plan requires that the telecommunication facilities are tested annually, and that CKPD regularly tests these telecommunications facilities on a monthly basis. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901688 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to train its operating personnel in the implementation of the restoration plan, in violation of this Standard. | EOP-005-1 | R6 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC copies of 1) the System Restoration Plan, dated January 1, 2010, 2) the log sheet describing the March 27, 2010 test of the Plan, and 3) the training log sheet showing that all of CKPD’s Service Dispatchers had received initial training for the Plan. | 2010-03-27 | 2010-04-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901689 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to verify the restoration procedure by actual testing or by simulation, in violation of this Standard. | EOP-005-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC a copy of its System Restoration Plan and evidence of testing dated March 27, 2010, to assure that the plan could be followed. The test included contacting neighboring entities. CKPD's restoration plan calls for CKPD to follow direction from BPA. | 2010-03-27 | 2010-04-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901683 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to have a plan to continue reliability operations in the event its control center became inoperable, in violation of this Standard. | EOP-008-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim in the event of control center inoperability. Further, restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-25 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD completed its Loss of Control Center Functionality Plan on January 1, 2010. The plan states that CKPD will deploy personnel to critical facilities and will relocate its dispatchers to one of three locations and establish communication via cell phones with remote substations. On March 20, 2010 CKPD tested its plan and on March 23, 2010 trained its dispatchers on the implementation of its plan. | 2010-03-25 | 2010-04-01 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901798 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of the registration, CKPD had failed to provide its operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the BPS, in violation of this Standard. | PER-001-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD’s documentation failed to provide its operating personnel with the responsibility and authority to take actions, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration that would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. CKPD mitigated this violation in four months, as it was necessary to renegotiate union contracts in order to get the appropriate references to NERC requirements in the dispatch personnel job descriptions. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD submitted to WECC documentation of its System Operations Manual and job descriptions (as of 9/18/2009) that it provides operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the bulk electric system. | 2009-09-18 | 2010-01-22 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901745 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of the registration, CKPD was not staffed with adequately trained operating personnel, in violation of this Standard. | PER-002-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD's operations staff was not fully trained at the time it was registered on May 8, 2009, CKPD had begun its training program on April 14, 2009, to abate the risk to reliability. At the time of its registration as a TOP, CKPD had already started training its operators. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC its Clark Public Utilities System Operator Training Program, which served as a proof of training for CKPD's system operators. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on 4/14/2009 before the standard was applicable to CKPD. CKPD completed the training of its six operators on 9/21/2009. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901746 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD did not have a training program with training objectives and did not document initial and continuing training that addressed competencies and knowledge. The training staff was not identified and their competencies in both knowledge of system operations and instructional capabilities was not identified, in violation of this Standard. | PER-002-0 | R3 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD's existing program did not meet the criteria of this Standard, CKPD did have a training program in place and commenced training prior to its registration date. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC its Clark Public Utilities System Operator Training Program, which met the requirements of R3. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on 4/14/2009, before the standard was applicable to CKPD. CKPD completed the training of its six operators on 9/21/2009. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901747 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, in violation of this Standard. | PER-002-0 | R4 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD did not provide its operating personnel with the required drills and simulations to satisfy the requirements of the Standard, CKPD had a training program for operators that included simulations of system emergencies. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided WECC with its System Operator Training Program, dated September 16, 2009, to show that it provides its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on April 14, 2009, before the standard was applicable to CKPD. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901797 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to staff all operating positions that had the primary responsibility, either directly or through communications with others, with personnel that were NERC-certified for the applicable functions for the real-time operation of the interconnected BPS, and positions directly responsible for complying with NERC standards, in violation of this Standard. | PER-003-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD lacked NERC-certified operating personnel at the time of its registration as a TOP, its personnel did have experience and training to operate the CKPD system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-28 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided an email verifying completion of NERC Certification for all applicable positions as of 1/28/2010. | 2010-01-28 | 2010-02-26 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901653 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to have documentation showing that its system operators had the responsibility and clear decision-making authority to take whatever actions were necessary to protect the BPS, in violation of this Standard. | TOP-001-1 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD lacks the appropriate documentation of authority to alleviate operating emergencies, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration that would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD submitted to WECC an operating procedure on 9/18/2009 titled CKPD - Reliability Responsibilities and Authorities (7/31/09) that states the operator has the authority and responsibility to take action, up to and including dropping load to respond to emergency conditions. | 2009-09-18 | 2009-11-04 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901692 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to: maintain a set of current plans designed to evaluate options, set procedures for reliable operation through a reasonable future time period and be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained, in violation of this Standard. | TOP-002-2 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Development of plans to evaluate options and set procedures for reliable operation through a reasonable future time period are long-term planning activities that are normally performed on an annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BPS and CKPD system reliability during the short period of time until CKPD's planning function became operational. Further, CKPD's violation was primarily documentation, i.e., CKPD's existing documentation needed to be organized, and planning guidelines for expected normal operations needed to be extended into the future. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan through 2010. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901693 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to ensure its operating personnel participated in the system planning and design study processes, so that these studies contained the operating personnel perspective and system operating personnel were aware of the planning purpose, in violation of this Standard. | TOP-002-2 | R2 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning and design study functions are long-term activities that are normally performed on an annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BPS and CKPD system reliability during the short period of time until CKPD's planning function became operational and incorporated the experience of its operating personnel. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan through 2010. Operating personnel participated in the implementation of this plan. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901695 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate (where confidentiality agreements allowed) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | TOP-002-2 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Current-day, next-day, and seasonal planning are operations planning activities that are normally performed on a long-term or annual basis. Thus, the coordination for the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place to ensure that normal Interconnection operations would proceed in an orderly and consistent manner during the short period of time until CKPD's planning function became operational. The larger encompassing BA, which previously coordinated these activities, would be fully aware of CKPD planning and operations. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan, and an email showing proof of coordination with BPA and PacifiCorp West. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901696 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | TOP-002-2 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns is an operational planning activity that is normally performed on a long-term or annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BES and CKPD system reliability during the short period of time until CKPD's planning function became operational. Further, CKPD's violation was primarily documentation, i.e., CKPD's existing documentation needed to be organized and expanded to cover additional requirements. Also, CKPD has no interchange schedules. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD included information on expected demand (LSE) and expected generator operations (GOP). A copy of the results were provided to BPA as the BA and the Transmission Service Provider for CKPD. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901697 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | TOP-002-2 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning to meet the conditions listed in this requirement are operational planning activities that are normally performed on a long-term or annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BES and CKPD system reliability during the short period of time until CKPD's planning function became operational and the perspective of its operating personnel incorporated. Further, CKPD's violation was primarily documentation, i.e. CKPD's existing documentation needed to be better organized to demonstrate compliance with reliability requirements. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 study results showing the scheduled system configuration, generation dispatch, and demand patterns (CKPD is not a BA and has no interchange schedules). CKPD indicated that this scheduled system configuration is expected to be used during seasonal normal conditions, seasonal extreme conditions and seasonal N-1 conditions. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC201002022 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to monitor system frequency, in violation of this Standard. | TOP-006-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. CKPD is a small system composed of 69 kV and 115 kV lines, completely surrounded by BPA. BPA indicated in a letter dated April 6, 2009 that issues affecting CKPD's system would have minimal impact on the reliability of the BPA system. WECC determined that due to its relatively small impact with respect to the more robust surrounding system, the fact that it is not a BA, and the fact that it has no interchange schedules, failure to monitor system frequency would have little effect on its operations or on the reliability of the interconnected system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-04-28 | 2009-07-28 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided evidence to WECC that it was monitoring system frequency, and that system frequency was added to the applicable display screens in the dispatch center. | 2009-07-28 | 2010-09-15 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901779 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had not specified criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1, in violation of this Standard. | VAR-001-1 | R3 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to specify a criteria for exempting generators from having to maintain the voltage or reactive schedule on the CKPD transmission system, CKPD had only one generator connected to its system, and that generator was not exempt. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documentation on 1/29/2010: Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and Appendix A - applicable and exempt generators. CKPD maintains a list of exempt generators, and has procedures to notify owners and operators of their status. CKPD has no exempt generators connected to the transmission system. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901780 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had failed to specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. CKPD did not provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage), in violation of this Standard. Also, the current voltage schedule was established by BPA, not CKPD. | VAR-001-1 | R4 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to specify a voltage or reactive power schedule for its River Road generating facility, BPA (the surrounding BA and former TOP for CKPD's facilities) did establish a voltage schedule that is telemetered to the one generator connected to CKPD's system, River Road, in real-time. BPA continued to require the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided evidence on 1/29/2010 that it specified a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. CKPD provided the voltage or Reactive Power schedule to the associated Generator Operator and directed the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901781 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD did not know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers (PSS), in violation of this Standard. The status was known by BPA, not CKPD. | VAR-001-1 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to know the status of the AVR and PSS at the River Road generating facility, BPA did establish a voltage schedule that is telemetered to River Road in real-time. The voltage at River Road and the status of the AVR and PSS are telemetered back to BPA. The issue with this violation is not that system operators did not know the status of the River Road AVR and PSS, but rather that the status must be known by the current Transmission Operator, CKPD. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC on 1/29/2010 its Voltage and Reactive Power Monitoring and Controlling Procedures, dated 1/2/2010. This evidence showed that CKPD knows the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. Under the Procedure, if CKPD is notified of the loss of an automatic voltage regulator control, CKPD will direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901782 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, in violation of this Standard. However, those functions were being performed by BPA. | VAR-001-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD was not able to independently direct the operation of the AVR and PSS at the River Road generating facility, BPA had established a voltage schedule that is telemetered to River Road in real-time. The voltage at River Road and the status of the AVR and PSS are telemetered back to BPA. The interconnection voltage of the River Road generating facility is at the discretion of BPA, which monitors and regulates voltage in the area. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documents on 1/29/2010: the Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and a letter from BPA to CKPD, dated June 25, 2009. The evidence showed that CKPD will operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901783 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had failed to operate or direct the operation of capacitive and inductive reactive resources within its area – including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. Those functions were being performed by BPA. | VAR-001-1 | R8 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD was not able to operate or direct the operation of capacitive and inductive reactive resources within its area to maintain system and Interconnection voltages within established limits, BPA controls to the voltages contained in its Voltage Schedules document at the interconnections with CKPD. BPA maintains the reactive flow at these stations by maintaining the voltage schedule at these stations, thus maintaining system and Interconnection voltages within established limits. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documents on 1/29/2010: the Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and a letter from BPA to CKPD, dated 6/25/2009. The evidence showed that CKPD will operate or direct the operation of capacitive and inductive reactive resources within its area to maintain system and Interconnection voltages within established limits. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
Western Electricity Coordinating Council (WECC) | Navopache Electric Cooperative, Inc. (NPEC) | NCR05260 | WECC201002041 | Settlement Agreement | On June 17, 2010, WECC conducted an off-site Compliance Audit of NPEC, as a Distribution Provider, and examined NPEC’s compliance with PRC-005-1 from June 17, 2007 to June 17, 2010. WECC determined that NPEC owns and operates a transmission Protection System that affects the reliability of the bulk power system (BPS). WECC concluded that in addition to its distribution systems, NPEC also owns and operates the Coronado Substation in St. John, Arizona, which includes a 500 kV-69 kV transformer and associated over-current and differential relaying and high-side protection systems. WECC determined that a potential failure of the high-side protection systems would cause an outage of the Sugarloaf 500 kV line and impact the BPS. WECC examined NPEC’s Protection System maintenance and testing program and concluded that it did not include maintenance and testing intervals for its voltage and current sensing devices, and that its maintenance and testing program failed to address DC circuitry, in violation of PRC-005-1 R1.1. | PRC-005-1 | R1 | High | Severe | WECC determined that the violations posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because NPEC and the Salt River Project (SRP) have duplicative protective systems. SRP’s system has its own breakers, designed to prevent an outage beyond the 500 kV line. SRP’s breakers reduced the reliability risk to the BPS posed by a potential failure of NPEC’s transmission protection devices. | 2007-06-18 | 2011-02-28 | $40,000 (for WECC201002041, WECC201002042) | Compliance Audit | NPEC Revised its maintenance and testing program to include voltage and current sensing devices and DC circuitry. | 2011-02-28 | 2011-06-13 | Agrees and Stipulates to the Facts | A Settlement Agreement covering violations of PRC -005-1 R1 and R2 and PRC-008-0 R1 and R2 for NPEC (NOC-514) was approved by the BOTCC on May 14, 2010 and filed with FERC under NP10-160-000 on September 13, 2010. October 14, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although this is NPEC’s second violation, WECC Enforcement determined that a full penalty aggravation was not warranted with respect to R1. In the course of verifying completion of NPEC’s Mitigation Plan for the prior violation of PRC -005-1 R1, WECC erred in determining that NPEC’s Maintenance and Testing Program contained all of the elements required by the Standard. In fact, the Maintenance and Testing Program was still deficient because it did not include all Protection System equipment or maintenance and testing intervals, as required by R1. WECC acknowledged the error and that it could have provided a more rigorous review of the Maintenance and Testing Program when verifying completion of the Mitigation Plan related to the first violation of PRC-005-1 R1. Further, WECC considered NPEC’s repeat violation of PRC -005-1 R2 as an aggravating factor in its final penalty determination. WECC did not review NPEC’s Internal Compliance Program and did not give NPEC a mitigating credit for having a Compliance Program.
Western Electricity Coordinating Council (WECC) | Navopache Electric Cooperative, Inc. (NPEC) | NCR05260 | WECC201002042 | Settlement Agreement | On June 17, 2010, WECC conducted an off-site Compliance Audit of NPEC, as a Distribution Provider, and examined NPEC’s compliance with PRC-005-1 from June 17, 2007 to June 17, 2010. WECC determined that NPEC owns and operates a transmission Protection System that affects the reliability of the bulk power system (BPS). WECC concluded that in addition to its distribution systems, NPEC also owns and operates the Coronado Substation in St. John, Arizona, which includes a 500 kV-69 kV transformer and associated over-current and differential relaying and high-side protection systems. WECC determined that a potential failure of the high-side protection systems would cause an outage of the Sugarloaf 500 kV line and impact the BPS. On the basis of the Compliance Audit and subsequent requests for information, WECC also concluded that NPEC could not provide evidence of testing of its DC circuitry and voltage/current sensing devices, and evidence of the date these devices were last maintained and tested. Therefore, WECC determined that NPEC also violated PRC-005-1 R2. | PRC-005-1 | R2 | High | Severe | WECC determined that the violations posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because NPEC and the Salt River Project (SRP) have duplicative protective systems. SRP’s system has its own breakers, designed to prevent an outage beyond the 500 kV line. SRP’s breakers reduced the reliability risk to the BPS posed by a potential failure of NPEC’s transmission protection devices. | 2007-06-18 | 2011-07-18 | $40,000 (for WECC201002041, WECC201002042) | Compliance Audit | NPEC completed the required maintenance and testing and committed to have regular maintenance schedules as defined in its Protection System maintenance and testing program. | 2011-07-18 | 2011-11-16 | Agrees and Stipulates to the Facts | A Settlement Agreement covering violations of PRC -005-1 R1 and R2 and PRC-008-0 R1 and R2 for NPEC (NOC-514) was approved by the BOTCC on May 14, 2010 and filed with FERC under NP10-160-000 on September 13, 2010. October 14, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although this is NPEC’s second violation, WECC Enforcement determined that a full penalty aggravation was not warranted with respect to R1. In the course of verifying completion of NPEC’s Mitigation Plan for the prior violation of PRC -005-1 R1, WECC erred in determining that NPEC’s Maintenance and Testing Program contained all of the elements required by the Standard. In fact, the Maintenance and Testing Program was still deficient because it did not include all Protection System equipment or maintenance and testing intervals, as required by R1. WECC acknowledged the error and that it could have provided a more rigorous review of the Maintenance and Testing Program when verifying completion of the Mitigation Plan related to the first violation of PRC-005-1 R1. Further, WECC considered NPEC’s repeat violation of PRC -005-1 R2 as an aggravating factor in its final penalty determination. WECC did not review NPEC’s Internal Compliance Program and did not give NPEC a mitigating credit for having a Compliance Program.
Western Electricity Coordinating Council (WECC) | Nevada Power Company (NEVP) | NCR05261 | WECC201102422 | Notice of Confirmed Violation | From March 14, 2011 to March 25, 2011, WECC conducted an on-site compliance audit of NEVP (Audit). During and prior to the Audit, the Audit Team reviewed NEVP’s Periodic Data Submittals related to its Power System Stabilizer (PSS) reports. On its Fourth Quarter 2008 Periodic Data Submittal, NEVP indicated it had a PSS outage from December 12, 2008 through December 15, 2008. The Audit Team conducted an interview with NEVP staff to discuss the circumstances and details associated with the December 2008 PSS outage. The Audit Team determined NEVP's Clark Station Unit #10 generator (Clark Unit #10) was in service when the PSS was out of service. The Audit Team noted that the PSS did not appropriately engage when NEVP brought Clark Unit #10 online and that NEVP was not aware of the PSS misoperation until NEVP ran an incident tracking report and determined the PSS was not in operation. NEVP clarified that failure of the PSS to engage upon start-up resulted in the unit operating for approximately 60.5 hours without the PSS in service. Similarly, NEVP discovered this issue approximately 60.5 hours after the unit start-up. Therefore, by the time NEVP, as a Generator Operator, was aware of the change in status of the PSS, the thirty-minute window to notify the Transmission Operator had elapsed. However, NEVP did notify the Transmission Operator upon discovering the change in status. | VAR-002-1a | R3 | Medium | Lower | WECC determined that the violation posed a minimal risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSS remained in service on the remaining units representing 97% of the NEVP system, which would protect the NEVP system and the BPS. In addition, the duration of the violation was limited to only 60.5 hours from December 12, 2008 to December 15, 2008. Clark Unit #10 is a steam turbine generator with a total capacity of approximately 85 MW fed by 2 combustion gas turbines. Together the three units make up a combined cycle block with approximately 253 MW of total generating capacity. The total generating capacity at the Clark Station generating facility is approximately 510 MW. NEVP’s total generating capacity is approximately 2,900 MW. Therefore, the violation is limited to a generating unit that represents 3% of the generation available to NEVP and the Transmission Operator. Further, the PSS remained in service for all other NEVP units when the Clark Unit #10 PSS was offline, therefore if Clark Unit #10 started to swing, the PSS on the remaining units (representing 97% of the NEVP system) would protect the NEVP system and the BPS. For these reasons, WECC determined this violation posed minimal risk to the reliability of the BPS. | 12/12/2008 (when the PSS outage began) | 12/15/2008 (when the PSS was restored) | 2000 | Compliance Audit / Periodic Data Submittal | NEVP immediately placed the PSS back in service once it was determined to be offline on December 15, 2008. NEVP then completed a root cause analysis to determine the break down in procedure and implemented the following actions to prevent this issue from recurring in the future: 1) installed relaying and connected the AVR and PSS to the Ovation software; 2) tested and installed new alarm logic to notify when PSS is out of service; 3) retrained all operators; 4) implemented new checklists for operators and shift supervisors; and 5) addressed personnel performance issues through corporate disciplinary actions. | 2009-01-16 | 2011-11-03 | Does Not Contest | WECC considered NEVP’s internal compliance program (ICP) as a mitigating factor. WECC found that: (1) NEVP has a fully documented ICP that has been reviewed and approved by the General Counsel who also serves as its Chief Compliance Officer; (2) NEVP’s oversight position is identified and staffed, and is supervised at a high level within the company; (3) the ICP oversight position has direct access to the CEO and Board of Directors; (4) NEVP operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards; (5) the ICP has sufficient staff and an adequate budget; (6) the ICP has NEVP senior management support and participation; and (7) NEVP’s ICP has a semi-annual or shorter review cycle.
Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC201102620 | Notice of Confirmed Violation | On January 25, 2011, PSE, as a Generator Operator, self-reported VAR-002-1.1b R3 to WECC. At 1530 PPT on January 9, 2011, PSE's Mint Farm generating station (Mint Farm) control room operator indentified that the steam turbine Power System Stabilizer (PSS) had not been in operation for approximately 9.5 hours. Once the condition was identified, the PSS was turned on. However, the plant did not notify the Transmission Operator, Bonneville Power Administration (BPA), of the change in status to the PSS within the required 30 minutes. The Transmission Operator was notified the following morning once it was discovered that the notification had not occurred. A root cause analysis indentified operator error as the primary root cause since the PSS is alarmed on the control system human-machine interface (HMI). Standard operating procedures detail the proper plant startup steps for PSS and the plant dispatch protocol include notifying the Transmission Operator of changes to automatic voltage regulator (AVR) and PSS status. A subsequent assessment of past PSS PI application data at Mint Farm uncovered a similar event with the steam turbine PSS on August 22, 2010. On that occasion, the PSS was off for 53 minutes. The operator did not notify the Transmission Operator of the change in status once the PSS was reactivated. This was the same operator from the January 9, 2011 event and the root cause was also operator error for the reasons outlined above. Given the finding of a second issue at Mint Farm in the PI application data, PSE reviewed available PI data for its remaining units equipped with PSS. This analysis revealed four unreported instances of PSS outages on the combustion gas turbine at PSE's Goldendale generating station (Goldendale) on August 3, 2010 (73 hours), August 6, 2010 (4 hours), November 5, 2010 (3 hours) and December 27, 2010 (4.5 hours). PSE investigated an additional PSS outage in January 2010. In each instance, it appears the PSS failed to activate after the unit tripped offline. On February 17, 2011, plant personnel verbally confirmed that they had no record of notifying the Transmission Operator about the change in status to the PSS when it was reactivated on each of those occasions. On the August 6, 2010 incident, the site operator observed the PSS outage and reported it to the control room operator. The control room operator activated the PSS and noted it in the plant log. Although PSS status for Goldendale is transmitted real-time to BPA via ICCP (Inter-Control Communications Protocol), BPA does not actively monitor PSS status for the plant. The analysis has identified that the primary cause of the Goldendale incidents were PSE's operators being unaware of the requirement to notify the Transmission Operator of changes to the PSS status within 30 minutes. WECC determined that PSE, as the Generator Operator, had more than five, but less than ten incidents of failing to notify its Transmission Operator, as required by VAR-002-1.1b R3.2. | VAR-002-1.1b | R3 | Medium | High | WECC determined the violation posed a minimal risk and not a serious or substantial risk to the bulk power system (BPS). PSE was not aware of any impact to the BPS because of the PSS being out of service at either facility. All but one of the outages were in short duration. In addition, the PSS for the other turbine was activated (combustion turbine PSS at Mint Farm, steam turbine PSS at Goldendale), which would have helped with the system damping if needed. The Transmission Operator confirmed that there were no issues on the transmission lines for the Mint Farm January 9, 2011 event. For the remaining dates, BPA did not make PSE aware of any impact at the time of those past events. | 8/3/2010 (Date of first instance) | 1/10/2011 (When BPA was notified) | 10900 | Self-Report | 1) For the 1/9/2011 Mint Farm incident, PSE notified the Transmission Operator upon discovery that the Transmission Operator was not notified. (Completed 1/10/2011) 2) PSE reviewed the proper procedures with the control room operators at Mint Farm for notifying its Transmission Operator within 30 minutes of AVR or PSS change in status. (Completed 1/14/2011) 3) PSE reviewed the Mint Farm communications protocol and operating procedures for clarity and revised the procedures and protocols as needed to clarify the notification process descriptions. (Completed 2/18/2011) 4) PSE assessed past PI application data for other possible PSS outages at Mint Farm. (Completed 2/11/2011) 5) PSE assessed available 2010 - 2011 PI application data for the remainder of PSE units equipped with PSS. For any identified PSS outages, PSE evaluated records to determine if the Transmission Operator was notified when PSS status was changed. (Completed 2/17/2011) 6) PSE notified all its plant managers and supervisors to review with operators NERC requirement to notify the Transmission Operator within 30 minutes of a change in status to AVR and PSS and to provide confirmation after the review has been completed. (Notification sent 2/17/2010) 7) PSE reviewed and updated AVR and PSS procedures at all other PSE plants to ensure they clearly reflect the NERC notification requirement. (Completed 3/15/2011) 8) PSE provided internal webinar refresher training for generation operations staff regarding all the requirements of VAR-002. (Completed 3/16/2011) 9) PSE implemented PSS alarming on affected units at Mint Farm and Goldendale. (Completed 2/22/2011) 10) PSE developed a plan and schedule for implementing additional AVR and PSS alarming at the remainder of PSE generating units. This included adding alarms at locations currently without alarming and adding supplemental text about notifying the Transmission Operator at those sites already alarmed. (Completed 4/15/2011) 11) PSE conducted gap analysis of internal processes for collecting and reporting data for the WECC quarterly AVR/PSS data submittals and implemented process improvements. (Completed 5/1/2011) | 2011-05-01 | 2011-11-03 | Neither Admits nor Denies | PSE had a documented compliance program in place at the time of the violations that WECC considered a mitigating factor in determining the penalty. WECC reviewed PSE’s internal compliance program (ICP) and found that: PSE's ICP was well designed and implemented; processes and procedures are tightly managed and controls are in place; key individuals, including the ICP Manager and Director are committed; executive leadership is knowledgeable and actively supports the program; and PSE’s ICP addresses all elements identified in FERC’s Revised Policy Statement on Enforcement.
Western Electricity Coordinating Council (WECC) | Sacramento Municipal Utility District (SMUD) | NCR05368 | WECC201102632 | Settlement Agreement | On January 20, 2011, SMUD, as a Load-Serving Entity, submitted a Self-Certification and on February 18, 2011, SMUD submitted a Self-Report addressing noncompliance with IRO-STD-006-0 WR1. SMUD discovered its possible noncompliance upon reviewing data related to Unscheduled Flow (USF) events. On October 14, 20101, the Path Operator for Path 66, a WECC Qualified Transfer Path, initiated a USF Curtailment Procedure, Step 5, at 14:25 Pacific Time which stayed in effect for hour ending 16:00. SMUD Initiated a Restricted Transaction at 14:28 by scheduling 20 MW on an off-path, after the Path Operator initiated the Curtailment Procedure, and contributed 3.4 MW of unscheduled flow on Path 66. The SMUD Power System Operations (PSO) acted to cut the schedule at 1503. Pursuant to the Sanction Table appended to the Standard, this violation represents one occurrence at Level One of Noncompliance. | IRO-STD-006 | WR1 | N/A | N/A | Although widespread failure to comply with IRO-STD-006 WR1 could pose significant risk to the reliability of the bulk power system (BPS), in this case, the line, the path operator and SMUD had compensating measures in place. Impact during USF events is dependent upon how much an entity contributes to flow on a potentially overloaded path, what other resources the path operator has available to mitigate potential overloads of the transmission system, and any available operating margin. The unscheduled flow involved with this violation is a fraction of one percent of the Path Rating for Path 66. Specifically, although SMUD scheduled 20 MW, it cut the schedule within three minutes of the curtailment procedure going into effect, resulting in SMUD only contributing 3.4 MW to Path 66. Path 66 is rated at 4,800 MW. Further, at the time the path operator initiated the curtailment procedure, Path 66 was below its operating limit by approximately 250 MW, leaving a 250 MW operating margin. The transmission operator continued to have the option of curtailing transactions directly scheduled on Path 66 to reduce flow in the event of an imminent overload. For these reasons, WECC determined that this violation posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. | 2010-10-14 | 2010-10-14 | 0 | Self-Certification | On November 1, 2010, a Principal Lead was hired to focus on communication and training for SMUD Real Time trading staff. The existing Unscheduled Flow desk procedure was emailed to all real-time trading staff upon final approval. One-on-one discussions were implemented with each real-time employee to insure their complete understanding of this standard and the revised desk procedure. This training was focused one-on-one instruction. | 2011-03-07 | 2011-08-04 | Does Not Contest | WECC considered the severity of the violation including compensating measures along with the length of the violations as mitigating factors. Pursuant to the Sanction Table appended to the Regional Standard, this violation represents one occurrence at Level One of Noncompliance. The Sanctions Table for this Standard state that the following sanction should be assessed "Letter to Responsible Entity's Chief Executive Officer informing the Responsible Entity of noncompliance with copies to NERC, WECC Member Representative, and WECC Operating Committee Representative."
Western Electricity Coordinating Council (WECC) | White Creek Wind I, LLC (WCW) | NCR00541 | WECC201002374 | Settlement Agreement | On November 12, 2010, while conducting an internal audit, WCW discovered that it did not have a FRM. Rather, WCW utilized a Wind Energy Resource Assessment document that stated that the generators were the most limiting element, and included other information such as historical wind data, turbine placement, and other studies done in the development of the facility. However, the Wind Energy Resource Assessment did not reference other component types required in R1. On December 17, 2010, WCW submitted a Self-Report concerning a violation of FAC-008-1 R1 due to WCW’s failure, as a Generator Owner, to have a Facility Ratings Methodology (FRM) that met all the sub-requirements of FAC-008-1 R1. | FAC-008-1 | R1 | Medium | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the facility was designed such that the actual wind generators were the most limiting element, and WCW’s personnel were trained that the generators were the most limiting element. In addition, WCW has generating capacity of approximately 205 MW, and interconnects to the BPS at 230 kV via two 34.5 kV/230 kV transformers. | 2008-07-23 | 2010-11-12 | $7500 (Settlement of WECC201002374 and WECC201002375) | Self-Report | WCW put in place on November 12, 2010 NAES Corporation's standard methodology for Facility Ratings documentation, and will periodically review the Facility Ratings Methodology and Facility Ratings for verification. | 2010-11-12 | 2011-11-09 | Agrees and Stipulates to the Facts | WECC determined that there were no aggravating factors warranting a higher penalty. In addition, WECC considered that this is WCW’s first assessed violation of any reliability standard. WECC considered that WCW was cooperative throughout the process, and there was no evidence of any attempt to conceal the violation.
Western Electricity Coordinating Council (WECC) | White Creek Wind I, LLC (WCW) | NCR00541 | WECC201002375 | Settlement Agreement | On November 12, 2010, while conducting an internal audit, WCW discovered that it did not have a valid FRM, and therefore, its facility ratings were not developed in accordance with a FRM as required by FAC-009-1 R1. On December 17, 2010, WCW submitted a Self-Report concerning a violation of FAC-008-1 R1 due to WCW’s failure, as a Generator Owner, to develop facility ratings in accordance with a valid Facility Ratings Methodology (FRM). | FAC-009-1 | R1 | Medium | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the facility was designed such that the actual wind generators were the most limiting element, and WCW’s personnel were trained that the generators were the most limiting element. In addition, WCW has a generating capacity of approximately 205 MW, and interconnects to the BPS at 230 kV via two 34.5 kV/230 kV transformers. | 2008-07-23 | 2010-11-12 | $7500 (Settlement of WECC201002374 and WECC201002375) | Self-Report | WCW put in place on November 12, 2010 NAES Corporation's standard methodology for Facility Ratings documentation, and then WCW used this methodology to determine the Facility Ratings in accordance with FAC-009 R1. | 2010-11-12 | 2011-11-09 | Agrees and Stipulates to the Facts | WECC determined that there were no aggravating factors warranting a higher penalty. In addition, WECC considered that this is WCW’s first assessed violation of any reliability standard. WECC considered that WCW was cooperative throughout the process, and there was no evidence of any attempt to conceal the violation.