## Public Non-CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Midwest Independent Transmission System Operator, Inc. (MISO) | NCR00826 | MRO201100272 | Settlement Agreement | On September 18, 2007, the MRO region experienced a category four disturbance which included a cascade of multiple lines that form the Minnesota-Wisconsin Stability Interface. The loss of these lines was followed by over frequency generator tripping and under frequency load shedding which ultimately resulted in the formation of system islands. MRO initiated a Compliance Violation Investigation (CVI) on March 3, 2008 and NERC assumed leadership of this CVI on March 5, 2008. On September 14, 2009, NERC issued a Preliminary Notice of Findings and Analysis to MISO detailing a finding of noncompliance with the Standard. The CVI team determined that MISO, as the Reliability Coordinator (RC), failed to provide directives to generators in a clear, concise, and definitive manner; failed to use proper three-way communications; and did not ensure that three-way protocols were followed, as required by the Standard. In the first instance, the directive given by MISO to one entity was unclear when it failed to identify the amount of generation MISO was directing be brought online. MRO determined that the entity used three-way communication in repeating back the directive to MISO and responded appropriately. In the second instance, three-way communication procedure was not followed in the directive given by MISO to another entity. MRO determined that even though the directive from MISO to the second entity was clear and carried out properly by the recipient operator, the three-way communication protocol was not followed. The directives were given during the restoration period and did not contribute to the loss of load. | COM-002-2 | R2 | Medium | Severe (Note that COM-002-2, R2 did not have an assigned VSL or applicable Levels of Noncompliance on the date of the violation, September 18, 2007. The VSL assignments were approved subsequently.) | MRO determined that MISO's violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because in both instances, MISO's directives were followed and correctly implemented, thereby satisfying the Standard's purpose of ensuring effective communications by operating personnel. Further, the Event Analysis Report recognized that MISO's rapid coordination enabled quick restoration (accomplished in 8 minutes 11 seconds) and stabilization of the BPS in the area for which MISO is the Reliability Coordinator. | 2007-09-18 | 2007-09-18 | 0 | NERC Compliance Violation Investigation | On May 13, 2011, MISO submitted a Mitigation Plan (MIT-07-3708) to MRO to address the violation of COM-002-2 R2. In accordance with the Mitigation Plan, MISO engaged in various mitigation activities, including: (1) provided dedicated communications training to its personnel in two training cycles in 2009 and in every training cycle in 2010; (2) revised its policies and procedures to improve compliance with this Standard, including a script to be used by operators; (3) engaged its Members in development and use of appropriate telephone protocol procedures, training and drills to ensure that communications occur in compliance with the Standard; (4) initiated operator call sampling and incentives; (5) tied the results of such sampling directly to operator performance assessments; and (6) reinforced compliance with this Standard through a slogan contest, all-employee meeting, visual support, and dedicated training. | 2008-12-08 | 2011-05-16 | Does not contest | MRO considered the following mitigating factors when determining the penalty amount: (1) MISO has no previous violations of the instant Standard and has other violations in the ReliabilityFirst region which do not involve the same or similar Standards; (2) MISO has a documented compliance program and culture that are well-defined and well-established through its corporate policy. The MISO Standards Compliance and Strategy department has a staff of eight employees headed by a Compliance Officer; and (3) MISO will conduct by April 1, 2012 two "Communications Forums" focused on control room communications and compliance with this Standard, and intended to promote collaboration and coordination between the entities responsible for complying with this Standard. MRO did not consider the loss of load in the penalty determination because these directives were given during the restoration period after the loss of load. MRO determined that there were no additional mitigating or aggravating factors in determining the penalty amount.
Northeast Power Coordinating Council, Inc. (NPCC) | Mirant Bowline, LLC (Mirant Bowline) | NCR07145 | NPCC200900121 | Settlement Agreement | During an October 11, 2009 through October 16, 2009 compliance audit of Mirant Bowline, NPCC discovered a violation of PRC-005-1 R1.1. NPCC determined that Mirant Bowline, as a Generator Owner, did not show maintenance and testing intervals for its current transformer (CT) and voltage or potential transformer (PT) generation Protection System devices. Documents provided to NPCC by Mirant Bowline, of its relay maintenance and testing program for the bulk power system, did not show maintenance and testing intervals for its CT and PT devices. The components of the Protection System include protective relays, associated communication systems, CTs, PTs, station batteries and DC control circuits. The 70 total CTs and PTs comprised fewer than 25% of the 408 applicable Protection System devices. | PRC-005-1 | R1; R1.1 | High | Lower | NPCC Enforcement determined that the violation posed a moderate but not serious or substantial risk to the reliability to the bulk power system. Although Mirant Bowline could not provide evidence that it verified the integrity of the CT and PT devices by performing testing on these devices periodically or defined testing intervals for these devices as per Mirant Bowline's maintenance document, there were no misoperation events or indication of failing/failed devices during the period. CT and PT testing was completed on April 1, 2010 for units 1 and 2, and all CT and PT devices tested satisfactorily. Also, based on evidence reviewed, no other potential evidence of noncompliance was identified with respect to all other aspects of Mirant Bowline. Mirant Bowline also employs back-up relaying providing backup protection should the primary systems fail. | 6/21/2007 (When Mirant Bowline registered for the Generator Owner function.) | 2/25/2010 (When Mirant Bowline's maintenance and testing program was enhanced to include maintenance and testing intervals for the CT and PT devices.) | $17,500 (for NPCC200900121 and NPCC200900122) | Compliance Audit | 1. Completed testing of CT and PT devices. 2. Revised the Protection System maintenance and testing program to include last testing date and next testing date for CT and PT devices. | 2011-05-03 | 2011-07-28 | Neither Admits nor Denies | Mirant Bowline has a documented internal compliance program which was reviewed and considered a neutral factor by NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Mirant Bowline, LLC (Mirant Bowline) | NCR07145 | NPCC200900122 | Settlement Agreement | During an October 11, 2009 through October 16, 2009 compliance audit of Mirant Bowline, NPCC discovered a violation of PRC-005-1 R2.1 and R2.2. NPCC determined that Mirant Bowline, as a Generator Owner, did not show testing of any of its 70 current transformer (CT) and voltage or potential transformer (PT) devices on its generation Protection System list. This list did show a listing of all protective relays, date last tested, testing interval periodicity and next required test date. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | NPCC Enforcement determined that the violation posed a moderate but not serious or substantial risk to the reliability to the bulk power system. Although Mirant Bowline could not provide evidence that it verified the integrity of the CT and PT devices by performing testing on these devices periodically or defined testing intervals for these devices as per Mirant Bowline's maintenance document, there were no misoperation events or indication of failing/failed devices during the period. CT and PT testing was completed on April 1, 2010 for units 1 and 2, and all CT and PT devices tested satisfactorily. Also, based on evidence reviewed, no other potential evidence of noncompliance was identified with respect to all other aspects of Mirant Bowline's relay maintenance and testing program for the requirements of PRC-005-1. Mirant Bowline also employs back-up relaying providing backup protection should the primary systems fail. | 6/21/2007 (When Mirant Bowline registered for the Generator Owner function.) | 5/3/2011 (Mitigation Plan completion.) | $17,500 (for NPCC200900121 and NPCC200900122) | Compliance Audit | 1. Completed testing of CT and PT devices. 2. Revised the Protection System maintenance and testing program to include last testing date and next testing date for CT and PT devices. | 2011-05-03 | 2011-07-28 | Neither Admits nor Denies | Mirant Bowline has a documented internal compliance program which was reviewed and considered a neutral factor by NPCC. Affiliated entities of Mirant Bowline have prior violations of PRC-005-1 R2.1 which were not considered aggravating factors in penalty determination. The filings: NP09-25-000 (Mirant Mid-Atlantic LLC), NP-10-2-000 (Mirant Potomac River, LLC), NP10-65-000 (Mirant Delta, LLC) and NP11-88-000 (Mirant Potrero, LLC), all include prior PRC-005-1 R2.1 violations by affiliates of Mirant Bowline. These prior violations were not considered aggravating factors because the conduct involved in the instant violation was not repetitive of the prior affiliates' conduct. In addition, there was nothing in the record to suggest that broader corporate issues were implicated.
Northeast Power Coordinating Council, Inc. (NPCC) | Niagara Mohawk Power Corporation (NMPC) | NCR07163 | NPCC201000177 | Settlement Agreement | On April 13, 2010, NPCC conducted a Spot Check of NMPC and discovered a violation of COM-002-2 R2. NPCC determined that NMPC, as a Transmission Operator (TOP), was in violation of the Standard. The NMPC control room operator failed to issue directives in a clear, concise, and definitive manner as required by the Standard. When issuing a directive to perform switching at a substation, the NMPC control room operator did not use the proper communication technique. Further, the NMPC control room operator did not ensure that the recipient of the communication repeated the information back correctly, as required by the Standard. The operator at the substation willingly accepted the switching order and performed the switching without incident. | COM-002-2 | R2 | Medium | Severe | NPCC determined that this violation posed a moderate risk but not serious or substantial risk to the reliability of the bulk power system (BPS) because the communication at issue was given during a period of restoration of equipment, and therefore took place under normal conditions rather than during a time of high stress, system instability, or system emergency. Additionally, the directive which was given in an improper manner was nonetheless carried out by the recipient in the correct manner and thus did not cause any additional risk. NPCC determined that there was a moderate risk because the switching directives associated with the communication errors could have been performed incorrectly which would have resulted in delays in proper restoration or additional equipment being forced out of service. | 6/14/2009 (when the improper communication occurred) | 2009-06-14 | 25000 | Spot Check | On November 23, 2010, NMPC submitted a Mitigation Plan to address the violation of COM-002-2 R2. In accordance with the Mitigation Plan: (1) NMPC's Transmission Control Center management team began random auditing of three-part communications of Security and System Operator communications. An audit form was developed and random tapes of communications were reviewed and discussed with the operator. The operators are made aware of communication technique expectations during these audits; (2) NMPC performed enhanced internal refresher training during Cycle 3 training in June 2010. Material covered included the COM-002-2 Reliability Standard, the NYISO Communication Running Order, and featured an audit of random communication by all of the class participants; (3) NMPC participated in the NYISO Fall 2010 System Operator Training Seminar, which featured refresher training on COM-002-2 in addition to an exercise in three-part communications at the NYISO Training Center; and (4) NMPC instituted a greater emphasis on three-part communication in all continuing operator training. | 2010-12-03 | 2011-03-11 | Neither Admits nor Denies | NPCC considered NMPC's Internal Compliance Program, which was in place at the time of the violation, to be a mitigating factor when determining the penalty amount. Specifically, NPCC considered that NMPC's ICP exists with sufficient Senior Leadership involvement; the ICP describes the annual training program related to compliance; NMPC reviews the ICP program activities regularly; NMPC keeps up to date with NERC/NPCC activities; and NMPC provides ample communication of the company’s commitment and expectations of employees.
ReliabilityFirst Corporation (RFC) | City of Niles Light Department (City of Niles) | NCR02710 | RFC201000674 | Settlement Agreement | RFC conducted a compliance audit of the City of Niles from October 18, 2010 to October 29, 2010. RFC determined that the City of Niles, as a Distribution Provider (DP), failed to provide the basis for the testing and maintenance interval applicable to its DC control circuitry in its Protection System maintenance and testing program, in violation of PRC-005-1, R1. RFC determined that although the Program required testing and maintenance according to a four-year testing and maintenance interval, the City of Niles did not document the basis for the identified testing and maintenance interval, as required by PRC-005-1, R1. The DC control circuitry represents 2 of 53 Protection System devices. | PRC-005-1 | R1 | High | Severe (from July 18, 2007 to May 18, 2011); High from May 19, 2011 to June 22, 2011 | RFC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, the City of Niles is a municipal utility with a peak load of 68 MW. Second, the City of Niles represented that it performed testing on its DC control circuitry devices in May 2007 as part of the installation and commissioning testing, although it did not retain records of the testing activity. In addition, the City of Niles completed maintenance and testing on its DC control circuitry on May 25, 2011 and found no problems with the devices. The entity completed this testing approximately four years from May 2007, the time it last tested the devices, which corresponds to the testing interval for DC circuitry now stated in its maintenance and testing program. | 9/28/2007(City of Niles was required to comply with this Standard) | 06/22/2011 (Mitigation Plan was completed) | $4000 (for RFC201000674 and RFC201000675) | Audit | On June 24, 2011, the City of Niles submitted as complete Mitigation Plan (MIT-07-3956) to address the violations of PRC-005-1 R1 and R2. In accordance with the Mitigation Plan, the City of Niles: (1) Revised its Program on June 22, 2011 to include the basis for the four-year testing and maintenance interval for its DC control circuitry; and (2) Performed all outstanding maintenance and testing on its DC control circuitry in accordance with the updated Plan. | 2011-06-22 | 2011-08-26 | Neither admits nor denies | RFC determined that there were no aggravating or mitigating factors in determining the penalty amount. RFC stated the City of Niles did not have a formal Internal Compliance Program (ICP).
ReliabilityFirst Corporation (RFC) | City of Niles Light Department (City of Niles) | NCR02710 | RFC201000675 | Settlement Agreement | RFC conducted a compliance audit of the City of Niles from October 18, 2010 to October 29, 2010. RFC determined that the City of Niles, as a Distribution Provider (DP), failed to provide documentation that it implemented its maintenance and testing program as it applied to its DC control circuitry. The City of Niles failed to provide documentation that it maintained and tested its two DC circuitry devices. As a result, the City of Niles failed to provide evidence (a) that it maintained and tested any of its DC control circuitry within the defined intervals of PRC-005-1, R2, and (b) of the date it last maintained and tested its DC control circuitry, as required by the PRC-005-1, R2 | PRC-005-1 | R2 | High | Severe | RFC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, the City of Niles is a municipal utility with a peak load of 68 MW. Second, the City of Niles represented that it performed testing on its DC control circuitry devices in May 2007 as part of the installation and commissioning testing, although it did not retain records of the testing activity. In addition, the City of Niles completed maintenance and testing on its DC control circuitry on May 25, 2011 and May 27, 2011 and found no problems with the devices. The entity completed this testing approximately four years from May 2007, the time it last tested the devices, which corresponds to the testing interval for DC circuitry now stated in its maintenance and testing program. | 9/28/2007(City of Niles was required to comply with this Standard) | 5/27/2011 (date completed the maintenance and testing of its DC control circuitry) | $4000 (for RFC201000674 and RFC201000675) | Audit | On June 24, 2011, the City of Niles submitted as complete Mitigation Plan (MIT-07-3956) to address the violations of PRC-005-1 R1 and R2. In accordance with the Mitigation Plan, the City of Niles: (1) Revised its Program on June 22, 2011 to include the basis for the four-year testing and maintenance interval for its DC control circuitry; and (2) Performed all outstanding maintenance and testing on its DC control circuitry in accordance with the updated Plan. | 2011-06-22 | 2011-08-26 | Neither admits nor denies | RFC determined that there were no aggravating or mitigating factors in determining the penalty amount. RFC stated the City of Niles did not have a formal Internal Compliance Program (ICP).
ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000629 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of VAR-002-1 R2. ReliabilityFirst determined that Sunbury, as a Generator Operator, had failed to maintain its voltage schedule as directed by its Transmission Operator (TOP). PJM Interconnection, LLC (PJM), Sunbury’s TOP, provides a default voltage schedule in the PJM Manual 03 "Transmission Operations" for those operators that do not receive a specific voltage schedule. The 230 kV voltage schedule is 235 kV, plus or minus 4 kV; PJM Manual 03 also lists a high limit voltage of 242 kV. Sunbury never received a specific voltage schedule from its TOP, and never obtained an exemption from the TOP. Sunbury does not and cannot control the transformers that control the switchyard voltages because they are located in the switchyards and are owned and operated by a different interconnected utility. On July 12, 2010 and August 20, 2010, the 230 kV switchyard at Sunbury exceeded the PJM default voltage schedule. On July 12, 2010 for forty-five minutes, the Sunbury 230 kV switchyard was at 239.5 kV, and on August 20, 2010 for six hours, the Sunbury 230 kV switchyard was above 239 kV. Although Sunbury exceeded the PJM default voltage schedule; it did not exceed the high limit of 242 kV. | VAR-002-1 | R2 | Medium | Lower | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system because at all relevant times, Sunbury cooperated with any voltage or reactive assistance requests received from the Transmission Owner or from the TOP. Sunbury has never received notification from either the Transmission Owner or the TOP that Sunbury failed to follow a directive related to voltage or reactive assistance. In addition, the Transmission Owner also provided a screen shot from its computers that monitor and control the Susquehanna region 230 kV voltages in which Sunbury is located. This screen shot indicates the high limit of 242 kV, which Sunbury did not exceed. Furthermore, the generator Automatic Voltage Regulators (AVRs) are always operated in automatic mode except during startup periods or in case of malfunction or system anomalies. In all cases, the TOP is notified whenever the AVR is switched to manual mode, and then again when it is returned to automatic mode. Sunbury conducted reactive testing on Unit 4 (required by PJM) on September 28, 2010. This testing requires that the generator be operated to its limit of MVAR lag operation for one hour. Subsequently, the generator must be operated to its limit of MVAR lead operation. Since Sunbury does not control or have access to the yard voltages, the voltage data was provided by the Transmission Owner. The voltage data provided by the Transmission Owner shows that there was no voltage change in the 230 kV yard, even though Sunbury operated the generator to both its lead and lag limits. | 8/2/2007 (When the Standard became mandatory and enforceable.) | 5/4/2011 (Mitigation Plan completion.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury conducted a conference call between Sunbury and the other interconnected utility to discuss voltage control capability; 2. Sunbury contacted PJM to discuss the voltage schedule issue to determine feasibility or possible exclusions; 3. The other interconnected utility conducted a system study to determine suitable voltage control based upon Sunbury maintaining low side generator step-up (GSU) voltage/reactive; 4. The information was submitted to PJM for approval; 5. Sunbury installed metering as necessary; 6. PJM reviewed the study and commented; and 7. PJM issued a voltage directive to Sunbury. | 2011-07-06 | 2011-12-28 | Neither Admits nor Denies | Due to extenuating circumstances associated with the violation of VAR-002-1 R2, there is no monetary penalty associated with the violation of VAR-002-1 R2. These included Sunbury never receiving a specific voltage schedule from its TOP, and never obtaining an exemption from the TOP, as well as the fact that Sunbury does not and cannot control the transformers that control the switch yard voltages. ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000630 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of FAC-008-1 R1.2.1. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to include the Ratings Methodology for its transmission conductors and relay protective devices in its Facility Ratings Methodology. Although Sunbury mentioned transmission conductors as part of its system and equipment, Sunbury failed to specifically mention transmission conductors and separately identify their Rating. | FAC-008-1 | R1.2.1 | Medium | High | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system because Sunbury did mention the transmission conductors in the Facility Ratings Methodology, and had determined the Ratings for those devices throughout the violation duration. Specifying the transmission conductors as a separate circuit element had no impact on the Facility Ratings overall, nor did it change the identification of the most limiting element. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 11/4/2010 (When Sunbury revised its Facility Ratings Methodology to include transmission conductors.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury revised its Facility Ratings Methodology to specify transmission conductors as a separate element included in the Facility Ratings; and 2. Sunbury also revised its Facility Rating Methodology spreadsheet to include the transmission conductors from the main unit transformers to the generator bay. | 2010-11-04 | 2011-02-15 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000631 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of PRC-005-1 R1. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to include all maintenance and testing intervals and their basis as well as summaries of maintenance and testing procedures for all of its Protection System devices in its Protection System maintenance and testing program. Sunbury’s Procedure PRC-005 Transmission and Generation Protection System Maintenance and Testing program (Program), dated February 8, 2010, failed to include all necessary elements. The Program failed to include maintenance and testing intervals and their basis for all 50 of its voltage and current sensing devices in violation of PRC-005-1 R1.1. In addition, the Program failed to include summaries of maintenance and testing procedures for all voltage and current sensing devices and its eight direct current control circuits in violation of PRC-005-1 R1.2. This violation involved 58 of Sunbury's 108 (55%) Protection System devices. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system. Specifically, the risk was mitigated because Sunbury has redundant protection in place. In addition, Sunbury has alarms that sound in both the plant control rooms and the plant control house upon the loss of power or similar malfunction. Additionally, except as noted in these violation descriptions, Sunbury tested its Protection System devices in accordance with their intervals, and all devices were functional and available. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 10/20/2010 (When Sunbury updated its Protection System maintenance and testing program.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury revised its Program to clarify battery maintenance and testing intervals, and that the maintenance and testing interval listed in the Program applies to all generator Protection System devices; and 2. The revised Program also includes summaries of maintenance and testing procedures for all Protection System devices. | 2010-12-03 | 2011-03-10 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000632 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of PRC-005-1 R2. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to provide evidence that it maintained and tested direct current control circuitry within the defined intervals and failed to identify the dates that it last tested direct current control circuitry. Sunbury failed to test direct current control circuitry within the defined interval, in violation of PRC-005-1 R2.1. In addition, Sunbury failed to identify the dates that it last tested its direct current control circuitry, in violation of PRC-005-1 R2.2. This violation involved all of Sunbury’s direct current control circuitry (100%) which constituted eight of Sunbury’s 108 (7.4%) Protection System devices. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system. Specifically, the risk was mitigated because Sunbury has redundant protection in place. In addition, Sunbury has alarms that sound in both the plant control rooms and the plant control house upon the loss of power or similar malfunction. Additionally, except as noted in these violation descriptions, Sunbury tested its Protection System devices in accordance with their intervals, and all devices were functional and available. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 10/20/2010 (When Sunbury updated its Protection System maintenance and testing program.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | Sunbury completed all delayed maintenance and testing on direct current control circuitry and began recording the test dates of those devices. | 2010-12-03 | 2011-03-10 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
SERC | Progress Energy Carolinas (PEC) | NCR01298 | SERC200900412 | Settlement Agreement | On December 8, 2009, PEC self-reported a violation of PRC-005-1 R1. During an investigation into battery inspection work orders, PEC discovered that it had failed to include the appropriate basis for battery maintenance intervals in its maintenance and testing documentation as required by the Standard. SERC was able to verify that PEC has a documented transmission Protection System maintenance and testing program. In 2008, PEC’s Asset Management group made a recommendation to revise the inspection of substation batteries from a six-month interval to a 12-month interval. The revised procedure was scheduled to become effective on August 1, 2009. With the revision, battery inspection and battery maintenance would be performed together on an annual basis. In addition, under the revised procedure, PEC would start conducting battery and battery charger maintenance together in order to streamline and eliminate unnecessarily redundant maintenance activities. PEC’s work management group completed the rescheduling of its battery maintenance activities in anticipation of the revised procedures’ August 1, 2009 implementation date but its procedure drafting group did not revise the Substation Equipment Maintenance Schedule until September 23, 2009, and the battery maintenance procedure until October 26, 2009. SERC determined that PEC, as a Transmission Owner, was in violation of PRC-005-1 R1.1 for failing to include the appropriate basis for battery maintenance intervals in its maintenance and testing documentation, as required by the Standard. There was no PRC-005-1 R2 issue in connection with this December 8, 2009 Self-Report. | PRC-005-1 | R1/ R1.1 | High | Lower | SERC determined that the PRC-005-1 R1.1 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the revised procedure had been implemented in PEC’s work order management system so that performance of battery maintenance and testing would take place according to the authorized intervals. In addition, all battery voltages are continuously monitored. An alarm would activate if an abnormal voltage was detected, resulting in the initiation of maintenance activity. | 8/1/2009 (date PEC's work order management system was changed to implement the new intervals without updating its procedures) | 1/11/2010 (Mitigation Plan completion) | $12,000 (For SERC200900306, and SERC200900412) | Self-Report | To correct the violation of PRC-005-1 R1.1 and to prevent a recurrence of the violation, PEC performed the following: 1. Developed a specific basis procedure for battery and battery charger maintenance; 2. Revised its Protection Basis Document, which provides the basis for all time-directed preventative maintenance applied to Transmission, Distribution, and Generation Protective Systems on October 26, 2009; 3. Revised the Transmission Maintenance Program Policy to require the group that implements the work management system not to release or modify work orders until they have verified that the procedures governing the work orders have been approved; and 4. Developed check points in a Functional Support Work Scope Document that must be completed by the work management group prior to releasing or modifying work orders. The checklist requires that the procedure’s effective date be recorded and verified prior to the release or modification of a work order. | 2010-01-11 | 2010-08-10 | Admits | Based on PEC’s September 20, 2010 responses to SERC’s Compliance Culture Questionnaire, Progress Energy’s (PEC's parent company) documented compliance program was initially approved on December 13, 2007, and was developed to formally document and drive existing compliance business practices. PEC’s compliance program is disseminated to all organizations within PEC that must comply with NERC Standards. The existence of PEC’s compliance program was a mitigating factor in determining the penalty. Progress Energy’s compliance program is prepared for and approved by Progress Energy’s ERO Steering Committee. The ERO Steering Committee is comprised of officers of PEC and Progress Energy Florida and is chaired by the ERO Compliance Officer, who is Progress Energy’s Executive Vice President – General Counsel and Corporate Secretary. The ERO Compliance Officer is independent of all PEC organizations that must comply with NERC Standards. The ERO Compliance Officer reports directly to the Chairman/President/CEO and has direct access to the Board of Directors. Company Officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments.
SERC | Progress Energy Carolinas (PEC) | NCR01298 | SERC200900306 | Settlement Agreement | On August 26, 2009, PEC self-reported a violation of PRC-005-1 R2. PEC discovered this violation while performing an inventory of its Protection System assets located within customer-owned facilities. When PEC inventoried the customer-owned Kinston DuPont 115 kV substation on August 20, 2009, it found two Coupling-Capacitor Voltage Transformers (CCVTs) owned by PEC that were not captured in its database. PEC’s Protection System maintenance and testing program for these CCVTs required maintenance to be performed by April 1, 2009, which had not occurred. PEC performed the required maintenance on August 20, 2009. PEC performed a comprehensive inventory of its Protection System components associated with PRC-005-1 under its Mitigation Plan. On October 25, 2010, PEC filed another Self-Report explaining that during the inventory, it found a column ground relay that had not been included in its equipment database. PEC’s investigation confirmed that the identified column ground relay did not have sufficient documentation to demonstrate that calibrations had been performed within the eight year intervals (+25 %) as required in the maintenance and testing program. The previous test date was July 27, 1998 and therefore, the subsequent testing should have occurred no later than July 27, 2008; however, the required test was not performed until September 2, 2010. SERC reviewed PEC’s Self-Report and its procedure along with the associated records and determined that a violation of PRC-005-1 R2.1 had occurred due to PEC’s failure to complete the required testing and maintenance of the relay within the assigned interval. On December 9, 2010, PEC self-reported an additional violation that was discovered while performing its Mitigation Plan inventory. PEC identified a battery that should have been re-classified on July 1, 2008, as a Protection System device in its equipment database. PEC’s investigation confirmed that the identified battery did not have sufficient documentation to demonstrate that the required maintenance was performed for the six- and 12-month preventative maintenance (PM) (+25%) as required in the maintenance and testing program. The six-month PM should have been performed no later than June 26, 2008, and the twelve-month no later than August 1, 2008, however the required maintenance and testing was not performed until August 13, 2008. SERC reviewed PEC’s Self-Report and procedure along with the associated records and determined that an additional violation of PRC-005-1 R2.1 had occurred due to PEC’s failure to complete the required testing and maintenance of the battery within the assigned intervals. SERC determined that PEC, as a Transmission Owner, was in violation of PRC-005-1 R2.1 for failing to have evidence that its Protection System devices had been maintained and tested within the defined intervals as required. No issues of noncompliance were identified for PEC’s generation Protection System. | PRC-005-1 | R2/ R2.1 | High | Lower | SERC determined that the PRC-005-1 R2.1 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) The CCVTs are designed to protect a customer’s delivery station and the tap lines serving the station. The CCVTs provide a back-up protective function for the components of the BPS. The devices that provide primary protection for the BPS were being tested and maintained at the prescribed intervals. In addition, testing and maintenance was performed on the CCVTs although not within the intervals specified in PEC's Protection System maintenance and testing program; (2) PEC has multiple layers of protection built into its system. Its 500 kV lines have redundant fast-tripping line protection systems that covers faults to the breakers. The column ground relay provides back-up protection. On September 2, 2010, testing was performed on the column ground relay and no recalibration was required; and (3) The maintenance and testing on the battery was performed two weeks out of interval. In addition, PEC monitors battery voltages in real time and monitors should trigger under-voltage alarms. This should allow for a timely response to a battery problem if the voltage were to drop below a pre-determined level. | 7/1/2008 (date the battery was re-classified as a Protection System device) | 9/30/2010 (Mitigation Plan completion) | $12,000 (For SERC200900306, and SERC200900412) | Self-Report | To correct the violation of PRC-005-1 R2.1 and to prevent a recurrence of the violation, PEC completed the following actions detailed in its Mitigation Plan: 1. Maintenance was performed on the two 115 kV CCVTs the same day that the location was field-verified; 2. PEC's equipment database was corrected to properly show the two CCVTs as located at the Kinston DuPont 115 kV Substation; 3. PEC performed an inventory of its NERC Protection System assets associated with its PRC-005 Protection System equipment. The inventory included verification of the assets within PEC's equipment database, a physical survey of the Protection System assets at PEC substations, including those with customer-owned equipment, as well as a reconciliation of the physical survey results with the PEC equipment database; and 4. PEC reviewed the equipment database process for improvements and re-emphasized the process through training and leadership with emphasis on the necessity of an accurate equipment database for NERC Protection System maintenance. The training targeted Engineering, Maintenance and Construction personnel and covered PEC's NERC Protection System maintenance & testing program, evidence requirements, the equipment database, and the Equipment Change Request process. | 2010-09-30 | 2010-02-14 | Admits | Based on PEC’s September 20, 2010 responses to SERC’s Compliance Culture Questionnaire, Progress Energy’s (parent company) documented compliance program was initially approved on December 13, 2007, and was developed to formally document and drive existing compliance business practices. PEC’s compliance program is disseminated to all organizations within PEC that must comply with NERC Standards. The existence of PEC’s compliance program was a mitigating factor in determining the penalty. Progress Energy’s compliance program is prepared for and approved by Progress Energy’s ERO Steering Committee. The ERO Steering Committee is comprised of officers of PEC and Progress Energy Florida and is chaired by the ERO Compliance Officer, who is Progress Energy’s Executive Vice President – General Counsel and Corporate Secretary. The ERO Compliance Officer is independent of all PEC organizations that must comply with NERC Standards. The ERO Compliance Officer reports directly to the Chairman/President/CEO and has direct access to the Board of Directors. Company Officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments.
Texas Reliability Entity, Inc. (Texas RE) | Brazos Electric Power Co Op, Inc. (Brazos) | NCR04016 | TRE201100277 | Settlement Agreement | On February 21, 2011, Brazos, as a Generator Operator, submitted a Self-Report identifying a violation of IRO-001-1.1 R8. At 05:18 CST on February 2, 2011, Electric Reliability Council of Texas Independent System Operator (ERCOT ISO), its Reliability Coordinator, was experiencing a system emergency (EEA‐2a), when it issued the following verbal directive: “Do not take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. Report when online available capacity is at risk due to an adverse circumstance.” At 08:09 the same day, while the system emergency was still in effect, Brazos removed Unit 2 of Whitney Dam, a 15 MW hydroelectric resource, from service in order to conserve water for later use. Realizing the mistake, at 08:11, the Brazos operator requested the Whitney Dam operator return Unit 2 to service, but the unit was then subject to a 30-minute operational limitation delay before restart could occur. Unit 2 was returned to service at 08:42. During the course of the above events, ERCOT ISO was not contacted. Accordingly, Texas RE determined that Brazos did not follow a reliability directive issued by the Reliability Coordinator. | IRO-001-1.1 | R8 | High | High | Texas RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the 15 MW size of the unit and because Brazos was able to deploy sufficient additional generation from its other available generation resources. | 2/2/2011 (When the Reliability Coordinator issued the directive) | 2/2/2011 (When Brazos complied with the directive) | $8,500 (for TRE201100277 and TRE201100278) | Self-Report | Brazos implemented its mitigation process which emphasizes and clarifies to the Qualified Scheduling Entity (QSE) control room operators and supervisors the required actions in the event of an ERCOT ISO directive. The following two parts reflect the key mitigation activities to this event: 1. Retraining of all QSE control room operators and supervisors to reemphasize their duty and the policy of Brazos to comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. In a meeting of QSE control room operators and supervisors which took place on February 22, 2011, the training was conducted emphasizing the critical nature of following all reliability directives. The importance of complying with Reliability Coordinator directives was reinforced by the manager of market operations and the vice president - power supply and generation at this same meeting. 2. Disciplinary action has been administered to the QSE resource operator on duty and his supervisor in accordance with the Brazos compliance plan dated September 29, 2010, Section D.3, Item 8.B.ii., which institutes “disciplinary action up to and including termination.” The resource operator on duty and the market operations specialist received a written reprimand for failing to follow Brazos’ procedures. The QSE resource supervisor and manager of market operations also received a written instruction to retrain staff. | 2011-04-25 | 2011-10-04 | Neither Admits nor Denies | Brazos' compliance program, in effect at the time of the violation, was considered a mitigating factor in the determination of the penalty amount. Brazos has a named compliance manager with the responsibility to oversee the development, implementation and maintenance of the compliance plan. The compliance manager has direct access to the CEO and/or the Brazos board of directors. Brazos regularly reviews and modifies its internal compliance program on an annual basis. The compliance manager also regularly conducts a compliance awareness program and compliance training program. The compliance training program is included in the compliance plan. Brazos senior management fully supports the compliance program and allocates adequate resources, including outsourcing, self-audits and budgets as well as establishing the necessary positions and associated responsibilities to ensure compliance. Brazos states that on an annual basis it conducts internal audits and reviews its compliance plan.
Texas Reliability Entity, Inc. (Texas RE) | Brazos Electric Power Co Op, Inc. (Brazos) | NCR04016 | TRE201100278 | Settlement Agreement | On February 21, 2011, Brazos, as a Generator Operator, submitted a Self-Report identifying a violation of TOP-001-1 R3. At 05:18 CST on February 2, 2011, Electric Reliability Council of Texas Independent System Operator (ERCOT ISO), its Reliability Coordinator, was experiencing a system emergency (EEA‐2a), when it issued the following verbal directive: “Do not take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. Report when online available capacity is at risk due to an adverse circumstance.” At 08:09 the same day, while the system emergency was still in effect, Brazos removed Unit 2 of Whitney Dam, a 15 MW hydroelectric resource, from service in order to conserve water for later use. Realizing the mistake, at 08:11, the Brazos operator requested the Whitney Dam operator return Unit 2 to service, but the unit was then subject to a 30-minute operational limitation delay before restart could occur. Unit 2 was returned to service at 08:42. During the course of the above events, ERCOT ISO was not contacted. Accordingly, Texas RE determined that Brazos did not follow a reliability directive issued by the Reliability Coordinator. | TOP-001-1 | R3 | High | Severe | Texas RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the 15 MW size of the unit and because Brazos was able to deploy sufficient additional generation from its other available generation resources. | 2/2/2011 (When the Reliability Coordinator issued the directive) | 2/2/2011 (When Brazos complied with the directive) | $8,500 (for TRE201100277 and TRE201100278) | Self-Report | Brazos implemented its mitigation process which emphasizes and clarifies to the Qualified Scheduling Entity (QSE) control room operators and supervisors the required actions in the event of an ERCOT ISO directive. The following two parts reflect the key mitigation activities to this event: 1. Retraining of all QSE control room operators and supervisors to reemphasize their duty and the policy of Brazos to comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. In a meeting of QSE control room operators and supervisors which took place on February 22, 2011, the training was conducted emphasizing the critical nature of following all reliability directives. The importance of complying with Reliability Coordinator directives was reinforced by the manager of market operations and the vice president - power supply and generation at this same meeting. 2. Disciplinary action has been administered to the QSE resource operator on duty and his supervisor in accordance with the Brazos compliance plan dated September 29, 2010, Section D.3, Item 8.B.ii., which institutes “disciplinary action up to and including termination.” The resource operator on duty and the market operations specialist received a written reprimand for failing to follow Brazos’ procedures. The QSE resource supervisor and manager of market operations also received a written instruction to retrain staff. | 2011-04-25 | 2011-10-04 | Neither Admits nor Denies | Brazos' compliance program, in effect at the time of the violation, was considered a mitigating factor in the determination of the penalty amount. Brazos has a named compliance manager with the responsibility to oversee the development, implementation and maintenance of the compliance plan. The compliance manager has direct access to the CEO and/or the Brazos board of directors. Brazos regularly reviews and modifies its internal compliance program on an annual basis. The compliance manager also regularly conducts a compliance awareness program and compliance training program. The compliance training program is included in the compliance plan. Brazos senior management fully supports the compliance program and allocates adequate resources, including outsourcing, self-audits and budgets as well as establishing the necessary positions and associated responsibilities to ensure compliance. Brazos states that on an annual basis it conducts internal audits and reviews its compliance plan.
Texas Reliability Entity, Inc. (Texas RE) | ExxonMobil Refining and Supply Company (ExxonMobil) | NCR04058 | TRE201000124 | Settlement Agreement | On May 18, 2010, after receiving notices from Texas RE of an upcoming compliance audit, ExxonMobil submitted a Self-Report to Texas RE concerning a violation of PRC-005-1 R2. The Self-Report described a failure to perform maintenance and testing on station batteries, protective relays, and current and potential transformers with the defined intervals of ExxonMobil’s Protection System Maintenance and Testing Program (Program) and failure to provide adequate documentation of maintenance and test results as required by the Program. Texas RE determined that ExxonMobil, as a Generator Owner, missed quarterly testing on battery pilot cell tests, missed the annual battery system load tests and certain 5-year load tests that were required under ExxonMobil's battery maintenance and testing program. ExxonMobil missed testing some relays under its two year maintenance and testing cycle for its protective relays. ExxonMobil also missed some of its annual load check tests for current and potential transformers. 403 or 71% of ExxonMobil's 569 devices were affected. | PRC-005-1 | R2 | High | High | This violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because although there is a risk of protection system failure or misoperation due to the lack of proper maintenance and calibration of the protective relays and battery systems, Texas RE determined that if the facility experienced an issue, it would be isolated to ExxonMobil's facility. Furthermore, redundant relaying schemes were in place. In addition, the facility at issue is relatively small, providing the BPS with a net of 50 MW capacity operating at approximately 20% capacity factor. | 6/28/2007 (date ExxonMobil was registered on the Compliance Registry) | 7/15/2011 (Mitigation Plan completion) | $13,000 (for TRE201000124 and TRE201000123) | Audit | • ExxonMobil provided all available missing maintenance records for Protection Systems devices to Texas RE. • ExxonMobil discussed TRE's Audit findings with its maintenance personnel, and provided refresher training in the proper use of its scheduling/tracking and record retention systems. • ExxonMobil reviewed its maintenance and testing procedures for its Protection Systems devices, and made modifications to include steps for record retention. • ExxonMobil completed all outstanding maintenance and testing for its Protection Systems devices. | 2011-07-15 | 2011-07-20 | Neither Admits nor Denies | Texas RE received the Self-Report on May 18, 2010, after Texas RE sent an Audit notification to ExxonMobil. The Audit concluded July 21, 2010, and is the date the violations were deemed to have been discovered by Texas RE. A Settlement Agreement covering several violations, including a violation of PRC-005-1 R2 for ExxonMobil Oil Corporation - Beaumont Refinery (ExxonMobil BR) (NCR01239), an affiliate of ExxonMobil in the SERC Region, (NOC-428) filed with FERC under NP10-90-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE determined that ExxonMobil BR’s previous violation of PRC-005-1 R2 in NOC-428 constituted a prior violation that should be considered an aggravating factor in the penalty determination. While ExxonMobil has multiple documented operating and maintenance procedures in place to ensure NERC compliance, Texas RE did not consider ExxonMobil’s compliance program as a mitigating factor in determining the penalty.
Texas Reliability Entity, Inc. (Texas RE) | ExxonMobil Refining and Supply Company (ExxonMobil) | NCR04058 | TRE201000123 | Settlement Agreement | On May 18, 2010, after receiving notices from Texas RE of an upcoming compliance audit, ExxonMobil submitted a Self-Report to Texas RE concerning a violation of CIP-001-1 R2. The Self-Report described ExxonMobil’s failure to include consistent communications procedures in its sabotage reporting guidelines. Texas RE determined that ExxonMobil, as a Generator Operator, did not have a sabotage procedure sufficient to show compliance with the Standard. An ExxonMobil Baytown Complex Emergency Procedure (Procedure) was created in April 2008 to directly address sabotage events that would impact the bulk electric grid. The sabotage procedure did not consistently contain provisions for the communication of information concerning sabotage events to ERCOT Independent System Operator. Texas RE determined that the Procedure was not sufficient as a stand-alone document to demonstrate compliance, as it included multiple procedures concerning various types of sabotage that could impact the electric grid. | CIP-001-1 | R2 | Medium | High | This violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because ExxonMobil operators were aware of the requirement to contact ERCOT ISO as an operating practice. Certain, but not all, ExxonMobil sabotage procedures specify ERCOT ISO as a party to contact in the event of sabotage. Texas RE determined that this violation was principally documentation-related. | 6/28/2007 (date ExxonMobil was registered on the Compliance Registry | 1/12/2011 (Mitigation Plan completion) | $13,000 (for TRE201000124 and TRE201000123) | Audit | ExxonMobil included ERCOT ISO in the contact lists for the following emergency procedures: Bomb Threat, Suspicious Package, Suspicious Powder, and Unauthorized Intruder. | 2011-01-12 | 2011-07-20 | Neither Admits nor Denies | Texas RE received the Self-Report on May 18, 2010, after Texas RE sent an Audit notification to ExxonMobil. The Audit concluded July 21, 2010, and is the date the violations were deemed to have been discovered by Texas RE. While ExxonMobil has multiple documented operating and maintenance procedures in place to ensure NERC compliance, Texas RE did not consider ExxonMobil’s compliance program as a mitigating factor in determining the penalty.
Texas Reliability Entity, Inc. (Texas RE) | Luminant Generation Company, LLC (Luminant) | NCR10219 | TRE201000273 | Settlement Agreement | On September 2, 2010, Luminant submitted a Self-Report identifying a violation of PRC-005-1 R2. Luminant, as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 1,068 protection system devices, tests for 76 devices (7.12% of total devices) comprising some relays and instrument transformers were completed outside the documented test intervals (three-year periodicity). These 76 protection system devices were not identified and included in Luminant's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switchyard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, Luminant did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Lower | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. Luminant has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Luminant registered with NERC registry) | 11/16/2011 (the date the Mitigation Plan was completed) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | Luminant submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. Luminant is a subsidiary of Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
Texas Reliability Entity, Inc. (Texas RE) | Big Brown Power Company, LLC (Big Brown) | NCR10217 | TRE201000272 | Settlement Agreement | On September 2, 2010, Big Brown submitted a Self-Report identifying a violation of PRC-005-1 R2. Big Brown, as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 58 protection system devices, ten (17.24% of total devices) devices comprising some relays and instrument transformers were completed outside the documented test intervals (three year periodicity). These ten protection system devices were not identified and included in Big Brown's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switch yard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, Big Brown did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Lower | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. Big Brown has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Big Brown registered with NERC registry) | 11/16/2011 (the date the Mitigation Plan was completed) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | Big Brown submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. Big Brown is a subsidiary of Luminant Holding Company LLC (LHC), a subsidiary of Energy Future Holdings Corp. Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
Texas Reliability Entity, Inc. (Texas RE) | Tradinghouse Power Company LLC (TPC) (TPC was removed from the NERC registry as a GO effective 1/1/2011) | NCR10220 | TRE201000274 | Settlement Agreement | On September 2, 2010, TPC submitted a Self-Report identifying a violation of PRC-005-1 R2. TPC , as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 29 protection system devices, eight (27.59% of total devices) devices comprising some relays and instrument transformers were completed outside the documented test intervals (three year periodicity). These eight protection system devices were not identified and included in TPC's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switchyard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, TPC did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. On December 31, 2010, Unit 2 of the Tradinghouse Steam Electric Station permanently retired from service. Unit 1 at Tradinghouse was retired in 2009. There are no other generating units at this plant site or assigned to this entity, therefore, TPC no longer has any generation assets and was removed from the NERC registry as a Generator Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Moderate | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. TPC has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Tradinghouse registered with NERC Registry) | 12/31/2010 (the last date TPC's units were operational) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | TPC submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. TPC is a subsidiary of Luminant Holding Company LLC (LHC), a subsidiary of Energy Future Holdings Corp. Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
Western Electricity Coordinating Council (WECC) | AES Alamitos (ALGS) | NCR05002 | WECC201102728 | Settlement Agreement | On December 8, 2010, WECC notified ALGS that it would be conducting an off-site compliance Audit. On February 18, 2011, ALGS submitted a Self-Report, stating that, as a Generator Owner, it was unable to produce evidence of testing and maintenance within defined intervals for all of its batteries subject to this Standard. During the Audit, WECC's Subject Matter Expert determined that ALGS had a documented Maintenance and Testing Program for its Protection System devices and sampled testing records for 29 devices. ALGS provided evidence of the date the batteries were last tested and maintained but was unable to demonstrate that the testing was performed within the defined intervals specified in its Program for one set of batteries comprised of three batteries. Based on the record and additional information obtained from ALGS, WECC enforcement determined that ALGS could not provide evidence of testing within the intervals defined in its program, in violation of this Standard. The scope of the violation was limited to one set of batteries, which account for less than 25% of ALGS's total batteries. | PRC-005-1 | R2.1 | High | Lower | WECC determined that this violation did not pose serious or substantial risk and posed a minimal risk to the reliability of the bulk power system because although ALGS failed to test its batteries within the specified intervals, it provided evidence that it tested the devices pursuant to its Plan for Protection Systems, including relays and DC circuitry. Also, ALGS was able to provide evidence of testing for the majority of its batteries subject to PRC-005-1. Further, WECC determined that in the event of a malfunction, ALGS's batteries are equipped with an alarm system designed to immediately alert personnel of any failure or defect. | 2007-06-18 | 2011-03-31 | 8700 | Self-Report | On March 4, 2011, ALGS submitted a Mitigation Plan and completed the following activities: (1) Assigned a Team Leader to oversee PRC-005-1 compliance and ensure maintenance and testing of its Protection System devices was appropriately documented; (2) Revised its Maintenance and Testing Procedures to include review and approval by the station manager; (3) Revised its Maintenance and Testing document forms; (4) Implemented the revised Maintenance and Testing procedures; and (5) Added an updated Preventative Maintenance work notification in the Systems Applications and Products (SAP) program. | 2011-03-31 | 2011-11-28 | Agrees and Stipulates to the Facts | WECC considered the following mitigating factors in determining the penalty amount: (1) ALGS took voluntary corrective actions to remediate this violation; (2) ALGS self-reported the violation; (3) ALGS's Internal Compliance Program was documented and disseminated throughout the operations staff; ALGS has ICP oversight staff, which is a supervised at a high level in the organization; ALGS has allocated sufficient resources to its ICP and the ICP has the support and participation of the senior management; ALGS reviews and modifies its ICP regularly and the ICP includes formal, internal self-auditing for compliance with the Reliability Standards on a periodic basis; the ICP includes disciplinary action for employees involved in violations of the Reliability Standards; (4) This is not a repeat violation; (5) ALGS was cooperative throughout the compliance process and completed all of WECC's compliance directives; and (6) WECC found no evidence that ALGS attempted to conceal the violation or that the violation was intentional. WECC determined that there were no aggravating factors in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | City of Glendale (GLEN) | NCR05081 | WECC201102856 | Settlement Agreement | On June 30, 2011, GLEN submitted a Self-Report addressing a violation of the WECC Regional Reliability Standard IRO-STD-006-0, WR1. The purpose of this Standard is the mitigation of transmission overloads due to unscheduled line flow on Qualified Paths. Specifically, on May 11, 2011, GLEN's agent for real time trading and scheduling, ACES Power Marketing LLC (APM), notified GLEN of possible Unscheduled Flow (USF) violations which occurred on October 14, 2010, October 15, 2010, and June 5, 2010. The first instance, event 7617, occurred as a result of the trader failing to respond for one hour, which resulted in 2.2 MW of noncompliance. The second instance, event 7642, occurred when APM responded to a WebSAS alarm and curtailed tag 24096 by 4 MW, providing the necessary relief. Following this response, a purchase was made on tag 24130 which inadvertently pushed the line over its limit, resulting in 0.8 MW of noncompliance. APM attempted to adjust the tag back, which would have resulted in compliance, but WAPA-Lower Colorado (WALC) denied the adjustment due to late submission. The third instance, event 7311, occurred when APM failed to respond to a schedule and tag of 3 MW identified by WebSAS impacting path California-Oregon Intertie Path (COI) that should have been adjusted to 0 MW, resulting in 1.0 MW of noncompliance. At the time of the violation, this Standard applied to GLEN, in its function as a Load-Serving Entity. | IRO-STD-006-0 (Note that on July 1, 2011, this Standard was replaced by IRO-006-WECC-1. The new Standard applies to Balancing Authorities (BA) and Reliability Coordinators (RC). Because GLEN's registered functions do not apply to the new Standard's applicability criterion, the Standard no longer applies to GLEN.) | WR1 | N/A | N/A | WECC determined that this violation posed a minimal but not a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) the transmission operator continued to have the option of curtailing transactions that were directly scheduled on the Qualified Path to reduce loading in the event of an imminent overload; (2) the amount of flow increase on the path was less than 1% of the path ratings; and (3) the violation did not result in an overload of the transmission system. WECC determined that this violation is a "Level 1" noncompliance. | 10/14/2010, 10/15/2010, 6/5/2010 (the dates of the three separate events) | 10/14/2010, 10/15/2010, 6/5/2010 (the dates of the three separate events) | 500 | Self-Report | On July 1, 2011, GLEN submitted to WECC a Mitigation Plan (MIT-11-3882) to address the violation of IRO-STD-006-0, WR1. In accordance with the Mitigation Plan, GLEN has taken the following action: (1) reviewed the WebSAS utility training materials used by APM and received written confirmation from APM that all traders have received supplemental training; (2) GLEN's Energy Management group ran a monthly report using WebSAS to verify compliance with the USF standard from January 2010 to June 2011; (3) APM has taken steps to ensure that the audible and visual alarms associated with the WebSAS utility are checked by the trader each day and each shift to ensure they are in working order; and (4) GLEN's Internal Audit Department performed a review of APM’s desk procedures and activities, including a spot check of selected transactions. | 2011-07-27 | 2011-08-02 | Does Not Contest | WECC determined there were no aggravating factors in determining the penalty amount. GLEN has no prior violations of any Reliability Standards.
Western Electric Coordinating Council (WECC) | Griffith Energy, LLC (GRGO) | NCR03052 | WECC201002858 | Settlement Agreement | On October 21, 2010, GRGO submitted a Self-Report stating that GRGO experienced a problem with its Steam Turbine Generator (STG) on October 12, 2010, and discovered that the Power System Stabilizer (PSS) control for the steam turbine was in an OFF position when it should have been in an ON position. GRGO's plant is comprised of one steam turbine and two combustion turbines. On March 23, 2010, the STG was powered down for a replacement of a bad communications card and then powered up and restored to normal operation. However, because GRGO was not aware that the default position was the OFF position, it did not turn it back ON, and the STG PSS system continued to operate in an OFF position. Based on the record, WECC determined that GRGO, as a Generator Operator, failed to ensure that the STG PSS control system was kept in service at all times in order to provide frequency support to the grid. | VAR-STD-002b-1 | WR1 | The sanctions for this regional standard are determined based on a level of non-compliance ranging from Level 1 to Level 4 | The sanctions for this regional standard are determined based on a level of non-compliance ranging from Level 1 to Level 4 | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because GRGO's two combustion turbines' PSSs were ON during the period of the violation, minimizing the need for GRGO's steam turbine to stabilize the generators. Although the STG PSS system was in the OFF position, the plant as a whole performed in an expected manner and was able to support grid frequency deviations per control design on two separate occasions. In addition, WECC determined that the size of the generator involved - 250 MW steam turbine generator, reduced the risk to the BPS. Also, GRGO investigated all generation data for the period of operation without the STG PSS in service and no abnormalities were noted. GRGO's Transmission Operator, the Western Area Power Administration, showed no abnormalities due to GRGO's STG PSS system being OFF. | 2010-03-23 | 2010-10-12 | 1000 | Self-Report | GRGO immediately restored the PSS to its normal ON operation position after discovering its status on October 12, 2010. According to its Mitigation Plan (MIT-10-3874), GRGO: 1) Conducted refresher training with all operations and management personnel on the PSS and VAR-STD-002b-1; 2) Committed to work with the steam turbine controls vendor to change PSS operational logic, if possible, so that the system defaults to "ON" position following a loss of power; 3) Updated the plant's distributed controls system to include alarm indication when PSS not in service; 4) Updated operator shift rounds to include a check of PSS operation. | 2011-01-28 | 2011-11-18 | Does Not Contest | WECC considered the following factors in determining the penalty amount: GRGO's violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS, the violation was self-reported, there were no aggravating factors in determining the penalty amount, and the violation did not pose an ongoing risk to the BPS.
Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102909 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing noncompliance with MOD-010-0 R1. According to the Self-Report, during an internal review of standards, NCPA found that, as a Generator Owner, it had not been submitting or checking all data from the regional coordinator Pacific Gas and Electric (PGAE) and had failed to provide complete equipment characteristics and system data and review of data as required. During the investigation, it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-010-0 | R1 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102910 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing noncompliance with MOD-010-0 R2. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, failed to implement a formal process that ensures all data is reviewed for accuracy prior to being submitted to the area coordinator. Specifically, NCPA failed to jointly coordinate the development of the data requirements and reporting procedures with Pacific Gas and Electric (PGAE). NCPA's failure to follow a documented procedure for submitting data to PGAE resulted in data being submitted to PGAE prior to NCPA reviewing for accuracy. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-010-0 | R2 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102911 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing possible noncompliance with MOD-012-0 R1. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, had not provided dynamic system modeling and simulation data to Pacific Gas and Electric (PGAE), the regional coordinator. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-012-0 | R1 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102912 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing possible noncompliance with MOD-012-0 R2. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, had not provided complete equipment characteristics and system data and review of data to Pacific Gas and Electric (PGAE), the regional coordinator, for use in the WECC system-wide model. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-012-0 | R2 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.