## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Issue Tracking # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Northeast Power Coordinating Council, Inc. (NPCC) | ReEnergy Sterling CT Limited Partnership (RES); formerly Exeter Energy Limited Partnership (Exeter) | NCR11110; NCR07083 (inactive 4/26/2011) | NPCC201100253 | Settlement Agreement | On November 30, 2010, a complaint was filed with NPCC stating that Exeter, as a Generator Operator (GOP), was in violation of TOP-002-2a R3. On October 23, 2010, at 16:00 EST, Exeter had cleared its Host Balancing Authority's (BA) day-ahead market for October 24, with a self-scheduled bid of 23 MW, beginning at hour ending 1:00. Later on October 23, 2010, at 21:22, the operator for Exeter notified the BA's system operator that, as of 20:10 on that day, Exeter's turbine was out of service for a scheduled outage. In a follow-up call initiated by the BA's system operator shortly thereafter, Exeter informed the system operator that the turbine would likely be out of service until the morning of October 26, 2010. While Exeter took the plant out of the day-ahead market during the outage period, it failed to make a corresponding designation of "Not Available" in the real-time market, thereby failing to make it clear to the BA that the plant was no longer available for services. Also, as a result of the scheduled outage, Exeter was unable to meet its self-scheduled obligation in the day-ahead market. Exeter failed to give a proper seven-day notice to the BA that the turbine will be out of service. Based on these facts, NPCC determined that Exeter was in violation of TOP-002-2a R3 for a failure to coordinate its next-day operations and scheduled outage with its BA, as required by this Standard. | TOP-002-2a | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the Exeter facility has a maximum capability of 31 MW compared to the 29,900 MW overall capacity within the BA area, generally generates at a level of 22 MW and is connected at a voltage level of 115 kV. Also, the BA was not required to significantly alter its dispatch operating plan due to the unavailability of the Exeter generator and has not otherwise made any findings of adverse impact to the BPS due to Exeter's failure to coordinate and obtain BA's approval for the outage. NPCC determined that these factors mitigated the risk to the BPS to minimal. | 10/24/2010 (when Exeter failed to coordinate the outage) | 10/26/2010 (when the outage ended) | $15,000 (for NPCC201100253 and NPCC201100254) | Complaint | RES/Exeter completed the following mitigation activities, in accordance with its Mitigation Plan: 1) Implemented a new communications procedure to address communications between RES/Exeter and the BA for generator maintenance and outage scheduling; and 2) Administered training on the newly implemented communication procedure. | 2011-09-15 | 2012-03-21 | Neither Admits Nor Denies | NPCC considered RES's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount. RES took ownership of the Exeter facility after the violation occurred and during the processing of the mitigation activities but did take compliance responsibility and cooperated with NPCC to bring the matter to conclusion. Unlike Exeter, RES showed a commitment to address the violation and to provide a process to minimize the possibility of repeat occurrences.
Northeast Power Coordinating Council, Inc. (NPCC) | ReEnergy Sterling CT Limited Partnership (RES); formerly Exeter Energy Limited Partnership (Exeter) | NCR11110; NCR07083 (inactive 4/26/2011) | NPCC201100254 | Settlement Agreement | On January 17, 2011, Exeter submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of TOP-002-2a R13. On July 1, 2010, an email with an attached letter was sent by the Balancing Authority's, ISO-New England's, manager of system operations support to CMS Energy Resource Management Company (CMS ERM), requesting that arrangements be made for the Exeter plant to conduct reactive capability tests with the first prior to September 15, 2010 for lagging reactive capability, and the second prior to October 31, 2010 for leading reactive capability. At the time of this violation, CMS ERM was providing management services to Exeter, but as a registered entity, Exeter continued to be responsible for compliance with, and accountable for any violations of, the NERC Reliability Standards. CMS ERM emailed this communication to the Exeter plant, but this message was inadvertently overlooked by plant personnel, and the requested Volt-Ampere Reactive (VAR) testing was not performed. On December 16, 2010, ISO-New England sent a letter to CMS ERM stating that CMS ERM had failed to conduct and report either of the two required reactive capability tests for the Exeter plant as required by TOP-002-2a R13. Based on these facts, NPCC determined that Exeter was in violation of TOP-002-2a R13 for a failure to conduct and report either of the two required reactive capability tests as requested by the Balancing Authority. | TOP-002-2a | R13 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the Exeter facility has a name plate rating of 31 MW compared to the 29,900 MW overall capacity within the Balancing Authority area and is connected at a voltage level of 115 kV. Due to its small capacity and connection to the grid at the 115 kV level, the Exeter facility is capable of generating or absorbing a small amount of reactive power, thereby reducing the risk to the BPS. Also, although the unit did not prove its VAR capability to the Balancing Authority, the unit was still fully capable of delivering reactive power if called upon. | 11/1/2010 (when Exeter failed to perform the required tests) | 9/9/2011 (Mitigation Plan completion) | $15,000 (for NPCC201100253 and NPCC201100254) | Self-Report | RES completed the following mitigation activities, in accordance with its Mitigation Plan: 1) Performed leading and lagging reactive capability testing; 2) Contracted with a third-party vendor to provide lead participant, risk, and consulting services to assure completion of requested tasks on or before its due date. The agreement requires the third party vendor to notify RES of all reliability and operation-based actions, activities, and duties associated with or related to the NERC Reliability Standards, as notified by the Balancing Authority, to ensure that any such requests and other requirements are acted upon in accordance with such requests. | 2011-09-09 | 2012-03-21 | Neither Admits Nor Denies | NPCC considered RES's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount. RES took ownership of the Exeter facility after the violation occurred and during the processing of the mitigation activities but did take compliance responsibility and cooperated with NPCC to bring the matter to conclusion. Unlike Exeter, RES showed a commitment to address the violation and to provide a process to minimize the possibility of repeat occurrences.
ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2012001310 | Settlement Agreement | On January 9, 2012, Consumers submitted a Self-Report to ReliabilityFirst stating that as a Generator Operator (GOP), Consumers was in violation of VAR-002-1.1b R2. Consumers’ DE Karn generating units #1 and #2 each interconnect to the bulk power system (BPS) at 138 kV and have respective generating capacities of 255 MW and 260 MW. Consumers normally operates these generating units consistent with the voltage schedule provided by its Transmission Operator (TOP). On Thursday, November 10, 2011, at 7:01 am, Consumers was required to change the voltage output of DE Karn generating units #1 and #2 to 145 kV pursuant to its regular schedule, but failed to do so until 10:58 am. Consumers operated the DE Karn generating units #1 and #2 between 142 - 143 kV during this time. Audible and visual alarms informing the operator to change the voltage went off, but the operator failed to notice the alarms because the operator was occupied with the startup of the DE Karn generating unit #2 and was monitoring the switching status of the substation. ReliabilityFirst determined that Consumers violated VAR-002-1.1b R2 by failing to maintain the generator voltage output as directed by the TOP. | VAR-002-1.1b | R2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the BPS because risk was mitigated by the following factors. First, additional Consumers' generating units were online that were available to provide voltage or reactive support. Additionally, Consumers’ Automatic Voltage Regulator was operating in automatic mode during the time period of the violation. Consumers was operating less than 5% outside of its voltage schedule, thereby decreasing the likelihood of compromising BPS voltage. Finally, Consumers has both audible and visual alarms in place in the control room to alert operators to change the voltage for the units at issue. Although the operator was focused on startup and switching of DE Karn generating unit #2, and failed to notice the alarms in this instance, the alarms exist to inform operators to change the voltage. | 11/10/2011 (when Consumers operated DE Karn generating units #1 and #2 outside the voltage schedule) | 11/10/2011 (when Consumers returned to operating DE Karn generating units #1 and #2 inside the voltage schedule) | 2500 | Self-Report | On January 9, 2012, Consumers submitted to ReliabilityFirst a Mitigation Plan to address the violation of VAR-002-1.1b R2. In accordance with the Mitigation Plan, Consumers validated the audible and visual control room alarms that alert the operator to change voltage and modified these alarms so that they repeat at regular intervals until satisfied. Consumers also reviewed the voltage schedule requirements with all DE Karn generating units #1 and #2 operators. | 2012-02-03 | 2012-06-01 | Agrees/ Stipulates | ReliabilityFirst considered certain aspects of Consumers’ internal compliance program (ICP) as mitigating factors when determining the penalty amount. Consumers has a NERC Compliance Assurance process in place to ensure that it meets the requirements of the Reliability Standards. In addition, the individuals responsible for compliance have direct relationships with senior executives. Consumers’ Transmission and Regulatory Strategies Compliance personnel are responsible for FERC and NERC compliance and report directly to the Vice President of Energy Supply Operations. Furthermore, Consumers periodically conducts internal self-evaluations for compliance with the Reliability Standards. The Chairman of the Executive Management Committee regularly reports compliance status to the Consumers compliance review committee. Consumers previously self-reported violations of VAR-002 R1 and R3. However, the facts and circumstances of the previous violations are dissimilar to the facts and circumstances of the instant violation. Consumers’ previous violations occurred due to a manufacturer labeling error on the Automatic Voltage Regulator, and the instant violation was a voltage schedule excursion. Consumers’ affiliate, TES Filer City (TES), as a GOP, previously self-reported violations of VAR-002 R1 and R3. TES did not notify its TOP within thirty minutes that on August 4, 2008 and April 5, 2010, its Automatic Voltage Regulator was operated in manual mode while Consumers’ instant violation is a voltage schedule excursion. Therefore, ReliabilityFirst did not consider Consumers’ compliance history as an aggravating factor in the penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | Horse Hollow Generation Tie, LLC (HHGT) | NCR10392 | TRE201100384 | Settlement Agreement | On September 2, 2010, HHGT submitted its Self-Certification for FAC-001-0 and then submitted a Self-Report for FAC-001-0 R1 on September 14, 2010. On December 6, 2010, HHGT submitted a corrected Self-Report. Following a review of HHGT's Self-Certification and Self-Reports, Texas RE determined that HHGT, as a Transmission Owner (TO), violated FAC-001-0 R1 because HHGT did not document, maintain and publish facility connection requirements until May 25, 2010. To show compliance with this Standard, HHGT provided the appropriate document dated May 25, 2010 and an Interconnection Agreement dated June 26, 2009, which served as the document available for facility connection requirements. However, Texas RE determined that the 2009 Interconnection Agreement did not ensure full compliance with this Standard because it was only between HHGT and a neighboring TO, it was specific to some but not all facilities, and it did not address the connection requirements for all the facilities owned by HHGT. | FAC-001-0 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). Although HHGT did not document, maintain and publish facility connection requirements during the violation period, the interconnection point linking HHGT's 345 kV line to another entity's substation had adequate facility connection requirements. In addition, the risk was reduced by the fact that the facilities not addressed by the facility connection requirements are part of a line that cannot add any other connections without coordination with HHGT and without HHGT's permission. During the period of non-compliance, no requests for interconnection or additions were made to HHGT's transmission line. | 10/15/2009 (when HHGT was registered as a TO and the Standard became mandatory and enforceable) | 5/25/2010 (Mitigation Plan completion) | $14,000 (for TRE201100384, TRE201100385, TRE201100563 and TRE201100386) | Self-Certification | In accordance with its Mitigation Plan, HHGT developed and issued a facility connection requirements document, which addresses FAC-001-1 R1. | 2010-05-25 | 2012-04-18 | Neither Admits nor Denies | Texas RE considered the presence and the quality of HHGT's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. HHGT is a wholly-owned indirect subsidiary of NextEra Energy Resources, LLC (NEER), which is a subsidiary of NextEra Energy. Texas RE determined that HHGT's ICP is overseen by the Senior Vice President of Internal Audit and Corporate Compliance, who reports to NextEra Energy's CEO and has access to the Board of Directors of NextEra Energy. Also, the Senior Vice President and the Director of Internal Audit and Corporate Compliance often meet with senior management to discuss and address issues associated with the ICP. Each year, NextEra Energy has conducted workshops and training on the ICP and NERC Reliability Standards compliance. The level of training depends on the responsibilities of the individual.
Texas Reliability Entity, Inc. (Texas RE) | Horse Hollow Generation Tie, LLC (HHGT) | NCR10392 | TRE201100385 | Settlement Agreement | On September 2, 2010, HHGT submitted its Self-Certification for FAC-001-0 and then submitted a Self-Report for FAC-001-0 R2 on September 14, 2010. Following a review of HHGT's Self-Certification and Self-Reports for FAC-001-0 R1 and R2, Texas RE determined that HHGT, as a Transmission Owner (TO), violated FAC-001-0 R2 because it failed to have a facility connections requirements document per R1 until May 25, 2010 and therefore HHGT's facility connection requirements did not address the items included in R2.1 to R2.1.16 of this Standard until May 25, 2010. | FAC-001-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). Although HHGT did not document, maintain and publish facility connection requirements during the violation period, the interconnection point linking HHGT's 345 kV line to another entity's substation had adequate facility connection requirements. In addition, the risk was reduced by the fact that the facilities not addressed by the facility connection requirements are part of a line that cannot add any other connections without coordination with HHGT and without HHGT's permission. During the period of non-compliance, no requests for interconnection or additions were made to HHGT's transmission line. | 10/15/2009 (when HHGT was registered as a TO and the Standard became mandatory and enforceable) | 5/25/2010 (Mitigation Plan completion) | $14,000 (for TRE201100384, TRE201100385, TRE201100563 and TRE201100386) | Self-Certification | In accordance with its Mitigation Plan, HHGT developed and issued a facility connection requirements document, which addresses FAC-001-1 R2. | 2010-05-25 | 2012-04-18 | Neither Admits nor Denies | Texas RE considered the presence and the quality of HHGT's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. HHGT is a wholly-owned indirect subsidiary of NextEra Energy Resources, LLC (NEER), which is a subsidiary of NextEra Energy. Texas RE determined that HHGT's ICP is overseen by the Senior Vice President of Internal Audit and Corporate Compliance, who reports to NextEra Energy's CEO and has access to the Board of Directors of NextEra Energy. Also, the Senior Vice President and the Director of Internal Audit and Corporate Compliance often meet with senior management to discuss and address issues associated with the ICP. Each year, NextEra Energy has conducted workshops and training on the ICP and NERC Reliability Standards compliance. The level of training depends on the responsibilities of the individual.
Texas Reliability Entity, Inc. (Texas RE) | Horse Hollow Generation Tie, LLC (HHGT) | NCR10392 | TRE201100563 | Settlement Agreement | On September 2, 2010, HHGT submitted its Self-Certification for FAC-001-0. Following a review of HHGT's Self-Certification and Self-Reports for FAC-001-0 R1 and R2, Texas RE determined that HHGT, as a Transmission Owner (TO), violated FAC-001-0 R3 because it failed to have a facility connections requirement document as per R1 and R2 until May 25, 2010, and therefore failed to maintain and update its facility connection requirements, as required by R3. | FAC-001-0 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). Although HHGT did not document, maintain and publish facility connection requirements during the violation period, the interconnection point linking HHGT's 345 kV line to another entity's substation had adequate facility connection requirements. In addition, the risk was reduced by the fact that the facilities not addressed by the facility connection requirements are part of a line that cannot add any other connections without coordination with HHGT and without HHGT's permission. During the period of non-compliance, no requests for interconnection or additions were made to HHGT's transmission line. | 10/15/2009 (when HHGT was registered as a TO and the Standard became mandatory and enforceable) | 5/25/2010 (Mitigation Plan completion) | $14,000 (for TRE201100384, TRE201100385, TRE201100563 and TRE201100386) | Self-Certification | In accordance with its Mitigation Plan, HHGT developed and issued a facility connection requirements document, which addresses FAC-001-1 R3. | 2010-05-25 | 2012-04-18 | Neither Admits nor Denies | Texas RE considered the presence and the quality of HHGT's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. HHGT is a wholly-owned indirect subsidiary of NextEra Energy Resources, LLC (NEER), which is a subsidiary of NextEra Energy. Texas RE determined that HHGT's ICP is overseen by the Senior Vice President of Internal Audit and Corporate Compliance, who reports to NextEra Energy's CEO and has access to the Board of Directors of NextEra Energy. Also, the Senior Vice President and the Director of Internal Audit and Corporate Compliance often meet with senior management to discuss and address issues associated with the ICP. Each year, NextEra Energy has conducted workshops and training on the ICP and NERC Reliability Standards compliance. The level of training depends on the responsibilities of the individual.
Texas Reliability Entity, Inc. (Texas RE) | Horse Hollow Generation Tie, LLC (HHGT) | NCR10392 | TRE201100386 | Settlement Agreement | On September 2, 2010, HHGT submitted its Self-Certification for FAC-009-1 and then submitted a Self-Report for FAC-009-1 R1 on September 14, 2010. Following a review of HHGT's Self-Certification and Self-Report, Texas RE determined that HHGT, as a Transmission Owner (TO), did not have Facility Ratings for two Facilities that were consistent with its Facility Ratings Methodology, in violation of FAC-009-1 R1. The two Facilities comprise 100% of HHGT's Facilities. Once this instance of noncompliance was discovered, HHGT rerated the Facilities in accordance with its Facility Ratings Methodology on August 12, 2010. Electric Reliability Council of Texas (ERCOT), which serves as the Independent System Operator in the area covering HHGT's service territory, was notified of the revised Ratings of HHGT's Facilities on September 20, 2010. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the Facility Ratings that were inconsistent with HHGT's Facility Ratings Methodology were more conservative than the correct Facility limits of 925 MVA, thereby reducing the risk to the BPS to minimal. The Facilities are two 345 kV transmission lines, connected through a reactive compensation station to a radially-fed wind generation Facility. The most limiting element for this configuration has a normal rating of 925 MVA, and HHGT re-rated the lines at that level after it discovered this instance of noncompliance. The lines were energized on October 15, 2009 with an operational limit of 650 MVA until the series reactive compensation equipment installation and reactive power studies could be completed. The transmission lines' Ratings were increased to 720 MVA on January 8, 2010 after commissioning of the series reactive compensation equipment. Also, HHGT notified ERCOT of the revised Ratings, as required by ERCOT's rules, on September 20, 2010, thereby further reducing the risk to the BPS. Finally, there is no evidence suggesting that the normal Rating of 925 MVA for these lines was exceeded at any time during the period of the violation. In fact, HHGT was operating below the correct Facility limits of 925 MVA under the direction of ERCOT. | 10/15/2009 (when HHGT was registered as a TO and the Standard became mandatory and enforceable) | 8/12/2010 (when HHGT rerated the Facilities) | $14,000 (for TRE201100384, TRE201100385, TRE201100563 and TRE201100386) | Self-Certification | In accordance with its Mitigation Plan, HHGT rerated the two lines at issue and all Ratings were documented in a consistent manner. The new ratings were submitted to ERCOT as required by ERCOT's rules. | 2010-09-20 | 2012-03-08 | Neither Admits nor Denies | Texas RE considered the presence and the quality of HHGT's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. HHGT is a wholly-owned indirect subsidiary of NextEra Energy Resources, LLC (NEER), which is a subsidiary of NextEra Energy. Texas RE determined that HHGT's ICP is overseen by the Senior Vice President of Internal Audit and Corporate Compliance, who reports to NextEra Energy's CEO and has access to the Board of Directors of NextEra Energy. Also, the Senior Vice President and the Director of Internal Audit and Corporate Compliance often meet with senior management to discuss and address issues associated with the ICP. Each year, NextEra Energy has conducted workshops and training on the ICP and NERC Reliability Standards compliance. The level of training depends on the responsibilities of the individual.
Western Electricity Coordinating Council (WECC) | Grand Coulee Project Hydroelectric Authority (GCPHA) | NCR10043 | WECC201102937 | Settlement Agreement | On August 31, 2011, GCPHA, as a Generator Owner (GO), self-reported a violation of FAC-008-1 R1 for referring to "mechanical and electrical equipment" in general and not specifically identifying the terminal equipment to be included in the Facility Ratings Methodology (FRM). Additionally, GCPHA reported that its FRM did not adequately address the Emergency Ratings. Therefore, WECC determined that GCPHA violated FAC-008-1 R1 for not specifically identifying the terminal equipment that needs to be included in the FRM, and not addressing the Emergency Ratings adequately. | FAC-008-1 | R1 | Medium | High | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although GCPHA's FRM does not specifically identify terminal equipment, GCPHA does have a FRM in place that refers to mechanical and electrical equipment. Additionally, GCPHA's Methodology (FRM) rates all terminal equipment based on the manufacturer's nameplate rating. Further, the risk was reduced by the fact that GCPHA does not operate either of its two NERC registered plants according to emergency ratings, and therefore, the lack of calculated Emergency Ratings posed a minimal risk to the BES. Additionally, this is a hydro facility that does not operate in emergency conditions. | 8/23/2007 (when GCPHA registered as a GO) | 9/30/2011 (Mitigation Plan Completion) | $11,500 (for WECC201102937, WECC201102938, WECC201102939, and WECC201102940) | Self- Report | In accordance with its Mitigation Plan, GCPHA revised its FRM to address terminal equipment and Emergency Ratings methodology. | 2011-09-30 | 2012-04-09 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Grand Coulee Project Hydroelectric Authority (GCPHA) | NCR10043 | WECC201102938 | Settlement Agreement | On August 31, 2011, GCPHA, as a Generator Owner (GO), self-reported a violation of FAC-009-1 R1 because it did not document Facility Ratings that fully demonstrated that GCPHA had established Facility Ratings consistent with the associated Facility Ratings Methodology (FRM). Specifically, although individual equipment and facility ratings were known, Facility Rating tables documenting the rating of all equipment had not been developed. Therefore, WECC determined that GCPHA violated FAC-009-1 R1 for failure to establish Facility Ratings for its jointly and solely owned facilities that are consistent with the associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because during the period of this violation, GCPHA had all of its nameplate Ratings in the Facility but failed to document the Rating of all equipment in the facility. | 8/23/2007 (when GCPHA registered as a GO) | 9/30/2011 (Mitigation Plan Completion) | $11,500 (for WECC201102937, WECC201102938, WECC201102939, and WECC201102940) | Self- Report | GCPHA completed the development of Facility Ratings for all its facilities, including all equipment components, that are consistent with the associated FRM. | 2011-09-30 | 2012-04-13 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Grand Coulee Project Hydroelectric Authority (GCPHA) | NCR10043 | WECC201102939 | Settlement Agreement | On August 31, 2011, GCPHA self-reported a violation to WECC stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R1 because although its Protection System maintenance and testing program (Program) included a biennial interval for the maintenance and testing of its relays, the Program did not specify a basis for the interval. Additionally, the Program contained maintenance and testing requirements for its Current Transformers (CT) and Potential Transformers (PT), but it did not specify maintenance and testing interval or basis for these CTs and PTs. Lastly, the Program contained a biennial interval for the maintenance and testing for its DC (Direct Current) circuitry, but it did not specify a basis for the interval for those devices as well. Therefore, WECC determined that GCPHA was in violation of PRC-005-1 R1.1 for failing to include in its Protection System maintenance and testing program (i) a basis for its relay maintenance and testing interval, (ii) maintenance and testing intervals and basis for its CTs and PTs, and (iii) a basis for its DC circuitry maintenance and testing interval. | PRC-005-1 | R1; R1.1 | High | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although GCPHA's Protection System maintenance and testing program did not define the interval and basis for its PT and CT maintenance and testing, GCPHA routinely (at least once a year) conducts switchyard inspections that include checking CTs and PTs for insulator problems, oil leaks, and periodic infrared inspections. GCPHA also had alarms in place which reduced the risk to minimal. Additionally, internal CTs are routinely inspected during maintenance and testing on the associated piece of equipment such as a generator, transformer, circuit breaker or enclosed cubicle bus work. Also, although GCPHA did not specify the basis for its maintenance and testing interval of relays, it partially complied with this Standard by defining the interval as two years. Further, the generation involved in this violation is seasonal and on-line for only seven out of 12 months, and is not essential to mitigate voltage, frequency or stability constraints, and is not a "blackstart" unit or included in any regional restoration plan, which reduced the risk to the BPS to minimal. | 8/23/2007 (when GCPHA registered as a GO) | 9/1/2011 (Mitigation Plan completion) | $11,500 (for WECC201102937, WECC201102938, WECC201102939, and WECC201102940) | Self- Report | GCPHA completed the update to its Protection System Maintenance and Testing Program to include missing program elements, including interval basis determination for relays and DC Circuitry, as well as interval and basis for CTs and PTs. | 2011-09-01 | 2012-04-20 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Grand Coulee Project Hydroelectric Authority (GCPHA) | NCR10043 | WECC201102940 | Settlement Agreement | On August 31, 2011, GCPHA self-reported a violation to WECC stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2 because it failed to perform required maintenance and testing within its defined intervals for all its Potential Transformers (PT) and Current Transformers (CT), as well as 48 of 59 (81.4%) of its DC (Direct Current) circuitry. Additionally, GCPHA failed to provide the date when 39 of 59 (66.1%) of its DC Circuitry devices were last tested. Therefore, WECC determined that GCPHA violated PRC-005-1 R2.1 for failing to perform required maintenance and testing of its PTs and CTs, and R2.2 for not being able to provide a record that it performed functional tripping tests on its DC circuitry. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power systems (BPS) because GCPHA routinely (at least once a year) conducts switchyard inspections that include checking CTs and PTs for insulator problems and oil leaks and periodic infrared inspections. GCPHA also had alarms in place which reduced the risk to minimal. Additionally, internal CTs are routinely inspected during maintenance and testing on the associated piece of equipment such as a generator, transformer, circuit breaker or enclosed cubicle bus work. Lastly, the generation involved in this violation is seasonal and on-line for only 7 out of 12 months and is not essential to mitigate voltage, frequency or stability constraints, and is not a "blackstart" unit or included in any regional restoration plan, which reduced the risk to the BPS to minimal. | 8/23/2007 (when GCPHA registered as a GO) | 12/15/2011 (Mitigation Plan completion) | $11,500 (for WECC201102937, WECC201102938, WECC201102939, and WECC201102940) | Self- Report | GCPHA completed the following mitigation activities: 1) Completed the required maintenance and testing on all voltage and current sensing devices; and 2) Completed maintenance and testing on all DC circuitry; and 3) Completed review of program implementation to minimize the probability of reoccurrence in the future. | 2011-12-15 | 2012-04-09 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LADWP) | NCR05223 | WECC201002376 | Settlement Agreement | On October 8, 2010, LADWP submitted a Periodic Data Submittal for the period covering the Third Quarter of 2010. WECC reviewed the Periodic Data Submittal during an on-site Compliance Audit conducted from January 17, 2011 to January 28, 2011. WECC reviewed LADWP's compliance with BAL-002-0 R4 for the periods not addressed in the Third Quarter 2010 Periodic Data Submittal and determined the only instance of noncompliance occurred during the Third Quarter of 2010. WECC found that LADWP, as a Balancing Authority, was in violation of BAL-002-0 R4 because LADWP failed to meet its Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of LADWP's Reportable Disturbances. LADWP calculated its disturbance control performance to determine its Disturbance Recovery Criterion for the Third Quarter of 2010. LADWP reported it had three reportable disturbances. LADWP appropriately returned its Area Control Error (ACE) to pre-disturbance levels for two of the three reported disturbances. For the third Reportable Disturbance occurring on July 17, 2010, LADWP did not return the ACE to its pre-disturbance level within 15 minutes. Specifically, on July 17, 2010, the Haynes Generating Station Unit 5 tripped off from the LADWP system resulting in a loss of 282 MW (277 net MW). The LADWP System Operator responded to this contingency and recovered 212 MW within five minutes of the disturbance, leaving 65 MW to get the ACE back to zero. However, LADWP was not able to return to the pre-disturbance value within the default 15 minute Disturbance Recovery period. LADWP discovered its average recovery was 95.44%, instead of the required 100%, of its Disturbance Control Standard (DCS). LADWP took 26 minutes to return its ACE to zero, causing LADWP to meet only 96.51% of its DCS for the Third Quarter of 2010. | BAL-002-0 | R4; R4.1; R4.2 | Medium | Lower | This violation posed a minimal, and not serious or substantial risk to the reliability of the bulk power system (BPS). DCS is limited to the loss of supply and does not apply to the loss of load. LADWP lost 277 net MW of generating capability. LADWP had contingency reserves available to cover the generating loss. Further, LADWP recovered approximately 212 MW within five minutes of the disturbance, leaving approximately 65 MW to get its ACE back to zero. LADWP is a single municipal system located in large part within the footprint of an Independent System Operator (ISO), although LADWP is not part of the ISO. The loss of the generating capability represented a fraction of the amount of generation available to LADWP. Further, 65 MW represents an even smaller fraction of the generation available to LADWP. Such a fraction of generation is not likely to present challenges to the transmission lines feeding the LADWP system. Finally, LADWP had more than 1,000 MW of Contingency Reserves available during the disturbance and has a total generating capacity of approximately 7,266 MW. | 7/17/2010 (when LADWP did not return the ACE to its pre-disturbance level within 15 minutes of a Reportable Disturbance) | 7/17/2010 (26 minutes after the Reportable Disturbance when LADWP returned the ACE to its pre-disturbance level) | $60,000 (for WECC201002376; WECC201102388; WECC201002352; WECC201002353; and WECC201002387) | Periodic Data Submittal | LADWP determined the cause of the violation in this case was human error. Therefore LADWP re-trained its System Operators on the requirements of BAL-004 R4 and "reinforced its procedures by training its System Operators... to make sure they fully understand the LADWP balancing authority operating protocols to recover to the pre-disturbance ACE value within the 15 minutes." | 2011-03-08 | 2011-11-16 | Agrees/ Stipulates | WECC considered LADWP's Internal Compliance Program (ICP) to be a mitigating factor. WECC has reviewed LADWP's ICP on four occasions and notes that LADWP has shown continuous improvement and commitment to its ICP. Specifically, WECC found that: LADWP's ICP is documented; the ICP is disseminated throughout its operations; LADWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LADWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LADWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LADWP reviews and modifies its ICP regularly; LADWP's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LADWP's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LADWP) | NCR05223 | WECC201102388 | Settlement Agreement | From January 17, 2011 to January 28, 2011 WECC conducted an on-site Compliance Audit of LADWP. During and prior to the Compliance Audit, WECC reviewed: LADWP's Transmission Vegetation Management Program (TVMP) (December 2009 version 1.1, and December 27, 2010 version), Transmission Line Vegetation Management Work Plan 2010, LADWP Transmission Vegetation Management Personnel Qualifications, Specification 165 Detailed Requirements (Specification 165), a list of all LADWP transmission lines operated at or above 200 kV and a list of lower voltage lines designated by WECC as critical to the reliability of the Western Interconnection. WECC found that LADWP, as a Transmission Owner, was in violation of FAC-003-1 R1 because LADWP defined Clearance 1 (R1.2.1) and Clearance 2 (R1.2.2) distances inconsistently between the TVMP and the Transmission Line Vegetation Management Work Plan 2010. During the Audit, WECC requested that LADWP explain why the LADWP TVMP Clearance 1 distance is 25 feet (for lines at 230 kV) and 40 feet (for lines above 230 kV) and the LADWP Specification 165 document uses Clearance 1 distances of 15 feet and 30 feet, respectively. LADWP personnel clarified that the entity considers the Specification 165 document a contract with its vegetation management contractor (dated March 12, 2010), and the contract included old wording from a previous contract and had not been updated. WECC submitted a data request asking LADWP to provide documentation that demonstrates that LADWP personnel and contractors responsible for implementing the annual TVMP work plan know and manage to the appropriate clearances. LADWP provided its LADWP Transmission Line Vegetation Management Record with a final inspection date of February 17, 2010. WECC determined this document did not demonstrate compliance with R1.2.1 or R1.2.2, but rather added an additional instance of LADWP not describing and documenting its Clearance distances. WECC determined LADWP's documentation (including its TVMP, transmission vegetation inspection and corrective actions records, and Vegetation Management Services for Power Line Clearance contract specifications) inconsistently defined minimum Clearance 1 (R1.2.1) and Clearance 2 (R1.2.2) distances. Therefore, the WECC determined LADWP had a violation of FAC-003-1 R1 (specifically R1.2.1 and R1.2.2). | FAC-003-1 | R1; R1.2.1; R1.2.2 | High | Moderate | This violation posed a minimal, and not serious or substantial risk to the reliability of the bulk power system (BPS). Although LADWP submitted documents demonstrating that Clearance 1 and Clearance 2 distances were defined inconsistently between the TVMP and Annual Vegetation Management Work Plan, the potential risk is mitigated in this instance because, while implementing its Annual Vegetation Management Work Plans, LADWP inspects its transmission lines using a radial Clearance 2 distance that was greater than the Institute of Electrical and Electronics Engineers (IEEE) minimum approach distance to prevent flashover under all rated operating conditions. In addition, LADWP trimmed or removed vegetation in or adjacent to its Transmission Rights-of-Way to the greatest Clearance 1 specified in its TVMP. Therefore, WECC determined that this violation is primarily documentation in nature. LADWP established several Clearance 1 and Clearance 2 distances, established Clearances within general utility practices and, further, implemented its vegetation management program using such utility practices. | 3/12/2010 (the date the Transmission Line Vegetation Management Work Plan and the vegetation management contract contained inaccuracies with respect to the Clearance distances) | 3/8/2011 (Mitigation Plan completion) | $60,000 (for WECC201002376; WECC201102388; WECC201002352; WECC201002353; and WECC201002387) | Audit | LADWP reviewed the inconsistencies between its documents and provided explanations for such inconsistencies. LADWP provided training to all LADWP employees involved in vegetation management work, including the current TVMP and its required clearances. | 2011-03-08 | 2011-09-30 | Agrees/ Stipulates | The filed Violation Severity Level (VSL) for this Standard and Requirement is "Severe." WECC determined a "Moderate" VSL is appropriate. WECC determined "Moderate" is appropriate for the following reasons: 1. LADWP in all cases implemented Clearance 1 and Clearance 2 distances greater than the IEEE minimum approach distance to prevent flashover under all rated operating conditions; 2. LADWP trimmed or removed vegetation in or adjacent to its Transmission Rights-of- Way to the greatest Clearance 1 specified in its TVMP; 3. LADWP established Clearance 1 and Clearance 2 distances in its TVMP; 4. Although different than the TVMP, the entity established Clearance 1 and Clearance 2 distances in its annual work plan; and 5. Although different than the TVMP, the entity established Clearance 1 and Clearance 2 distances in its contract with its vegetation management service provider. WECC considered LADWP's Internal Compliance Program (ICP) to be a mitigating factor. WECC reviewed LADWP's ICP on four occasions and notes LADWP has shown continuous improvement and commitment to its ICP. Specifically, WECC found that: LADWP's ICP is documented; the ICP is disseminated throughout its operations; LADWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LADWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LADWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LADWP reviews and modifies its ICP regularly; LADWP's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LADWP's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LADWP) | NCR05223 | WECC201002352 | Settlement Agreement | On December 30, 2010, LADWP submitted a Self-Report to WECC stating that as a Transmission Owner, Distribution Provider, and Generator Owner, it was in violation of PRC-005-1 R2.1 because certain maintenance and testing activities for batteries related to Protection Systems did not occur within the defined interval (every three months, with six weeks of delay allowed), and documentation of such activities could not be found. WECC determined the scope of the violation is limited to LADWP's station batteries. LADWP missed its maintenance interval for 24 of its 110 station batteries, representing approximately 22 percent of LADWP’s total Protection System batteries. The violation is limited to missed or undocumented quarterly inspections. WECC determined LADWP has 110 batteries supporting its Protection System schemes and LADWP could not demonstrate that it maintained or tested 24 of such batteries according to LADWP's quarterly testing interval for station batteries; therefore WECC Enforcement determined LADWP had a violation of PRC-005-1 R2, specifically R2.1. | PRC-005-1 | R2.1 | High | Lower | This violation posed a minimal, and not serious or substantial risk to the reliability of the bulk power system (BPS). During the violation period, LADWP conducted 480 quarterly inspections out of the 499 scheduled inspections on 110 battery banks. Three inspections were late, three inspections were not properly documented, and 13 were missed. The 19 out of total 499 inspections represent 3.8% of the total scheduled inspections. Thus, LADWP conducted over 95 percent of its scheduled quarterly battery inspections of LADWP's total Protection System batteries. The violation is limited to missed or undocumented quarterly inspections. Further, LADWP has alarms on its station batteries, including the 24 related to this violation. LADWP also takes a conservative approach with regard to station battery use. Specifically, LADWP replaces its station batteries when a battery is run down to 60% of its conductivity. LADWP monitors for such situations. LADWP's Energy Control Center continuously monitors the status of each battery and immediately responds to the alarms described above. LADWP personnel take immediate action if a battery triggers an alarm. | 11/8/2009 (the first missed maintenance date for the battery) | 12/30/2010 (when LADWP maintained and tested the station batteries associated with this violation) | $60,000 (for WECC201002376; WECC201102388; WECC201002352; WECC201002353; and WECC201002387) | Self-Report | LADWP implemented improvements to its battery compliance monitoring process to better track completion of battery maintenance and testing. LADWP updated its ISS Regulatory Stationary Battery Policy, which included updates to existing policies, and new policies, to improve oversight and controls of battery maintenance activities. LADWP conducted training meetings with supervisors and staff directly involved with battery maintenance and testing to reinforce policies and procedures as documented in the ISS Regulatory Stationary Battery Policy. | 2011-02-02 | 2011-03-11 | Agrees/ Stipulates | LADWP had previous violations of PRC-005-1 R2. LADWP's one violation resulted from LADWP's failure to maintain and test Protection System relays and associated communication systems that LADWP did not initially determine were subject to PRC-005-1. LADWP had another violation resulted from LADWP missing its interval on a single back-up Protection System relay. WECC determined and applied mitigating credit to LADWP because it takes a conservative approach with regard to its station battery use. Specifically, LADWP replaces its station batteries when a battery is run down to 60% of its conductivity. LADWP monitors for such situations. LADWP's Energy Control Center continuously monitors the status of each battery and immediately responds to the alarms described above. LADWP personnel take immediate action if a battery triggers an alarm. WECC applied only partial aggravation for the prior violations because the present violation is different in nature from LADWP's previous assessed violations of the standard. The present violation relates to LADWP's failure to maintain and test batteries. The LADWP maintenance and testing team responsible at the time of the violation for inspecting batteries was a distinct team from the relay maintenance group. Therefore, the prior violations which involved relays involved different staff from a different department than the staff that was involved with the current violations regarding the batteries. WECC considered LADWP's Internal Compliance Program (ICP) to be a mitigating factor. WECC has reviewed LADWP's ICP on four occasions and notes LADWP has shown continuous improvement and commitment to its ICP. Specifically, WECC found that: LADWP's ICP is documented; the ICP is disseminated throughout its operations; LADWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LADWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LADWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LADWP reviews and modifies its ICP regularly; LADWP's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LADWP's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LADWP) | NCR05223 | WECC201002353 | Settlement Agreement | On December 30, 2010, LADWP submitted a Self-Report to WECC stating that as a Transmission Owner and Distribution Provider, it was in violation of PRC-008-0 R2 because certain maintenance and testing activities for batteries related to the Underfrequency Load Shedding (UFLS) relay equipment did not occur within the defined interval (every three months, with six weeks of delay allowed), and documentation of such activities could not be found. WECC determined the scope of the violation is limited to LADWP's UFLS Protection System batteries. LADWP has 41 batteries supporting its UFLS schemes, and LADWP could not demonstrate that it maintained or tested ten such batteries according to LADWP's quarterly testing interval for UFLS Protection System batteries; therefore, WECC determined LADWP had a violation of PRC-008-0 R2. | PRC-008-0 | R2 | Medium | Lower | This violation posed a minimal, and not serious or substantial risk to the reliability of the bulk power system (BPS). LADWP conducted 172 quarterly inspections out of 178 scheduled inspections on 41 battery banks. The six out of 178 inspections represent 3.4% of the total scheduled inspections. Thus, LADWP conducted over 95% of its scheduled quarterly battery inspections of UFLS Protection System batteries. The violation is limited to missed or undocumented quarterly inspections. Further, LADWP has alarms on its UFLS Protection System batteries, including the ten batteries related to this violation. LADWP also takes a conservative approach with regard to station battery use. Specifically, LADWP replaces its station batteries when a battery is run down to 60% of its conductivity. LADWP monitors for such situations. LADWP's Energy Control Center continuously monitors the status of each battery and immediately responds to the alarms described above. LADWP personnel take immediate action if a battery triggers an alarm. | 11/8/2009 (the first missed maintenance date for the battery) | 12/30/2010 (when LADWP maintained and tested the batteries related to the UFLS relay equipment) | $60,000 (for WECC201002376; WECC201102388; WECC201002352; WECC201002353; and WECC201002387) | Self-Report | LADWP implemented improvements to its battery compliance monitoring process to better track completion of battery maintenance and testing. LADWP updated its ISS Regulatory Stationary Battery Policy, which included updates to existing policies, and new policies, to improve oversight and controls of battery maintenance activities. LADWP conducted training meetings with supervisors and staff directly involved with battery maintenance and testing to reinforce policies and procedures as documented in the ISS Regulatory Stationary Battery Policy. | 2011-02-02 | 2011-06-27 | Agrees/ Stipulates | WECC determined and applied mitigating credit to LADWP because it takes a conservative approach with regard to its station battery use. Specifically, LADWP replaces its station batteries when a battery is run down to 60% of its conductivity. LADWP monitors for such situations. LADWP's Energy Control Center continuously monitors the status of each battery and immediately responds to the alarms described above. LADWP personnel take immediate action if a battery triggers an alarm. WECC considered LADWP's Internal Compliance Program (ICP) to be a mitigating factor. WECC has reviewed LADWP's ICP on four occasions and notes that LADWP has shown continuous improvement and commitment to its ICP. Specifically, WECC found that: LADWP's ICP is documented; the ICP is disseminated throughout its operations; LADWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LADWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LADWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LADWP reviews and modifies its ICP regularly; LADWP's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LADWP's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LADWP) | NCR05223 | WECC201002387 | Settlement Agreement | On November 9, 2010, LADWP submitted a Self-Report to WECC stating that as a Generator Operator, it was in violation of VAR-002-1.1b R3 because LADWP plant operators did not notify the Transmission Operator (TOP) of the change in status of the Automatic Voltage Regulator (AVR) within 30 minutes of the change. On September 30, 2010 at approximately 09:08 hours, LADWP's Unit 3 at the Castaic Power Plant was not able to maintain a set voltage with the AVR in service. Specifically, the unit's voltage set-point was 17.6 kV but the voltage was swinging between 17.3 kV and 17.6 kV. LADWP's Generator Operator switched the AVR to Current Control, disabling the AVR; this was an immediate unavoidable removal which was why WECC did not pursue an R1 violation . Upon making this change, the Unit 3 voltage stabilized at 17.6 kV. LADWP did not notify its TOP of the change in status until October 7, 2010. Therefore, WECC determined LADWP was in violation of VAR-002-1.1b R3 due to the status change on a generator Reactive Power resource and its failure to notify the TOP of the status change. | VAR-002-1.1b | R3 | Medium | Lower | This violation posed a minimal, and not serious or substantial risk to the reliability of the bulk power system (BPS). Although the unit operated with the AVR out of service for approximately one week, LADWP had to change the status of the AVR to ensure the unit maintained a stable voltage output. As soon as LADWP noticed that the set-point was swinging, LADWP took immediate action to maintain a reliable set-point. Further, the Castaic Unit 3 has a rated capacity of approximately 250 MW; it is one unit within LADWP's Castaic Power Plant. The Castaic Power Plant has a rated capacity of approximately 1,250 MW. Therefore the violation relates to a small amount of generation available to the Generator Operator and an even smaller amount of generation available to the TOP. | 9/30/2010 (when LADWP failed to notify its TOP within 30 minutes of the change in AVR) | 10/7/2010 (when LADWP notified its TOP of the change in AVR) | $60,000 (for WECC201002376; WECC201102388; WECC201002352; WECC201002353; and WECC201002387) | Self-Report | LADWP’s Castaic Power Plant Operations Supervisor immediately distributed a memorandum to all Castaic Power Plant control room operators to reinforce the importance of maintaining operations of a Castaic Unit under AVR control, and to immediately notify the Energy Control Center (ECC) whenever a Unit is not operating on AVR. The memorandum was updated to specify that the ECC is to be notified within 30 minutes whenever a Unit is not operating on AVR. Training was completed for all Castaic Power Plant control room operators on the instructions specified in the memoranda. | 2010-11-07 | 2011-02-24 | Agrees/ Stipulates | WECC considered LADWP's Internal Compliance Program (ICP) to be a mitigating factor. WECC has reviewed LADWP's ICP on four occasions and notes LADWP has shown continuous improvement and commitment to its ICP. Specifically, WECC found that: LADWP's ICP is documented; the ICP is disseminated throughout its operations; LADWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LADWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LADWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LADWP reviews and modifies its ICP regularly; LADWP's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LADWP's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 2 of Grant County (GCPD) | NCR05342 | WECC2012009226 | Settlement Agreement | On November 1, 2011, WECC notified GCPD that WECC was initiating the Self-Certification process for the period from January 1, 2011 to December 31, 2011. Under this process, GCPD's Self-Certification submittal was due by January 20, 2012. On January 18, 2012, GCPD self-reported a violation of PRC-005-1a R2. On January 19, 2012, GCPD submitted its Self-Certification. Specifically, GCPD reported that it did not have battery testing records consistent with intervals prescribed in its maintenance and testing program. As a Transmission Owner, Generator Owner and Distribution Provider, GCPD is subject to PRC-005-1a R2. On February 2, 2012 a WECC subject matter expert (SME) reviewed GCPD's Self-Certification and determined that GCPD was in violation of PRC-005-1a R2.1 for failing to maintain and test its Wanapum Station 1 battery bank within its program-defined battery interval. GCPD's Protection System maintenance and testing program states that maintenance and testing on station battery systems shall be performed every six months with a 25% (approximately 45-day) grace period. GCPD's facilities consist of 52 substations, of which 46 are distribution substations and six are transmission substations, each of which contains one or more battery banks (58 battery banks in total). The Wanapum Station 1 battery bank was the only battery bank that GCPD reported was not tested or maintained within its defined interval (1.7% of total applicable devices). GCPD's Wanapum Station 1 battery bank was last tested on May 12, 2011. The next test should have occurred no later than December 27, 2011; however, GCPD did not complete the test until January 10, 2012. As a result, the SME determined GCPD's failure to maintain and test the Wanapum Station 1 battery bank within its defined interval is a violation of PRC-005-1a R2.1. WECC Enforcement reviewed the Self-Certification and the SME's findings. WECC Enforcement determined that GCPD had a violation of PRC-005-1a R2.1 for failing to maintain and test the Wanapum Station 1 battery bank interval defined in its maintenance and testing program. WECC Enforcement further determined that GCPD was in violation of PRC-005-1a R2.1 from December 27, 2011, when GCPD missed the interval, until the present, because it has not fully mitigated the violation by completing its Mitigation Plan; however, the Wanapum Station 1 battery bank was maintained and tested on January 10, 2012; therefore, the battery maintenance was ultimately completed 14 days late. | PRC-005-1a | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although GCPD could not provide evidence that the battery bank at the Wanapum Station 1 substation was maintained and tested within its defined interval, GCPD has performed most of its maintenance and testing in accordance with its maintenance and testing program. GCPD's facilities consist of 52 substations, of which 46 are distribution substations and six are transmission substations, each of which contains one or more battery banks (58 battery banks in total). The Wanapum Station 1 battery bank, which represents 1.7% of all applicable devices, was the only battery bank that GCPD reported was not tested or maintained within its defined interval. GCPD compliance staff conducts visual inspections of the batteries at issue on regular basis, thereby further reducing the risk to the BPS. In addition, GCPD compliance staff performs routine reviews of maintenance scheduled to ensure testing is completed in accordance with defined intervals. However, the previous maintenance of the battery bank at issue occurred earlier than anticipated, which moved the next test date up in the testing schedule. Had the previous maintenance not occurred earlier than scheduled, the single battery bank would have been tested on time, within the defined maintenance interval. Although GCPD's personnel did make sure the earlier testing was properly accounted for by the computer system, GCPD's compliance staff failed to ensure that testing was done in accordance with the defined intervals. At the time of the violation, and currently, GCPD operates a task management software system that sends maintenance and testing alerts to identified personnel. However, if a test occurred earlier than anticipated, the task software system was designed to remind GCPD personnel of the next test date without properly accounting for earlier testing. Finally, WECC determined that the short period of the violation further mitigated the risk to the BPS, because testing was late 14 days. | 12/27/2011 (when GCPD failed to maintain and test the Wanapum Station 1 battery bank) | 1/10/2012 (when the battery bank was tested/ maintained) | 4500 | Self-Certification | GCPD performed testing and maintenance on the battery bank on January 10, 2012. GCPD's Mitigation Plan required it to: 1. Update existing maintenance reports to facilitate improved scheduling procedures; and 2. Alter its task management software to alert personnel of upcoming maintenance tasks and better support the maintenance schedule. | 2012-04-18 | 2012-06-15 | Does Not Contest | WECC considered certain aspects of GCPD's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor in the penalty assessment, including the fact that the ICP was well-documented and disseminated throughout its operations staff. Also, the ICP has oversight staff, which is supervised at high levels of the organization, and has independent access to the CEO and the board of directors. WECC determined this was GCPD's second violation of PRC-005 R2. Like the instant violation, in the previous violation, GCPD did not conduct and document all required maintenance and testing of Protection System devices within defined intervals. WECC determined that GCPD’s previous violation of PRC-005-1 R2 constituted a prior violation and an aggravating factor in the penalty determination. Since GCPD self-reported during the Self-Certification period, it did not receive self-reporting credit.
Western Electricity Coordinating Council (WECC) | Simpson Tacoma Kraft Co., LLC (STK) | NCR10303 | WECC201102946 | Settlement Agreement | On September 2, 2011, STK submitted a Self-Certification addressing noncompliance with VAR-002-1.1a R1. STK, as a Generator Operator, stated that when its generator began commercial operation on July 1, 2009, the design for the generator controls included an automatic voltage regulator (AVR). The engineering design for the unit did not, however, provide for the use of the AVR in the automatic voltage control mode. Instead, STK's generator operated in power factor (PF) control mode until June 1, 2011, when a unit outage prompted an engineering redesign to implement controls that would allow the AVR to operate in the automatic voltage control mode. On June 7, 2011 at 13:20 PDT, STK's unit came back online in automatic voltage control mode. WECC determined that STK failed to operate its generator with the AVR in automatic voltage control mode, without notifying its TOP that it was operating in the PF mode. | VAR-002-1.1a | R1 | Medium | Severe | WECC determined the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because STK has always operated within the voltage schedule established by its TOP. In addition, this generator is a steam turbine unit with a capacity of 55 MW. It is the only unit at this plant and its output is relatively small compared to the other generation integrated into the grid in the immediate area by the TOP. | 7/1/2009 (when the generator began operating with its AVR in the incorrect mode) | 6/7/2011 (when the generator began operating its AVR in the correct mode) | $2,500 (for WECC201102946 and WECC201102881) | Self-Certification | Pursuant to its Mitigation Plan, STK designed and installed new AVR controls to allow for operation in automatic voltage control mode. STK operators were also trained to notify the TOP within thirty minutes of a change in AVR operational mode, and were trained on the new control design. | 2012-03-16 | 2012-06-21 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Simpson Tacoma Kraft Co., LLC (STK) | NCR10303 | WECC201102881 | Settlement Agreement | On July 15, 2011, STK submitted a Self-Report addressing noncompliance with VAR-002-1.1b R3. STK, as a Generator Operator, reported that when its generator began commercial operation on July 1, 2009, the design for the generator controls included an automatic voltage regulator (AVR). The engineering design for the unit did not, however, provide for the use of the AVR in the automatic voltage control mode. Instead, STK's generator operated in power factor (PF) control mode until June 1, 2011, when a unit outage prompted an engineering redesign to implement controls that would allow the AVR to operate in the automatic voltage control mode. On June 7, 2011 at 13:20 PDT, the AVR was enabled to automatic voltage control; however, STK failed to notify its Transmission Operator (TOP) of the change in status until July 1, 2011. Thus, WECC determined that STK failed to notify the TOP within 30 minutes of the change in AVR control mode status, as required by the Standard. | VAR-002-1.1b | R3 | Medium | High | WECC determined the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because STK has always operated within the voltage schedule established by its TOP. In addition, this generator is a steam turbine unit with a capacity of 55 MW. It is the only unit at this plant and its output is relatively small compared to the other generation integrated into the grid in the immediate area by the TOP. | 6/7/2011 (when STK switched the status of its AVR from PF to automatic voltage control mode without notifying the TOP of the change in status) | 7/1/2011 (when STK notified the TOP of the generator change in status) | $2,500 (for WECC201102946 and WECC201102881) | Self-Report | Pursuant to its Mitigation Plan, STK retrained operators in its AVR policies and procedures after new AVR controls were installed. | 2012-03-16 | 2012-06-05 | Agrees/ Stipulates
Western Electricity Coordinating Council (WECC) | Southern Montana Electric Generation & Transmission Cooperative, Inc. (SMGT) | NCR05399 | WECC2011008700 | Settlement Agreement | On December 3, 2011, SMGT, as a Generator Owner (GO), self-reported a violation of PRC-005-1 R1. SMGT’s newly-constructed Highwood Generating Station, a 46 MVA generator, was energized on September 7, 2011. It has one 230 kV connection to the bulk power system (BPS). The generation Protection Systems, specifically relays, were tested during commissioning, but SMGT had not created a generation Protection System maintenance and testing program for Protection Systems that affect the reliability of the BPS at the time of its registration as a GO and Generator Operator on September 7, 2011. WECC determined that SMGT was in violation of PRC-005-1 R1 for failing to have a generation Protection System maintenance and testing program for its new Highwood Generating Station. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because of the following factors. SMGT's newly-constructed Highwood Generating Station came online on September 7, 2011, and its generation Protection Systems were tested during commissioning; therefore, for the period from September 7, 2011 (commissioning) to the present, SMGT's generation Protection Systems were properly maintained. All applicable components were recently tested. In addition, SMGT is a generating cooperative with one 46 MVA generator, the Highwood Generating Station. WECC took into account the size and location of the entity in determining that the instant violation posed a minimal risk to the BPS. | 9/7/2011 (when SMGT was registered as a GO) | 5/11/2012 (Mitigation Plan completion) | 1500 | Self-Report | SMGT created a comprehensive Protection System maintenance and testing program according to the requirements of PRC-005-1 R1, including documenting its testing intervals and their bases as required. | 2012-05-11 | 2012-05-25 | Does Not Contest
Western Electricity Coordinating Council (WECC) | Southwest Transmission Cooperative, Inc. (SWTC) | NCR05402 | WECC2011008758 | Notice of Confirmed Violation | On December 15, 2011, SWTC submitted a Self-Report to WECC stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2. SWTC reported that while preparing for its upcoming on-site compliance audit (Audit) scheduled for February 2012, the SWTC Communications, Meter, and Relay Department (CMR) discovered the Sandario Substation battery bank (1 out of 22 SWTC battery banks) had been overlooked and was not tested within its Protection System maintenance and testing program's defined intervals. Consequently, SWTC reported that it did not have battery testing records consistent with intervals prescribed in its Protection System maintenance and testing program. On February 7, 2012, during SWTC’s Audit, the WECC Audit Team reviewed SWTC’s evidence which showed that SWTC had failed to maintain and test the Sandario Substation battery bank and 6 electromechanical relays at the Apache Substation within its program’s defined intervals. Specifically, SWTC’s Protection System maintenance and testing program states battery system testing shall be performed every 12 months with a two-month buffer on either side of the due date (+/- 14 months), and electromechanical relay testing shall be performed every eighteen months with a two-month buffer on either side of the due date (+/- 20 months). The battery bank was last tested and maintained on September 3, 2009, outside of the buffer period. SWTC also reported that a work order was issued for the Sandario Substation battery maintenance on September 3, 2010, within SWTC’s 12-month interval but was not completed until December 27, 2010. Additionally, some of the Apache Substation electromechanical relays were tested on January 1, 2008, and then missed the scheduled testing on July 28, 2009. The 6 electromechanical relays in scope were not tested until February 13, 2010. SWTC was in violation of PRC-005-1 R2.1 for failing to maintain and test the Sandario Substation battery bank within the 12-14 month interval and failing to maintain and test 6 electromechanical relays at the Apache Substation within the 18-20 month interval as defined in its Protection System maintenance and testing program. | PRC-005-1 | R2; R2.1 | High | Moderate | WECC determined the violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SWTC’s failure to maintain and test 6 of the 14 electromechanical relays located at the Apache Substation could result in SWTC failing to properly detect or respond to false operations or other service failures on SWTC’s system. Because the Apache Substation's 14 electromechanical relays represent 18% of SWTC’s total Protection System relays, and the 6 electromechanical relays at the Apache Substation that were not maintained and tested within defined intervals represent 42% of the electromechanical relays at the Apache Substation, failing to maintain and test these 6 electromechanical relays within defined intervals for approximately 200 days put 598 MW of generation at risk of a service or operation failure. The potential risk was mitigated by several factors. SWTC did perform maintenance and testing, albeit inconsistently. The Sandario Substation battery bank was tested 53 days past due and the relays were tested 200 days past due. Although SWTC failed to test 1 of the 22 battery banks within defined intervals, SWTC’s battery systems are monitored continuously through the supervisory control and data acquisition (SCADA) system and Energy Management System (EMS), which issue alarms to the Control System Center if an event was to occur. SWTC’s Sandario Substation is a 115/25 kV substation that delivers customer load to a member distribution cooperative. The peak load of the Sandario Substation in 2010 was 9.7 MW. SWTC's relay systems are also monitored continuously through alarms and the SCADA system and there were no issues found with the Apache Substation relays when tested after the missed testing period. There were no system disturbances that resulted from the missed relay maintenance at the Apache Substation. | First instance: 10/1/2009 (when SWTC missed the 18-20 month relay buffer interval) Second instance: 11/3/2010 (when SWTC missed the 12-14 month battery bank buffer interval) | First instance: 2/13/2010 (when the missed interval was tested/ maintained) Second instance: 12/27/2010 (when the missed interval was tested/ maintained) | 25100 | Self-Report | SWTC’s Mitigation Plan required it to: (1) review the NERC PRC-005-1 Reliability Standard with Planning, Working Foremen and Field Crews; (2) inform and train Planning, Working Foremen and Field Crews of the importance in making sure all work orders are completed on time; (3) create a weekly work order report; (4) incorporate the CMR Planning Department into the monitoring process to start tracking the weekly work orders; (5) distribute the weekly work orders to the managers by CMR Planning; and (6) monitor all work orders to identify upcoming deadlines for completion and orders that have not been completed. Managers are required to reinforce and follow up with Planning, Working Foremen and Field Crews to make sure that the work orders do not fall out of scope and cause another violation. | 2012-06-25 | 2012-07-05 | Does Not Contest | WECC applied cooperation credit for this violation because the Audit Notice prompted SWTC to perform a review of its Protection System devices which led to the Self-Report. SWTC had an internal compliance program (ICP) in place at the time of the violation which was a mitigating factor in the penalty determination: (a) SWTC has a fully documented ICP that senior management is in the process of approving and putting in place; (b) SWTC's oversight position is staffed and is supervised at a high level within SWTC; (c) the ICP oversight position has direct access to the SWTC Chief Executive Officer and the SWTC Board of Directors; (d) SWTC operates and manages the ICP so that it is independent from personnel responsible for compliance with the Reliability Standards; (e) the ICP has sufficient staff and an adequate budget; (f) SWTC senior management support and participate in the ICP; and (g) SWTC's ICP has a semi-annual or shorter review cycle. SWTC has a previous violation of PRC-005-1 R1, filed with FERC in NP10-79-000. The conduct, facts and circumstances of the first violation are not the same or similar to the instant violation. The prior violation involved SWTC's program and failure to have a procedure for testing DC circuitry for circuit breakers or for DC power for its relays. Additionally in the prior violation, although SWTC's documentation included an interval for testing equipment, it did not list the basis for developing the interval and it did not provide a summary of SWTC's Protection System maintenance and testing procedures in its documentation. In the instant violation, SWTC overlooked a substation’s battery bank and 6 electromechanical relays which were not tested within its Protection System maintenance and testing program’s defined intervals. These factual differences were sufficient so that WECC determined that aggravation would not be appropriate. Moreover, there was no evidence that broader corporate issues were involved.
Western Electricity Coordinating Council (WECC) | Sycamore Cogeneration Company (SYCC) | NCR05417 | WECC2012009823 | Settlement Agreement | On March 12, 2012, SYCC self-reported a violation of PRC-005-1 R2. WECC determined that SYCC, as a Generator Owner, failed to maintain and test four generator backup field overvoltage relays, one on each of four 75 MW units at SYCC's 300 MW facility, per the requirements of its Protection System maintenance and testing program. SYCC failed to maintain and test four of its 59 relays (6.78%). All other relays on the units were tested. These overvoltage relays perform a backup function to the generator excitation control systems on each of the four units. | PRC-005-1 | R2 | High | Moderate | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the four overvoltage relays in question were included in SYCC's maintenance and testing program. However, when SYCC proceeded to test the relays on each unit, the relay technicians failed to test these four relays. These four relays perform a backup function to the generator excitation control systems on each unit, and the control systems all operated normally during the period of this violation. In addition, SYCC provided evidence that its other protective devices, including the generator neutral and phase overcurrent relays, were maintained and tested within the defined intervals of SYCC's Protection System maintenance and testing program, and it provided the date last tested/maintained. | 6/18/07 (when the Standard became mandatory and enforceable) | 3/23/12 (Mitigation Plan completion) | 4500 | Self-Report | SYCC completed the following mitigation activities: (1) tested the four relays at issue; (2) clarified the testing requirements in the Maintenance Management System for the overvoltage relays in accordance with the Generator Protection Maintenance and Testing Program; (3) reviewed the testing requirements for the relays with maintenance staff; (4) added an annual review of compliance documentation by compliance/engineering staff to the annual compliance program review; and (5) communicated lessons learned to other sites. | 2012-03-23 | 2012-06-13 | Does Not Contest