## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000458 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On January 21, 2010, APGI-Tapoco, as a Transmission Owner (TO) and Generator Owner (GO), self-reported that: 1) two relays were not tested within defined intervals; 2) some battery maintenance records could not be located; and 3) some additional data may have been lost due to a computer failure. On January 29, 2010, the SERC audit team reported a violation of PRC-005-1 R2 because APGI-Tapoco could not provide evidence for testing and maintenance intervals, and the date last tested and maintained for associated communication systems and DC control circuitry. At the request of SERC, APGI-Tapoco prepared a spreadsheet that included each TO and GO Protection System device. The spreadsheet included the defined maintenance and testing intervals, the most recent test date, and the previous test date for each Protection System device. Based on this review, SERC made the following findings: 1) Protective relays: intervals of 5 calendar years for electromechanical relays and 10 calendar years for electronic relays. A total of 362 devices: for 353 devices –no findings; for 2 devices –tested outside of interval; for 7 devices –no test record of when devices were last tested and maintained; 2) Associated communication systems: intervals not to exceed 10 calendar years. A total of 34 devices: 34 devices –no findings. 3) Current transformers and potential transformers: testing at installation. A total of 142 devices: for 136 devices –no findings; for 6 devices –no test record of when devices were last tested and maintained; 4) Station batteries: quarterly testing. A total of 8 devices: 8 devices tested outside of interval at least once during the enforceable period; and 5) DC control circuitry: testing not to exceed 10 calendar years. A total of 178 devices: 178 devices –no test record of when devices were tested and maintained. SERC determined that APGI-Tapoco was in violation of PRC-005-1 R2 because it could not provide evidence that 201 of the 724 Protection System devices (or approximately 28%) were tested within the defined interval or had previous maintenance and testing records. | PRC-005-1 | R2 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Although not a replacement for comprehensive maintenance and testing, APGI-Tapoco has basic alarming on its electronic relays, DC control circuitry, and battery chargers. The supervisory control and data acquisition system (SCADA) allows operators to monitor the alarms continuously 24 hours a day, 7 days a week, which should allow for a timely response to electronic relay, DC control circuitry, and battery failures; and 2) APGI-Tapoco conducted functional tests on all the missed Protection System devices and no issues were identified, except for two relays that required recalibration, suggesting that the Protection System devices likely would have performed their intended functions if called upon to do so; and 3) The APGI-Tapoco transmission system is 107 miles of transmission lines at 161 kV, which has five interconnections with two adjacent utilities. The APGI-Tapoco system includes four hydroelectric generating plants that operate along the Little Tennessee River with a total capacity of 353 MW. APGI-Tapoco’s total system load is currently served entirely by an adjacent utility pursuant to a contract, thereby reducing the risk to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/6/2012 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Self-Report and Compliance Audit | APGI-Tapoco completed the following actions: 1) Conducted testing and maintenance on all the devices identified as missing records from the original list of devices; and 2) Conducted a survey of the system with outside resources to ensure all relevant devices are included in the program and completed maintenance and testing of the additional devices identified in the survey. | 2012-03-06 | 2012-06-11 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000457 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On January 29, 2010, the SERC audit team reported a violation of FAC-008-1 R1 because APGI-Tapoco, as a Generator Owner (GO), could not specify the Facility Ratings Methodology (FRM) for Generator Step-Up (GSU) transformers. As part of its assessment, SERC reviewed APGI-Tapoco's FAC-008 procedure. According to APGI-Tapoco, it utilizes the Tennessee Valley Authority's (TVA) Transmission Owner (TO) FRM for its GO and TO functions. In addition, APGI-Tapoco had a supplemental document, dated October 13, 2006, that included generator ratings. After reviewing TVA’s TO FRM, SERC verified the audit team's finding that APGI-Tapoco failed to address GSU transformers because TVA’s TO FRM explicitly states that it does not address GSU transformers. However, APGI-Tapoco, as a GO, established Facility Ratings for its GSU transformers, so there was no FAC-009-1 R1 violation. The SERC audit team found the APGI-Tapoco's TO function addressed the requirement of this Standard. SERC determined that APGI-Tapoco was in violation FAC-008-1 R1 because its FRM failed to address GSU transformers, as required. | FAC-008-1 | R1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) APGI-Tapoco had established Facility Ratings for its GSU transformers; and 2) While not including all of the applicable equipment in the FRM could result in incorrect modeling and identification of system contingencies, the most limiting element identified by APGI-Tapoco, the generator, did not change once the FRM was revised and applied. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/14/2012 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco completed the following actions: 1) Established an APGI-Tapoco authorized FRM that includes all required elements for TO and GO equipment (including generators and GSU transformers); and 2) Re-evaluated the Facility Ratings based upon the revised FRM in order to cover all TO and GO equipment. | 3/14/2012 | 2012-06-01 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000469 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of EOP-005-1 R1 because APGI-Tapoco, as a Transmission Operator (TOP), did not have a restoration plan that met the requirements in Attachment 1-EOP-005. As part of the assessment, SERC reviewed APGI-Tapoco’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. Specifically, APGI-Tapoco’s Emergency Operations Plan had the following characteristics: 1) It failed to outline relationships and responsibilities of the personnel necessary to implement system restoration; 2) It explained that its units are not included in the Regional Blackstart Plan, but it failed to address communication adequacy and protocol and power supplies for APGI-Tapoco’s blackstart needs; 3) It did not address the possibility that the restoration plan cannot be completed as expected; 4) It included the necessary operating instructions and procedures for synchronizing areas of the system that have become separated; 5) It did not address the necessary operating instructions and procedures for restoring loads, including the identification of critical load requirements; 6) It did not have a set of procedures for simulating and, where practical, actually testing and verifying the plan resources and procedures; 7) It did not address retention of documentation that operating personnel have been trained annually in the implementation of the plan and participated in restoration exercises; 8) It did not include functions to be coordinated with and among Reliability Coordinators (RC) and neighboring TOPs; and 9) It did not address notification to other operating entities as the steps of the restoration plan are implemented. SERC determined that APGI-Tapoco was in violation of EOP-005-1 R1 because its restoration plan did not include 8 out of the 9 requirements listed in Attachment 1-EOP-005. | EOP-005-1 | R1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; 2) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority (BA) or the RC; and 3) APGI-Tapoco had an existing system restoration plan, which contained elements such as an overview of the systems, identification of authority and coordination contact list with phone numbers, identification of related Transmission Owners and BAs, and handling of interconnection emergencies. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco revised the existing system restoration plan to address all of the elements of Attachment 1-EOP-005 in R1. All of the operators reviewed the new system restoration plan. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000470 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of EOP-005-1 R2 because APGI-Tapoco, as a Transmission Operator, was unable to provide evidence that its restoration plan had been updated annually, as required. As part of its audit assessment, SERC reviewed the audit screening worksheet and the EOP-005 procedures that were in effect throughout the enforceable period. Based on the revision history table, the initial procedure was effective on May 5, 2007 and revised in September 2007 (no specific date), revised again on February 9, 2009, used for training and reviewed by dispatchers on October 27, 2009, and revised on December 10, 2009, April 27, 2010 and September 28, 2010. APGI-Tapoco’s EOP-005 procedure was not revised or reviewed in 2008. SERC determined that APGI-Tapoco was in violation of EOP-005-1 R2 because it did not review and update its restoration plan at least annually. Specifically, the procedure was not revised or reviewed in 2008. | EOP-005-1 | R2 | Medium | Moderate | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The annual review was missed by 5 months; 2) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; and 3) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority or Reliability Coordinator. | 9/30/2008 (one year following the last review of the restoration plan) | 2/9/2009 (the date the next review was conducted) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco revised the existing system restoration plan to include a single point of contact and methodology for the tracking of reviews, exercises and training. All of the operators reviewed the new system restoration plan. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000471 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported that APGI-Tapoco, as a Transmission Operator (TOP), was unable to provide evidence of coordination of its restoration plans with all of the required entities as required by EOP-005-1 R4. As part of the assessment, SERC reviewed the audit screening worksheet and the APGI-Tapoco procedure that was in effect at the beginning of the mandatory and enforceable period. The procedure states: “For purposes of system separation, where all interconnections are unavailable, the Power System Dispatcher shall proceed to restore generation, load, and transmission circuits internally to APGI-Tapoco’s system, and coordinate re-synchronization to the Interconnection with the [Utility A] Reliability Coordinator (RC) and the [Utility B] Transmission Control Center when the Interconnections become available.” The functions to be coordinated are not specified in the procedure. APGI-Tapoco has one operator in the control room, who acts as the TOP and Generator Owner, which satisfies the requirement of coordination between those two functions. However, APGI-Tapoco could not produce evidence of coordination with the Balancing Authorities (BAs) within its area, its Reliability Coordinator (RC), and neighboring TOPs and BAs. SERC determined that APGI-Tapoco was in violation of EOP-005-1 R4 because it could not produce evidence of coordination of its restoration plan with the BAs within its area, its RC, and neighboring TOPs and BAs. | EOP-005-1 | R4 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; 2) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the BA or RC; and 3) APGI-Tapoco had an existing system restoration plan, which contained elements such as an overview of the systems, identification of authority and coordination contact list with phone numbers, the identification of related Transmission Owners and BAs, and the handling of interconnection emergencies. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco revised the existing system restoration plan to address the coordination of restoration plans with the RC, BA and TOP. All of the operators reviewed the new system restoration plan. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000472 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of EOP-005-1 R5 because APGI-Tapoco, as a Transmission Operator, could not provide evidence that it periodically tested the communication facilities needed to implement its restoration plan. As part of the assessment, SERC reviewed the audit screening worksheet and APGI-Tapoco’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. The Emergency Operations Plan did not address periodically testing the telecommunication facilities needed to implement the restoration plan. According to APGI-Tapoco, the telecommunications facilities needed to implement its Emergency Operations Plan are comprised of a land line, the APGI-Tapoco private branch exchange (PBX) phone system, a satellite phone and a radio system. APGI-Tapoco was not able to produce any information verifying that it had periodically tested the telecommunication facilities necessary for implementing its Emergency Operations Plan. SERC staff determined that APGI-Tapoco was in violation of EOP-005-1 R5 because it failed to test periodically the telecommunication facilities needed to implement its restoration plan, as required. | EOP-005-1 | R5 | Medium | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Even though APGI-Tapoco was not periodically testing its telecommunication facilities, 3 out of the 4 facilities needed to implement the restoration plan, the land line, the APGI-Tapoco PBX phone system and the radio, are normal means of communication and are utilized throughout the day. Therefore, communication issues would be identified promptly; 2) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; and 3) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco completed the following actions: 1) Revised the existing system restoration plan to include a process for periodically testing and documenting its telecommunications systems; and 2) Completed testing of the telecommunications facilities needed to implement the system restoration plan; and 3) All APGI-Tapoco operators reviewed the new system restoration plan. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000473 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported that APGI-Tapoco, as a Transmission Operator, could not provide evidence that its operating personnel had been trained in the implementation of the restoration plan as required by EOP-005-1 R6. As part of its assessment, SERC reviewed APGI-Tapoco’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. The Emergency Operations Plan included a statement that the annual dispatcher training includes a review of the restoration plan; however, that was the only reference to training in the Emergency Operations Plan. APGI-Tapoco was not able to produce any information verifying that it trained operating personnel in the implementation of its Emergency Operations Plan. | EOP-005-1 | R6 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; and 2) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco performed operating personnel training with simulated exercises. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000474 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported that APGI-Tapoco, as a Transmission Operator, could not provide evidence of actual testing or simulation of the restoration procedure as required by EOP-005-1 R7. As part of its assessment, SERC reviewed APGI-Tapoco’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. The Emergency Operations Plan includes a statement that in October of 2009, the Emergency Operations Plan was tested and verified through startup from local sources and that an isolated re-start that is independent of interconnection supply can be done successfully. APGI-Tapoco was not able to produce any information establishing that actual testing or simulation of its Plan had occurred, as required. | EOP-005-1 | R7 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Tapoco load, which is less than 55 MW, and restoration is a factor of business interruption for APGI-Tapoco; 2) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator; and 3) APGI-Tapoco had an existing system restoration plan, which contained elements such as an overview of the systems, identification of authority and coordination contact list with phone numbers, the identification of related Transmission Owners and Balancing Authorities, and the handling of interconnection emergencies. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco verified its restoration procedure by performing system restoration exercises. | 2011-12-12 | 2012-06-27 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000475 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of EOP-008-0 R1 because APGI-Tapoco, as a Transmission Operator, could not provide evidence that it reviewed its contingency plan annually, as required by R1.7. As part of its assessment, SERC reviewed APGI-Tapoco’s EOP-008 plan, which was in effect at the beginning of the compliance period. Specifically, the EOP-008 plan met R1.1, R1.2, R1.4 and R1.7. However, the EOP-008 plan did not meet R1.3, R1.5, R1.6 and R1.8. SERC determined that APGI-Tapoco was in violation of EOP-008-0 R1 because it failed to have a plan to continue reliability operations in the event its control center becomes inoperable. Specifically, the APGI-Tapoco plan did not meet 4 out of the 7 substantive subrequirements of EOP-008-0 R1. | EOP-008-0 | R1 | High | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Tapoco load and restoration is a factor of business interruption for APGI-Tapoco. The total APGI-Tapoco load being served is less than 55 MW; and 2) The generation within the APGI-Tapoco system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority or Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/20/2011 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco completed the following actions: 1) Updated its existing contingency plan to address all of the subrequirements; 2) Tested the contingency plan; and 3) Trained all relevant operations personnel to ensure that they are able to implement the contingency plans. | 2011-12-20 | 2012-07-10 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC2011008265 | Settlement Agreement | On September 30, 2011, APGI-Tapoco, as a Transmission Operator (TOP), self-reported a violation of MOD-030-2 R3.2 due to the failure to update daily values on July 21, 2011 (1 day total). The failure was caused by an issue with the software password, which was corrected on July 22, 2011, after which the correct transfer of information began to occur. During the course of its assessment, SERC reviewed APGI-Tapoco’s Available Transfer Capability (ATC) implementation documentation, process flow diagram-model documentation, Available Flowgate Capability (AFC) automated process description, logs and calculations spreadsheets from July 17, 2011 through July 31, 2011, and various screen shots, which showed generation maximum and minimum output levels (R3.1), generators, transmission lines, transformers, and ties (R3.4), and interconnections for the immediately adjacent areas as well as the areas outside the Reliability Coordination Area (R3.5). SERC determined that APGI-Tapoco, was in violation of MOD-030-2 R3.2 for failing to make available to the Transmission Service Provider (TSP) a Transmission model to determine AFC that was updated at least once per day for AFC calculations for days two through 30. Specifically, APGI-Tapoco failed to provide a daily update on July 21, 2011. | MOD-030-2 | R3; R3.2 | pending | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AFC calculations are performed by the TSP regardless of whether or not the TOP data is updated. The TSP’s AFC calculations utilize existing model data; therefore, if data is not updated for one day, the TSP calculates the AFC using the previous day’s data. Because changes to the AFC calculations are mainly driven by changes in system configuration, typical day-to-day changes in AFC are negligible; therefore, a failure to update should have a minimal impact on system reliability. | 7/21/2011 (when the data upload failed) | 7/21/2011 (when the data upload was corrected) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Self-Report | APGI-Tapoco completed the following actions: 1) Changed the password in the software access code; 2) Established increased alarming for any failures of upload; 3) Implemented a procedure for handling potential issues in the alarming; and 4) Established a redundant computer system to ensure continuous operation. | 2012-02-13 | 2012-07-09 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC2011008266 | Settlement Agreement | On September 30, 2011, APGI-Tapoco, as a Transmission Service Provider (TSP), self-reported a violation of MOD-030-2 R10 because the recalculation of the Available Flowgate Capability (AFC) daily values was not completed on July 21, 2011 due to an issue with the software password on the Transmission Operator's (TOP) system that was performing the upload of the updated system models used by the APGI-Tapoco. During the course of its assessment, SERC reviewed APGI-Tapoco’s AFC automated process description, logs and calculations spreadsheets from July 17, 2011 through July 31, 2011. Based on the design of APGI-Tapoco’s AFC calculation engine for the TSP function, the AFC calculation should be performed by the TSP regardless of whether the upload of data from the TOP occurs. The TSP’s AFC calculation engine runs independent of whether the upload occurs, but it utilizes existing model data; therefore, if a data upload from the TOP fails, the TSP’s AFC calculation engine uses the data uploaded by TOP engine from the previous successful upload. However, APGI-Tapoco did not enable the archiving function of the AFC calculation engine until August 9, 2011; therefore, APGI-Tapoco was not able to provide evidence that the AFC calculations were performed from July 1, 2011, its registration date as a TSP, until August 9, 2011, when the archiving function was enabled. SERC determined that APGI-Tapoco was in violation of MOD-030-2 R10 because APGI-Tapoco failed to recalculate the hourly, daily and monthly AFC utilizing the updated models described in R3.2, R3.3 and R5 from July 1, 2011 until August 9, 2011. | MOD-030-2 | R10 | pending | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the entity that had been responsible for performing the AFC calculations until July 1, 2011, and that has adjacent flowgates, continued to perform the AFC calculations on the subject flowgates for the period at issue. All of the power scheduled out of APGI-Tapoco was sold to this entity during the violation period. Each side confirmed the transactions, which could only have been done if the AFC calculation revealed sufficient flow capability. | 7/1/2011 (when APGI-Tapoco registered as a TSP) | 8/9/2011 (when APGI-Tapoco first calculated the AFC) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Self-Report | APGI-Tapoco enabled the calculation engine's archiving function. | 2011-08-09 | 2012-08-07 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Tapoco Division (APGI-Tapoco) | NCR01168 | SERC201000476 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Tapoco an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of PER-002-0 R3.1 stating that APGI-Tapoco, as a Transmission Operator (TOP), could not provide evidence that its training program included a set of training program objectives. SERC learned that APGI-Tapoco's personnel identified by R2 are: 1) The Power System Operator (Previously Power System Dispatcher - name changed to Power System Operator in October, 2011) (R2.1 and R2.2); and 2) The Chief Power System Operator (Previously Chief Power System Dispatcher - name changed to Chief Power System Operator in October, 2011) (R2.2) As part of its assessment, SERC reviewed APGI-Tapoco’s training program that was in effect at the beginning of the enforceable period. APGI-Tapoco's program stated “… the program is necessary to assure requisite skills are taught, while existing skills are recognized,” but it did not contain defined objectives based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements, as required. SERC determined that APGI-Tapoco was in violation of PER-002-0 R3.1 because its training program did not define a set of training program objectives. | PER-002-0 | R3; R3.1 | High | Lower | SERC determined that the violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because APGI-Tapoco had a training program in place and was training the applicable personnel in accordance with the training program, despite the lack of stated training objectives. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/12/2012 (Mitigation Plan completion) | $11,000 (for SERC201000457, SERC201000458, SERC201000469, SERC201000470, SERC201000471, SERC201000472, SERC201000473, SERC201000474, SERC201000475, SERC2011008265, SERC2011008266, and SERC201000476) | Compliance Audit | APGI-Tapoco revised its training program to explicitly state the training objectives. | 2012-01-12 | 2012-07-18 | Neither Admits nor Denies | APGI-Tapoco is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. ‐ Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000455 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On January 29, 2010, the SERC audit team reported a violation of FAC-008-1 R1 stating APGI-Yadkin, as a Generator Owner and Transmission Owner, could not specify the Facility Ratings Methodology (FRM) for its relay protective devices. SERC reviewed APGI-Yadkin’s FAC-008 documentation. APGI-Yadkin’s FRM document addressed the Facility Ratings for all of its solely and jointly owned facilities, except for its relay protective devices. SERC determined that APGI-Yadkin was in violation of FAC-008-1 R1 because its FRM did not address relay protective devices, as required. | FAC-008-1 | R1 | Medium | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) The most limiting element identified by APGI-Yadkin did not change once the FRM was revised and applied to the relay protective devices at issue; and 2) The protection relays were not the limiting device in any of the Facility Ratings. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/12/2012 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Updated its FRM to include the requirements for treatment of relay protective devices; and 2) Updated its Facility Ratings determination to include protective relays. | 2012-03-12 | 2012-06-06 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000456 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On January 29, 2010, the SERC audit team reported a violation of PRC-005-1 R2 because APGI-Yadkin, as a Generator Owner (GO) and Transmission Owner (TO), could not provide evidence of testing and maintenance intervals and the date last tested or maintained for some of its Protection System devices. At the request of SERC, APGI-Yadkin prepared a spreadsheet that included each TO and GO Protection System device. The spreadsheet included the defined maintenance and testing intervals, the most recent test date, and the previous test date for each Protection System device. Based on its review of the spreadsheet, SERC made the following findings: 1) Protective relays: Maintenance —5 calendar years for electromechanical relays and 10 calendar years for electronic relays; testing —10 calendar years. A total of 98 devices; for 37 devices —no findings; for 13 devices —tested outside of interval; for 48 devices —no test record of when devices were last tested/maintained. 2) Associated communication systems: Maintenance —5 calendar years if connected to an electromechanical relay and 10 calendar years if connected to an electronic relay; testing not to exceed 10 calendar years. A total of 16 devices; for 16 devices —no findings. 3) Voltage and current sensing devices: Maintenance —5 calendar years if connected to an electromechanical relay and 10 calendar years if connected to an electronic relay; testing — at installation. A total of 140 devices; for 132 devices —no findings; for 8 devices —no test record of when devices were last tested/maintained. 4) Station batteries: Maintained —quarterly; testing —no interval. A total of 6 devices; for 2 devices — no findings; for 4 devices —maintained outside of interval during the enforceable period. 5) DC control circuits: Maintenance —5 calendar years if connected to an electromechanical relay and 10 calendar years if connected to an electronic relay; Testing —not to exceed 10 calendar years. A total of 90 devices; for 50 devices —no findings; for 40 devices —no test record of when devices were last tested/maintained. SERC determined that APGI-Yadkin was in violation of PRC-005-1 R2 because it could not provide evidence that 113 of the 350 (32.28%) Protection System devices were not tested within the defined interval or had previous maintenance and testing records. | PRC-005-1 | R2 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) Although not a replacement for comprehensive maintenance and testing, APGI-Yadkin has basic alarming on the primary line electronic relays, the communications systems and the battery chargers. Also, the supervisory control and data acquisition system allows operators to monitor the alarms continuously 24 hours a day, 7 days a week. This should allow for a timely response to electronic relay, communication system and battery failures; 2) Functional tests were conducted and no issues were identified indicating that the Protection System devices should have performed their intended functions if called upon to do so; and 3) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2/10/2012 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Conducted testing and maintenance on all the devices identified as missing records from the original list of devices; and 2) Conducted a survey of the system with outside resources to ensure all relevant devices are included in the program and completed maintenance and testing of the additional devices identified in the survey. | 2012-02-10 | 2012-05-21 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000460 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported a violation of EOP-005-1 R1 because APGI-Yadkin, as a Transmission Operator (TOP), did not have a restoration plan that met the requirements in Attachment 1- EOP-005. As part of its assessment, SERC reviewed APGI-Yadkin’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. Specifically, APGI-Yadkin’s Emergency Operations Plan had the following characteristics: 1) It failed to outline relationships and responsibilities of the personnel necessary to implement system restoration; 2) It explained that its units are not included in the Regional Blackstart Plan, but failed to address communication adequacy and protocol and power supplies for APGI-Yadkin’s blackstart needs; 3) It did not address the possibility that the restoration plan cannot be completed as expected; 4) It included the necessary operating instructions and procedures for synchronizing areas of the system that have become separated; 5) It included the necessary operating instructions and procedures for restoring loads, including the identification of critical load requirements; 6) It did not include a set of procedures for simulating and, where practical, actually testing and verifying the plan resources and procedures; 7) It did not address retention of documentation that operating personnel have been trained annually in the implementation of the plan and participated in restoration exercises; 8) It addressed the coordination of functions with neighboring TOPs but failed to address the coordination of functions with the Reliability Coordinator (RC). VACAR South, the RC, is not a party to this agreement, nor does the plan address coordination of activities with the RC in any section; and 9) It did not address notification to other operating entities as the steps of the restoration plan are implemented. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R1 because its restoration plan did not include 7 out of the 9 of the requirements in Attachment 1-EOP-005. | EOP-005-1 | R1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; 2) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority (BA) or the RC; and 3) APGI-Yadkin had an existing system restoration plan, which contained elements such as an overview of the systems, identification of authority and coordination contact list with phone numbers, identification of related Transmission Owners and BAs, and the handling of interconnection emergencies. | 6/18/2007 (when the Standard became mandatory and enforceable) | 11/28/2011 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin revised the existing system restoration plan to address all of the elements of Attachment 1-EOP-005 in R1. | 2011-11-28 | 2012-05-02 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000461 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported a violation of EOP-005-1 R2 because APGI-Yadkin, as a Transmission Operator was unable to provide evidence that its restoration plan had been reviewed and updated at least annually, as required. As part of its assessment, SERC reviewed the EOP-005 procedures that were in effect throughout the enforceable period. Based on the revision history table, the initial procedure was effective on September 19, 2006, revised on January 7, 2008, and again on May 4, 2010 and October 24, 2011. APGI-Yadkin’s EOP-005 procedure was not revised or reviewed in 2007 and 2009. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R2 because it did not review and update its restoration plan at least annually. Specifically, the procedure was not revised or reviewed in 2007 and 2009. | EOP-005-1 | R2 | Medium | Moderate | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; and 2) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority or Reliability Coordinator. | 1/1/2008 (when APGI-Yadkin missed annual review) | 5/4/2010 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin revised the existing system restoration plan to include greater detail, clarification of documentation and a document history table with reviewers and approvals. | 2010-05-04 | 2012-05-11 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000462 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported a violation of EOP-005-1 R3 because APGI-Yadkin, as a Transmission Operator, could not show that it had developed restoration plans with a priority of restoring the integrity of the Interconnection, as required. As part of its assessment, SERC reviewed APGI-Yadkin’s EOP-005 procedures that were in effect throughout the enforceable period. The original procedure, dated September 19, 2006, through revision 5, dated May 4, 2010, addresses the restoration of the integrity of the Interconnection as a priority. However, revision 6 of the EOP-005 procedure, dated October 24, 2011, failed to address the restoration of the integrity of the Interconnection as a priority. Revision 6.1, dated November 17, 2011 addressed the restoration of the integrity of the Interconnection as a priority. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R3 because its restoration plan was not developed with a priority of restoring the integrity of the Interconnection, as required. | EOP-005-1 | R3 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) APGI-Yadkin was out of compliance for approximately one month; 2) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; and 3) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Balancing Authority or Reliability Coordinator. | 10/24/2011 (when APGI-Yadkin revised its restoration plan) | 11/17/2011 (when revision 6.1 of the restoration plan became effective) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yakin revised the original procedure to include a statement explicitly addressing the restoration of the integrity of the Interconnection as a priority. | 2011-11-28 | 2012-05-02 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000464 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported a violation of EOP-005-1 R5 because APGI-Yadkin, as a Balancing Authority and Transmission Operator, could not provide evidence that it periodically tested the telecommunication facilities needed to implement its restoration plan. As part of its assessment, SERC reviewed APGI-Yadkin’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. The Emergency Operations Plan did not address periodically testing the telecommunication facilities needed to implement the restoration plan. According to APGI-Yadkin, the telecommunications facilities needed are a land line, the APGI-Yadkin private branch exchange (PBX) phone system, a satellite phone and a radio system. APGI-Yadkin was not able to produce any information verifying that it had periodically tested the telecommunication facilities necessary for implementing its Emergency Operations Plan. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R5 because it failed to periodically test the telecommunication facilities needed to implement the restoration plan, as required. | EOP-005-1 | R5 | Medium | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Even though APGI-Yadkin was not periodically testing its telecommunication facilities, 3 out the 4 facilities needed to implement the restoration plan, the land line, the APGI-Yadkin PBX and the radio, are normal means of communication and are utilized throughout the day. Therefore, communication issues would be indentified promptly; 2) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; and 3) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 11/28/2011 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Revised the existing system restoration plan to include a process for periodically testing and documenting its telecommunications systems; and 2) Completed testing of the telecommunications facilities needed to implement the system restoration plan. | 2011-11-28 | 2012-05-10 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000465 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported that APGI-Yadkin, as a Balancing Authority and Transmission Operator, could not provide evidence that its operating personnel had been trained in the implementation of the restoration plan as required by EOP-005-1 R6. As part of its assessment, SERC reviewed the original APGI-Yadkin Emergency Operations restoration plan which was in effect at the beginning of the mandatory and enforceable period and found that the restoration plan does not address training. APGI-Yadkin was not able to produce any information verifying that it trained operating personnel in the implementation of its plan. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R6 because it failed to train its operating personnel in the implementation of its restoration plan, as required. | EOP-005-1 | R6 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; and 2) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Reviewed and updated the system restoration plan; 2) Trained all operating personnel on the implementation of the system restoration plan, which included a simulated table top exercise; and 3) Established a divisional compliance procedure to integrate compliance with NERC Reliability Standards into individual performance objectives to prevent recurrence. | 2011-12-12 | 2012-05-10 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000466 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 4, 2010, the SERC audit team reported that APGI-Yadkin, as a Balancing Authority (BA) and Transmission Operator, could not provide evidence of actual testing or simulation of the restoration procedure as required in EOP-005-1 R7. As part of its assessment, SERC reviewed APGI-Yadkin’s Emergency Operations Plan, which was in effect at the beginning of the mandatory and enforceable period. The Emergency Operations Plan did not address verification by actual testing or by simulation. APGI-Yadkin was not able to produce any information establishing that actual testing or simulation of its Emergency Operations Plan had occurred, as required. SERC determined that APGI-Yadkin was in violation of EOP-005-1 R7 because APGI-Yadkin failed to verify its restoration procedure by actual testing or by simulation. | EOP-005-1 | R7 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; 2) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator; and 3) APGI-Yadkin had an existing system restoration plan, which contained elements such as an overview of the systems, identification of authority and coordination contact list with phone numbers, identification of related Transmission Owners and BAs, and the handling of interconnection emergencies. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/12/2011 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Trained all operating personnel on the implementation of the system restoration plan, which included a simulated table top exercise; and 2) Established a divisional compliance procedure to integrate compliance with NERC Reliability Standards into individual performance objectives to prevent recurrence. | 2011-12-12 | 5/11/2012 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000467 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled from January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of EOP-008-0 R1 because APGI-Yadkin, as a Balancing Authority and Transmission Operator, could not provide evidence for several subrequirements, which cover the details of its plans to continue reliability operations in the event its control center becomes inoperable. As part of its assessment, SERC reviewed the EOP-008 procedure, which was in effect at the beginning of the mandatory and enforceable period. Specifically, the EOP-008 procedure met R1.1, R1.4, R1.5 and R1.7. However, the EOP-008 procedure did not meet R1.2, R1.3, R1.6 and R1.8. SERC determined that APGI-Yadkin was in violation of EOP-008-0 R1 because it failed to have a comprehensive plan to continue reliability operations in the event its control center becomes inoperable. Specifically, APGI-Yadkin's contingency plan did not meet 4 out of the 8 subrequirements of EOP-008-0 R1. | EOP-008-0 | R1 | High | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The load being served is limited to internal APGI-Yadkin load, which is less than 1 MW, and restoration is a factor of business interruption for APGI-Yadkin; and 2) The generation within the APGI-Yadkin system has not been identified as critical to the reliability of the BPS and is not designated as part of the overall system blackstart plan of the Reliability Coordinator. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/28/2011 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin completed the following actions: 1) Updated its existing contingency plan to address all of the subrequirements; 2) Tested the contingency plan; and 3) Trained all relevant operations personnel to ensure that they are able to implement the contingency plans. | 2011-12-28 | 2012-05-15 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC201000468 | Settlement Agreement | On October 10, 2009, SERC sent APGI-Yadkin an initial notice of a compliance audit scheduled for January 25, 2010 through January 29, 2010. On February 3, 2010, the SERC audit team reported a violation of PER-002-0 R3.1 stating that APGI-Yadkin, as a Balancing Authority and a Transmission Operator, could not provide evidence that its training program included a set of training program objectives. As part of its assessment, SERC reviewed APGI-Yadkin’s training program that was in effect at the beginning of the enforceable period. While APGI-Yadkin’s program states that “ … the program is necessary to assure requisite skills are taught, while existing skills are recognized,” it does not contain defined objectives based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements, as required. SERC determined that APGI-Yadkin was in violation of PER-002-0 R3.1 because its training program did not define a set of training program objectives. | PER-002-0 | R3; R3.1 | High | Lower | SERC determined that the violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because APGI-Yadkin had a training program in place and was training the applicable personnel in accordance with the training program. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/12/2012 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Compliance Audit | APGI-Yadkin revised its training program to explicitly state the training objectives. | 2012-01-12 | 2012-07-18 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC2011008261 | Settlement Agreement | On September 30, 2011, APGI-Yadkin, as a Transmission Operator (TOP), self-reported a violation of MOD-030-2 R3 because the software license on the system that was performing the upload of the updated system models failed to upload the updated values. Failure of data uploads occurred on five days: April 28, 2011, April 29, 2011, April 30, 2011, May 1, 2011 and May 2, 2011. The software license issue was corrected on May 2, 2011, and the correct transfer of information began to occur. This Self-Report was designated as SERC violation ID SERC2011-401160. On September 30, 2011, APGI-Yadkin, as a TOP, self-reported an additional violation of MOD-030-2 R3 due to the failure to update daily values once on July 21, 2011. The failure was caused by an issue with the software password, which was corrected on July 22, 2011; the correct transfer of information ensued thereafter. This Self-Report was designated as SERC violation ID SERC2011-401162. Because the two Self-Reports were related, SERC utilized a single tracking number, SERC2011-401160, for both issues. During the course of its assessment, SERC reviewed APGI-Yadkin’s Available Transfer Capability (ATC) implementation documentation, process flow diagram-model documentation, Available Flowgate Capability (AFC) automated process description, logs and calculations spreadsheets from April 24, 2011 through May 8, 2011, and from July 17, 2011 through July 31, 2011, and various OATI screen shots, which showed generation maximum and minimum output levels (R3.1), generators, transmission lines, transformers, and ties (R3.4), and interconnections for the immediately adjacent areas as well as the areas outside the Reliability Coordination Area (R3.5). SERC determined that APGI-Yadkin was in violation of MOD-030-2 R3.2 for failing to make available to the Transmission Service Provider (TSP) a transmission model to determine AFC that was updated at least once per day for AFC calculations for intra-day, next day, and days 2 through 30. Specifically, APGI-Yadkin failed to provide updates from April 28, 2011 through May 3, 2011, and on July 21, 2011, resulting in a total of 7 calendar days of noncompliance with R3.2. | MOD-030-2 | R3; R3.2 | pending | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The AFC calculations are performed by the TSP regardless of whether or not the TOP data is updated. The TSP’s AFC calculations utilize existing model data; therefore, if data is not updated for one day, the TSP calculates the AFC using the previous day’s data. Because changes to the AFC calculations are mainly driven by changes in system configuration, typical day-to-day changes in AFC are negligible; therefore, a failure to update have a minimal impact on system reliability. | 4/28/2011 (when the first day of noncompliance occurred | 7/21/2011 (when the last day of noncompliance occurred) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Self-Report | APGI-Yadkin completed the following actions: 1) Corrected the software license issue and the password issue that caused the violation; 2) Implemented alarming in the event that the system fails to upload as scheduled; 3) Created a response procedure to ensure the daily requirements are met; and 4) Installed a redundant system as a preventative measure in the event the primary system fails. | 2012-02-14 | 2012-07-09 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes.
SERC Reliability Corporation (SERC) | Alcoa Power Generating, Inc. - Yadkin Division (APGI-Yadkin) | NCR01169 | SERC2012010058 | Settlement Agreement | On April 7, 2012, APGI-Yadkin, as a Generator Owner, self-reported a violation of PRC-005-1 R2 because it discovered some devices were missing from the overall list of PRC-005 Protection System devices. APGI-Yadkin has a previous violation of PRC-005-1 R2 (NERC Violation ID SERC201000456, being concurrently filed), that was identified during a SERC on-site audit. The completion of the Mitigation Plan for this violation was February 10, 2012, approximately two months prior to the April 7, 2012 Self-Report. While verifying the list of Protection System devices, APGI-Yadkin identified 2 protection schemes comprised of 8 protective relays, 2 current transformers (CTs), and 8 DC control circuits that had been omitted from the maintenance and testing program. All of the 18 devices are associated with each other. The 2 schemes are identical with 1 CT, 4 relays and 4 DC control circuits. Each device was missing previous maintenance and testing records; however, maintenance and testing was performed on each device as soon as the device was identified. The number of devices for each device type was calculated by adding together the number of devices from the previous violation (NERC Violation ID SERC201000456) and the newly identified devices. Out of the total 368 Protection System devices, APGI - Yadkin had 18 that were out of compliance, which is approximately 5% of the Protection System devices. SERC determined that APGI-Yadkin was in violation of PRC-005-1 R2 because 18 out of 368 (5%) Protection System devices did not have previous maintenance and/or testing records. | PRC-005-1 | R2 | High | Lower | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) The protective devices at issue impacted two protection schemes used to monitor the bus in a power distribution house that feeds less than 1 MW system interruptible load to one internal customer; 2) APGI-Yadkin has basic alarming on the primary line electronic relays. The supervisory control and data acquisition system allows operators to monitors the alarms continuously 24 hours a day, 7 days a week; 3) Calibration/maintenance tests were conducted on the relays after the violation was discovered. No issues were identified, which indicates that the Protection System devices should have performed their intended functions if called upon to do so; and 4) No issues were identified when the DC control circuits were functionally tested successfully, which indicates that the Protective System devices should have performed their intended functions if called upon to do so. | 6/18/2007 (when the Standard became mandatory and enforceable) | 6/16/2012 (Mitigation Plan completion) | $13,000 (for SERC201000455, SERC201000456, SERC201000460, SERC201000461, SERC201000462, SERC201000464, SERC201000465, SERC201000466, SERC201000467, SERC201000468, SERC2011008261, and SERC2012010058) | Self-Report | APGI-Yadkin completed the following actions: 1) Immediately tested the devices; and 2) Had an independent contractor perform a comprehensive review to ensure that there were no additional devices missing from its inventory. None were identified. | 2012-06-16 | 2012-09-10 | Neither Admits nor Denies | APGI-Yadkin is governed by Alcoa Inc.'s (Alcoa) FERC Compliance Policy and Plan (Plan). SERC considered the Plan to be a mitigating factor in determining the penalty. The Plan is made available to all affected personnel through email communications and posting to the local website. The Plan is reviewed periodically with all affected personnel by the Chief Compliance Officer (CCO). On-line training is conducted on an annual basis related to the compliance process and reporting of compliance violations. The CCO, who reports to the Executive Vice President and Chief Legal and Compliance Officer for Alcoa, is a member of senior management and has oversight responsibility for the Plan. Senior management participate in the internal audit process and the annual review of the compliance processes. SERC considered APGI-Yadkin's violation of PRC-005-1 R2 (NERC Violation ID SERC201000456, being concurrently filed), to be an aggravating factor in determining the penalty.
SERC Reliability Corporation (SERC) | Ameren Missouri (Ameren) | NCR10248 | SERC201100775 | Settlement Agreement | On March 10, 2011, Ameren, as a Generator Owner, self-reported a violation of PRC-005-1 R2.1, stating that in 2008 it failed to perform specific annual maintenance and testing requirements on 10 battery systems, which were generation Protection System devices, at Ameren's Goose Creek and Pinckneyville generating plants. SERC reviewed a spreadsheet prepared by Ameren that included each of Ameren’s Protection System devices and the defined maintenance and testing intervals, the most recent test date and when applicable the previous test date for each device. SERC verified the defined intervals based on a review of Ameren’s PRC-005 maintenance and testing procedures. In addition to the 10 batteries that Ameren self-reported, SERC identified 46 protective relays that were not in compliance at Ameren's Labadie generating plant. Based on this review, SERC determined that Ameren had tested 10 out of 69 station batteries (14.5%) outside of the defined interval. SERC also determined that Ameren had no current test record for 46 out of 807 protective relays (5.7%) and was outside of the defined interval for those protective relays by approximately one year. 41 of the 46 protective relays at issue were localized to a single 625 MW unit at Ameren's Labadie generating plant. In total, Ameren could not provide evidence that 56 out of 2,128 Protection System devices (2.6%) were tested within the defined interval. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors: 1. 41 out of 46 protective relays that were missing current test records and that were outside of the defined interval were localized to a single 625 MW unit at Ameren’s Labadie Unit 3. If the 41 relays misoperated, resulting in a false trip, the outage likely would have been localized to that unit. Ameren’s largest single contingency is the loss of a 1,190 MW unit. Thus, the loss of a 625 MW unit has less impact than Ameren's largest single contingency; 2. Most of the Protection System functions for Labadie Unit 3 are monitored and alarmed to alert control room operators in the event of a failure, prompting Ameren personnel to investigate and address any problems with the devices; and 3. The 10 station batteries at the Goose Creek and Pinckneyville generating plants that Ameren failed to conduct annual testing on affected 10 combustion turbine generators. Ameren conducted monthly and quarterly inspections of the batteries and subsequently performed the missed annual tests and found no problems, suggesting that the batteries likely would have performed as intended if called upon to do so. The units at issue had capacity factors of less than 10% during the year Ameren failed to conduct annual testing and maintenance on the station batteries. | 1/1/2009 (when Ameren's batteries became noncompliant with its Protection System maintenance and testing program) | 6/29/2012 (Mitigation Plan completion) | $5,000 | Self-Report | Ameren completed the following mitigation activities: 1. Hired an electrical engineer to monitor and ensure testing is completed in compliance with the NERC Reliability Standards; 2. Revised the inspection instructions for its generation Protection System maintenance and testing program; 3. Reviewed all of Ameren's generation Protection System devices to ensure compliance with its generation Protection System maintenance and testing program; 4. Updated the maintenance and testing records for the five relays at Labadie Unit 4; 5. Completed the annual Protection System maintenance and testing for the 41 relays at Labadie Unit 3; and 6. Revised the Protection System maintenance and testing program to remove protective relay interval extensions associated with major unit outages. | 2012-06-29 | 2012-08-14 | Neither Admits nor Denies | Ameren operated under the internal compliance program (ICP) of Ameren Corporation, Ameren's parent company, at the time of the Self-Report. SERC considered the ICP, Ameren's Self-Report, and its cooperation to be mitigating factors in the penalty determination. Ameren's ICP is managed by Ameren's Vice President of Federal Legislative and Regulatory Affairs, who works with Ameren's Compliance Department, comprised of a manager, a supervisor, a consulting engineer and a senior compliance specialist. The Vice President of Federal Legislative and Regulatory Affairs has independent access to the Chairman, President and CEO of Ameren Corporation and is authorized to bring any compliance matter to the top leadership of the Ameren Corporation. The ICP includes training for Ameren employees and consultants based on their job descriptions. SERC considered the remediated issue (SERC201000478) of PRC-005-1 R2 of Ameren Services Company, an affiliate of Ameren, filed with FERC under Docket No. RC12-13-000, as a neutral factor in the penalty determination because of the small percentage of devices missed and the dispersed nature of the missed devices in that issue.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007376 | Settlement Agreement | On February 17, 2011, a violation of EOP-002-2 R4 was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009, because BREC, as a Balancing Authority (BA), did not perform all actions necessary before requesting the initiation of an Energy Emergency Alert (EEA). Specifically, BREC did not curtail a 20 MW non-firm wholesale energy sale. The duration of the event on June 13, 2008 was 4 hours and 38 minutes from hour ending (HE) 1400, until HE 1900. On June 13, 2008, for HE 1400, BREC listed a non-firm sale of 133 MW, and for HE 1500, it listed a non-firm sale of 20 MW. According to BREC, the 133 MW value included 81 MW of hourly schedules that ended at 1400 and a 52 MW schedule that was curtailed to 0 MW by the Purchasing-Selling Entity due to generator outages. BREC, as a Transmission Operator or BA, can curtail non-firm sales at any time for reliability-based reasons. BREC contacted the Reliability Coordinator (RC) and requested the initiation of an EEA 2 at 1352. The RC posted the EEA to the Reliability Coordinator's Information System at 1355. At 1400, the 20 MW non-firm sale was allowed to flow instead of being curtailed, and flowed for one hour. BREC is a member of the Midwest Contingency Reserve Sharing Group (Group), which consists of 22 parties. BREC’s reserve share obligation is approximately one tenth of one percent of the total Group’s reserve share obligation. Therefore, BREC’s ability to impact the Group is minimal. SERC determined that BREC was in violation of EOP-002-2 R4 for failing to perform all actions necessary prior to requesting the initiation of the an EEA 2 on June 13, 2008. | EOP-002-2 | R4 | High | Severe | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the 20 MW non-firm wholesale energy sale occurred during an EEA 2, which could have caused an escalation to an EEA 3, the sale was to a member of the Group. This resulted in no reduction of the net capacity within the borders of the Group. | 6/13/2008 (when BREC failed to curtail the non-firm load for one hour) | 6/13/2008 (at the end of HE 1500) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | To mitigate this violation, BREC joined the Midwest ISO, which is responsible for planning transmission service, generation dispatch, and managing congestion impacting the BREC system. | 12/1/2010 | 2012-07-02 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007377 | Settlement Agreement | On February 17, 2011, a violation of EOP-002-2 R7.2 was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009. The violation alleged that following the Energy Emergency Alert (EEA) 2 declaration, BREC as a Balancing Authority (BA), did not perform all actions necessary before requesting the initiation of an EEA. Specifically, BREC did not curtail a 20 MW non-firm wholesale energy sale, as required by Attachment 1-EOP-002-0 - Energy Emergency Alerts, Alert Level 2. The CI was initiated to review EEA events that occurred from January 2008 through March 2009. The duration of the event on June 13, 2008 was four hours and 38 minutes from hour ending (HE) 1400 until HE 1900. On June 13, 2008, HE 1400 listed a non-firm sale of 133 MW and HE 1500 listed a non-firm sale of 20 MW. According to BREC, the 133 MW value included 81 MW of hourly schedules that ended at 1400 and a 52 MW schedule that was curtailed to 0 MW by the Purchasing-Selling Entity due to generator outages. BREC is a member of the Midwest Contingency Reserve Sharing Group (Group), which consists of 22 parties. BREC’s reserve share obligation is approximately one tenth of one percent of the total Group’s reserve share obligation. Therefore, its ability to impact the Group is minimal. SERC determined that BREC was in violation of EOP-002-2 R7.2 because it did not curtail a 20 MW non-firm wholesale energy sale after the initiation of an EEA 2 on June 13, 2008. | EOP-002-2 | R7; R7.2 | High | Severe | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the 20 MW non-firm wholesale energy sale occurred during an EEA 2, which could have caused an escalation to an EEA 3, the sale was to a member of the Group. This resulted in no reduction of the net capacity within the borders of the Group. | 6/13/2008 (when BREC failed to curtail the non-firm load for one hour) | 6/13/2008 (at the end of HE 1500) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | To mitigate this violation, BREC joined the Midwest ISO, which is responsible for transmission service, generation dispatch, and managing congestion impacting the BREC system. | 2010-12-01 | 2012-07-02 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007378 | Settlement Agreement | On February 17, 2011, a violation of PRC-009-0 R1.3 was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009, because BREC, as a Load Serving Entity (LSE) and Distribution Provider (DP) that owns or operates an Under Frequency Load Shedding (UFLS) program, did not provide evidence that an analysis of the May 29, 2009 UFLS event, the failure of a 161 kV capacitor bank, was performed and documented as required by PRC-009-0 R1. There was no loss of load as a result of this event. The information provided by BREC during the CI contained a description of the event including the initiating conditions, as required by R1.1, a review of the UFLS set points and tripping times, as required by R1.2, and a summary of the findings, as required by R1.4. However, BREC failed to include a simulation of the event, as required by R1.3. According to BREC, two UFLS relays operated during the May 29, 2009 event. Each relay picked up correctly at its appropriate setting based on the analysis of the voltage waveform captured on the fault recorder. The relays were also tested and showed proper calibration. SERC determined that BREC was in violation of PRC-009-0 R1.3 for failing to conduct an analysis that included a simulation of the UFLS event. | PRC-009-0 | R1; R1.3 | Medium | Severe | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Instead of the post-event simulation, BREC performed an analysis, the results of which indicated that the UFLS relays operated properly. | 5/29/2009 (the date of the UFLS relay operation) | 2/2/2012 (Mitigation Plan completion) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | BREC updated and combined its UFLS plan and event analysis and its misoperation event analysis into one procedure. | 2012-02-02 | 2012-03-29 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007379 | Settlement Agreement | On February 17, 2011, a violation of TOP-002-2 R5 by BREC, as a Balancing Authority (BA), was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009, because BREC’s day-ahead plans showed inadequate resources to meet scheduled system configuration, generation dispatch, interchange scheduling, and demand patterns. SERC compared BREC's day-ahead capacity (plus purchases, minus sales) to its anticipated load and reserve share, and determined that a deficit was anticipated by BREC for 515 out of 878 hours (58.6%) of provided data from June 29, 2007 through June 14, 2009. BREC is a member of the Midwest Contingency Reserve Sharing Group (Group), which consists of 22 parties. BREC’s reserve share obligation is approximately one tenth of one percent of the total Group’s reserve share obligation. Therefore, its ability to impact the Group is minimal. SERC determined that BREC was in violation of TOP-002-2 R5 for failing to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. Due to successful reserve sharing, there was no loss of load as a result of this violation. | TOP-002-2 | R5 | Medium | Severe | SERC determined that the issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). When BREC could not meet the expected demand, it had to rely on the other members of the Group to supply its energy requirements. Reserves are integral to the reliability of the BPS and members of such groups benefit from the pooling of resources. However, reserves are meant for emergency purposes not as a planned resource to supply expected load. Excessive reliance on reserves by multiple members could have negatively affected BPS reliability. In this case, the Group provided a viable means to share reserves and was designed to accommodate the needs of its members. | 7/26/2007 (the first instance of negative planned resources) | 12/1/2010 (Mitigation Plan completion) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | BREC joined the Midwest ISO, which would be responsible for transmission service, generation dispatch, capacity reserves, and managing congestion impacting the BREC system. | 2010-12-01 | 4/23/2012 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007380 | Settlement Agreement | On February 17, 2011, a violation of TOP-002-2 R6 by BREC, as a Balancing Authority (BA), was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009, because its day-ahead plans showed inadequate resources to meet unscheduled system configuration and generation dispatch at a minimum N-1 Contingency planning on specific dates. SERC compared the BREC day-ahead capacity (plus purchases, minus sales) to its anticipated load and reserve share, and determined that a deficit was anticipated by BREC for 515 out of 878 hours (58.6%) of provided data from June 29, 2007 through June 14, 2009. As a result of failing to plan to meet scheduled system configuration and generation dispatch, BREC could not have met unscheduled system configuration and generation (at a minimum N-1 contingency planning). BREC is a member of the Midwest Contingency Reserve Sharing Group (Group), which consists of 22 parties. BREC’s reserve share obligation is approximately one tenth of one percent of the total Group’s reserve share obligation. Therefore, its ability to impact the Group is minimal. SERC determined that BREC was in violation of TOP-002-2 R6 for failing to plan to meet unscheduled system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. Due to successful reserve sharing, there was no loss of load as a result of this violation. | TOP-002-2 | R6 | Medium | Severe | SERC determined that the issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). When BREC could not meet the expected demand, it had to rely on the other members of the Group to supply its energy requirements. Reserves are integral to the reliability of the BPS and members of such groups benefit from the pooling of resources. However, reserves are meant for emergency purposes not as a planned resource to supply expected load. Excessive reliance on reserves by multiple members could have negatively affected BPS reliability. In this case, the Group provided a viable means to share reserves and was designed to accommodate the needs of its members. | 7/26/2007 (the first instance of negative planned resources) | 12/1/2010 (Mitigation Plan completion) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | BREC joined the Midwest ISO, which would be responsible for transmission service, generation dispatch, capacity reserves, and managing congestion impacting the BREC system. | 2010-12-01 | 4/23/2012 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2011007381 | Settlement Agreement | On February 17, 2011, a violation of TOP-002-2 R7 by BREC, as a Balancing Authority (BA), was reported to SERC as a result of a Compliance Investigation (CI) initiated on April 30, 2009, because it failed to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency on specific dates. SERC compared the BREC day-ahead capacity (plus purchases, minus sales) to its anticipated load and reserve share, and determined that a deficit was anticipated by BREC for 515 out of 878 hours of provided data from June 29, 2007 through June 14, 2009. As a result of failing to plan to meet its anticipated load and reserve share, BREC could not have met capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. BREC is a member of the Midwest Contingency Reserve Sharing Group (Group), which consists of 22 parties. BREC’s reserve share obligation is approximately one tenth of one percent of the total Group’s reserve share obligation. Therefore, its ability to impact the Group is minimal. SERC determined that BREC was in violation of TOP-002-2 R7 for failing to plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. Due to successful reserve sharing, there was no loss of load as a result of this violation. | TOP-002-2 | R7 | Medium | Severe | SERC determined that the issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). When BREC could not meet the expected demand, it had to rely on the other members of the Group to supply its energy requirements. Reserves are integral to the reliability of the BPS and members of such groups benefit from the pooling of resources. However, reserves are meant for emergency purposes not as a planned resource to supply expected load. Excessive reliance on reserves by multiple members could have negatively affected BPS reliability. In this case, the Group provided a viable means to share reserves and was designed to accommodate the needs of its members. | 7/26/2007 (the first instance of negative planned resources) | 12/1/2010 (Mitigation Plan completion) | $15,000 (for SERC2011007376, SERC2011007377, SERC2011007378, SERC2011007379, SERC2011007380, SERC2011007381) | Compliance Investigation | BREC joined the Midwest ISO, which would be responsible for transmission service, generation dispatch, capacity reserves, and managing congestion impacting the BREC system. | 2010-12-01 | 4/23/2012 | Neither Admits nor Denies | Based on BREC’s September 14, 2011 responses to SERC’s Compliance Culture Questionnaire, BREC has a documented internal compliance program (ICP). The existence of BREC's ICP was a mitigating factor in determining the penalty. The ICP describes the roles and responsibilities of employees in order to comply with NERC’s Standards. The ICP is available to all BREC employees and is posted on BREC’s Intranet. Any changes made to the ICP are noted in the weekly newsletter and emailed to all of BREC’s employees. BREC’s Chief Executive Officer (CEO) reviews and approves the ICP. BREC’s ICP has been in place since February 16, 2008 and was most recently revised on March 16, 2011. BREC’s Vice President of System Operations has oversight of the ICP and is responsible for all NERC standards. The Vice President of System Operations has independent access to the CEO as well as the Board of Directors through monthly board meeting attendance. The Vice President of System Operations reviews and approves all compliance-related documents. Employee performance reviews reflect employee accountability for compliance functions although no formal disciplinary provisions have been established in the ICP.
SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC201000544 | Settlement Agreement | On May 28, 2010, Duke submitted a Self-Report to SERC identifying its noncompliance with PRC-005-1 R2. Three additional instances of noncompliance with this Standard were subsequently self-reported by Duke. A fifth instance of noncompliance was reported as a result of a Compliance Investigation. SERC utilized a single NERC Violation ID to capture all five instances. Duke's Transmission Owner (TO) and Generator Owner (GO) functions are involved. On December 6, 2011, Duke submitted a spreadsheet of Protection System devices for the TO function. On April 11, 2012, Duke submitted a spreadsheet of Protection System devices for the GO function, which included nuclear Protection System devices. Each spreadsheet contained the defined maintenance and testing intervals, the most recent test date, and the previous test date for each Protection System device. Based on its review, SERC made the following findings: Device count for the TO function: Protective relays: Duke has a total of 10,997, with 3-year, 6-year and 10-year testing intervals. 10,619 relays were in compliance, 378 relays were outside of the defined interval, and all relays had a previous test record. Associated communication systems: Duke has a total of 509, to be continuously monitored and with 3-year testing intervals. 503 associated communication systems were in compliance, 6 associated communication systems were outside of the defined interval, and all associated communication systems had a previous test record. Voltage and current sensing devices (PTs/CTs): Duke has a total of 17,064, with an annual infrared scan required. 17,007 PTs/CTs were in compliance, 57 PTs/CTs were outside of the defined interval and all PTs/CTs had a previous test record. Station batteries: Duke has a total of 208, with an 18-month testing interval. 207 batteries were in compliance, 1 battery was outside of the defined interval, and all batteries had a previous test record. DC control circuits: Duke has a total of 2,631, with a yearly testing interval. 2,621 DC control circuits were in compliance, 10 DC control circuits were outside of the defined interval, and all devices had a previous test record. Device count for the GO function: Protective relays: Duke has a total of 1,807, with 5-year and 10-year testing intervals. 1,502 relays were in compliance, 305 relays were outside of the defined interval, and all relays had a previous test record. Associated communication systems: The GO function does not have any associated communication systems. PTs/CTs: Duke has a total of 4,220, with testing required upon installation. All PTs/CTs were in compliance. Station batteries: Duke has a total of 118, with a yearly testing interval. All batteries were in compliance. DC control circuits: Duke has a total of 650, with testing required upon installation. All DC control circuits were in compliance. Duke's nuclear facility consists of 587 relays, no associated communication systems, 1,079 PTs/CTs, 14 batteries and 306 DC control circuits. All these devices were in compliance. Duke, as a GO and TO, has a total of 40,190 Protection System devices. SERC determined that Duke, as a TO and GO, was in violation of PRC-005-1 R2 because 757 out of 40,190 Protection System devices (approximately 1.9%) were not tested within the defined intervals. | PRC-005-1 | R2 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because devices maintained or tested outside of the defined interval increase the odds of malfunction. However, the risk was mitigated by the following factors: 1. For the TO’s 378 relays, 306 were within Duke’s acceptance criteria. The acceptance criteria refer to a tolerance level that Duke has defined, typically based on a manufacturer's recommendations, experience, and lessons learned from the industry, that the protective device must meet in order to function and provide protection. 68 relays were outside of Duke’s acceptance criteria, but were determined to be capable of providing a sufficient level of protection; and 4 were outside of Duke’s acceptance criteria and not capable of providing a sufficient level of protection. Duke had operable redundant schemes that were in service for all of its relays; 2. The TO’s 6 associated communication systems were within Duke’s acceptance criteria; 3. The TO’s 10 DC control circuitry devices were tested and met Duke’s acceptance criteria; 4. The TO’s 57 PT/CT devices were tested and met Duke’s acceptance criteria; 5. The TO’s 1 battery was tested and met Duke's acceptance criteria; and 6. The GO’s 305 relays had backup protection. In all, SERC determined that although the maintenance and testing intervals were missed, the devices were working and should have performed as needed except for 4 TO relays. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/20/2012 (Mitigation Plan completion) | 22000 | Self-Report and Compliance Investigation | Duke completed the following mitigating actions: 1. Tested all devices that lacked last maintenance or testing dates; 2. Revised construction/modification processes so that new or upgraded devices are identified as part of the design process and entered into the work management system and the maintenance and testing program; 3. Assigned the responsibility of the Fossil/Hydro PRC-005 maintenance and testing program to the generation maintenance services department; 4. Developed new processes to ensure device maintenance and testing activities are identified, scheduled, and completed within the required maintenance interval; and 5. Modified the applicable procedures and processes to address the reporting and the retention of maintenance and/or testing results. | 2012-04-20 | 2012-08-31 | Neither Admits nor Denies | Duke follows Duke Energy Corporation's (Duke Energy) NERC Reliability Standards Compliance Policy (Compliance Policy), which has been documented since 2008. Details of the compliance program are widely disseminated within Duke and its affiliated companies. In addition, Duke Energy issues a quarterly newsletter addressing internal and external Reliability Standards information. The Reliability Standards Executive Sponsor Committee is a senior management team that provides oversight for the Compliance Policy. Duke Energy's Vice President of Compliance and Service Delivery is responsible for and has independent access to the CEO and the Executive Sponsor Committee. The Compliance Policy is regularly reviewed and is subject to internal audit. The Duke Energy Compliance Policy includes protocol for employee disciplinary action in connection with violations of Reliability Standards, where appropriate. SERC considered the compliance program to be a mitigating factor in determining the penalty. A Settlement Agreement covering one violation of PRC-005-1 R2 for Duke was filed with FERC under NP10-51-000 on February 12, 2010 (NOC-378). On March 12, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC did not aggravate the penalty because, as the prior violation occurred in the early stages of mandatory enforcement of the Standards, the instant violation did not represent recurring conduct warranting aggravation. SERC also considered Duke Energy's prior violations in the ReliabilityFirst region of PRC-005-1 R2 filed with FERC under NP12-2-000 on October 31, 2011 (NOC-953) and NP13-5-000 on October 31, 2012 (NOC-1530). SERC did not aggravate the penalty because Duke's instant violation was discovered, reported and being processed before Duke Energy's violations were filed and made public.
Southwest Power Pool Regional Entity (SPP RE) | Board Of Public Utilities (Kansas City KS) (BPU) | NCR01061 | SPP201000211 | Settlement Agreement | During an on-site Compliance Audit conducted from February 22, 2010 through February 25, 2010, SPP RE found that BPU, as a Generator Owner and a Transmission Owner, did not state the basis for the maintenance and testing intervals for 100% of the Protection System devices in its Protection System maintenance and testing policy and procedure (Procedure). Specifically, BPU did not have maintenance and testing intervals for its relays, associated communication systems, voltage and current sensing devices, station batteries, and DC control circuitry. In addition, BPU did not have procedures or a summary of its procedures for associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BPU did not have a Procedure in place that addressed all of its Protection System devices. Only relays were addressed in the BPU Protection System maintenance and testing program. BPU employees and contractors that performed the maintenance and testing on the devices did not have direction on how to perform the test, the intervals which the testing should be performed, and what devices needed to be tested. BPU was performing visual inspections of its Protection System devices on a three month average. BPU employees are trained to visually inspect and record the condition of major components at each BPU substation or other location and to report their findings to the appropriate supervisor. If maintenance needs to be performed on particular devices, a work order is issued and BPU employees are assigned to restore the device to operable condition. | 6/18/2007 (when the Standard became mandatory and enforceable) | 7/31/2012 (Mitigation Plan completion) | $20,000 (for SPP201000211 and SPP201000212) | Compliance Audit | To mitigate its violation of PRC-005-1 R1, BPU updated its Procedure to include maintenance and testing intervals and their basis for all BPS Protection System devices. BPU also updated its Procedure to include transmission and generation devices and a high-level overview of maintenance and testing procedures for all Protection System devices. | 2012-07-31 | 2012-08-09 | Neither Admits nor Denies | BPU was cooperative throughout the enforcement process. BPU had an internal compliance program at the time of the violation, which was considered a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Board Of Public Utilities (Kansas City KS) (BPU) | NCR01061 | SPP201000212 | Settlement Agreement | During an on-site Compliance Audit conducted from February 22, 2010 through February 25, 2010 SPP RE found that BPU, as a Transmission Operator and Balancing Authority, did not coordinate automatic load shedding throughout its coverage area. Specifically, BPU’s Quindaro Units Q1 and Q2 underfrequency load shedding (UFLS) trip settings were not coordinated with the BPU UFLS set points. In its Automatic UFLS Locations Frequency Trip Setting document dated January 5, 2010, BPU provided a listing of its UFLS installations and the corresponding trip settings. The UFLS trip settings for the BPU system are 59.3, 59.0, and 58.7 Hz. However, the Quindaro UF Trip settings for units Q1 and Q2 were set at 59.5 Hz. The Quindaro Units Q1 and Q2 should have been set to trip at a frequency below the lowest system load shed setting of 58.7 Hz. | EOP-003-1 | R7 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BPU did not have proper coordination of its UFLS settings on all generating units in its coverage area. If an underfrequency event had occurred on the BPU system, BPU’s generators at Quindaro, Units Q1 and Q2, would have tripped at 59.5 Hz, before controlled load shedding was set to start. Had BPU’s generators tripped prior to controlled load shedding, it would have aggravated the underfrequency event and there was an increased probability that additional load shedding would have been necessary on the BPU system in order to recover from the underfrequency event. Additionally, BPU’s facilities operate at relatively low voltage levels, 161 kV and 69 kV; BPU’s peak load is 473 MW; there are only three interconnections on the BPU system and these interconnections are at the 161 kV level which is not substantial to the BPS. However, SPP RE determined that BPU's violation did not pose a serious or substantial risk to the BPS because an UFLS event had not occurred on the BPU systems during the violation timeframe. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/27/2010 (Mitigation Plan completion) | $20,000 (for SPP201000211 and SPP201000212) | Compliance Audit | To mitigate its violation of EOP-003-1 R7, BPU changed its generator settings for Quindaro Units Q1 and Q2 and its Nearman CT-UF4 generator to trip at 58.2 Hz, which is below the last automatic load shed setting of 58.7 Hz. | 2010-04-27 | 2010-06-17 | Neither Admits nor Denies | BPU was cooperative throughout the enforcement process. BPU had an internal compliance program at the time of the violation, which was considered a mitigating factor in the penalty determination.
Southwest Power Pool, Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (Eastman) | NCR01092 | SPP201000297 | Settlement Agreement | During a June 10, 2010 Compliance Audit, SPP RE determined that Eastman, as a Generator Owner, was in violation of PRC-005-1 R1. Prior to May 4, 2010, Eastman did not have a documented generation Protection System maintenance and testing program (PSMTP). Additionally, the PSMTP Eastman produced during the Audit, Standard Operating Procedure Number CN-05 dated May 4, 2010: 1) failed to include Eastman’s 3 station batteries, 151 instrument transformers, and 161 direct current (DC) control circuits; 2) addressed only Eastman’s 31 protective relays; and 3) excluded the basis for the three-year interval Eastman established for maintaining and testing protective relays. As a result, Eastman’s violation of PRC-005-1 R1 affected 100% of Eastman’s generation Protection System devices. Eastman does not own any associated communication systems. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Eastman submitted evidence that it tested all of its generation Protection System devices during commissioning of its facility in 2001. Additionally, Eastman tested 25 protective relays between October 2007 and May 2008, and tested 2 station batteries between May 2008 and April 2009. Further, Eastman’s supervisory control and data acquisition system monitors and alarms on 17 of its protective relays, thereby providing ongoing monitoring of those relays' operational status. Eastman’s facility represents only 5% of its Transmission Operator's generating resources, and its generation plant connects to the BPS at 138 kV with a maximum output of 468 MW. Despite its interconnection to the BPS, Eastman uses the generation facility primarily to support its chemical plant and its BPS-related generation is a by-product of that activity. As a result, Eastman supplies approximately 260 MW of non-firm generation output to the BPS. Additionally, despite its failure to implement a compliant PRC-005 PSMTP, Eastman stated that it had experienced no device failures or misoperations during the violation timeframe. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/15/2011 (Mitigation Plan completion) | $6,000 (for SPP201000297 and SPP201000298) | Compliance Audit | Eastman reviewed and revised its PSMTP to include all Protection System elements, including batteries, instrument transformers, and DC controls. Additionally, it established a basis for the inspection intervals of all Protection System elements, and implemented the revised PSMTP. Eastman adopted the revised PSMTP on December 15, 2011, which superseded the procedure dated May 4, 2010. | 2011-12-15 | 2012-01-18 | Neither Admits nor Denies | Eastman does not have a documented internal compliance program. However, Eastman's majority owner, Eastman Chemical Company, has established programs for managing and reporting company performance to regulatory entities. SPP RE considered this a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (Eastman) | NCR01092 | SPP201000298 | Settlement Agreement | During a June 10, 2010 Compliance Audit, SPP RE determined that Eastman, as a Generator Owner, was in violation of PRC-005-1 R2. Eastman could not produce documentation of the maintenance and testing of 317 of its 346 generation Protection System devices (92%). Eastman lacked documentation relating to 1 out of 3 battery banks (33%), all 151 of its instrument transformers (100%), and all 161 of its direct current (DC) control circuits (100%) in its generation Protection System maintenance and testing program (PSMTP). Additionally, although Eastman’s 31 protective relays were included in the Eastman PSMTP, 4 protective relays (13%) were tested outside of the three-year testing interval established in Eastman’s 2010 PSMTP. Three of the relays had last been tested in May 2006, and one relay was last tested in May 2005. Eastman does not own any associated communication systems. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Eastman submitted evidence that it tested all of its generation Protection System devices during commissioning of its facility in 2001. Additionally, Eastman tested 25 protective relays between October 2007 and May 2008, and tested 2 station batteries between May 2008 and April 2009. Further, Eastman’s supervisory control and data acquisition system monitors and alarms on 17 of its protective relays, thereby providing ongoing monitoring of those relays' operational status. Eastman’s facility represents only 5% of its Transmission Operator's generating resources, and its generation plant connects to the BPS at 138 kV with a maximum output of 468 MW. Despite its interconnection to the BPS, Eastman uses the generation facility primarily to support its chemical plant and its BPS-related generation is a by-product of that activity. As a result, Eastman supplies approximately 260 MW of non-firm generation output to the BPS. Additionally, despite its failure to implement a compliant PRC-005 PSMTP, Eastman stated that it had experienced no device failures or misoperations during the violation timeframe. | 6/18/2007 (when the Standard became mandatory and enforceable) | 6/1/2012 (Mitigation Plan completion) | $6,000 (for SPP201000297 and SPP201000298) | Compliance Audit | Eastman tested the three identified relays in accordance with Eastman's PSMTP. Additionally, Eastman tested all other Protection System elements, including batteries, instrument transformers, and DC control circuits, and submitted the test results to SPP RE for review. | 2012-06-01 | 2012-07-19 | Neither Admits nor Denies | Eastman does not have a documented internal compliance program. However, Eastman's majority owner, Eastman Chemical Company, has established programs for managing and reporting company performance to regulatory entities. SPP RE considered this a neutral factor in the penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | San Miguel Electric Cooperative, Inc. (SMEC) | NCR00253 | TRE201100312 | Settlement Agreement | On March 31, 2011, SMEC submitted a Self-Report to Texas RE stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2.1. SMEC reported that it failed to perform maintenance and testing for 57 station batteries, which represents 1 set out of 65 total devices, within the defined monthly intervals, for the period September 2008 to April 2011, in accordance with SMEC’s PRC-005 procedures. Texas RE determined that SMEC was in violation of PRC-005-1 R2.1 for failure to provide evidence that Protection System devices were maintained and tested within the defined intervals. SMEC attributes the missed testing to scheduling errors caused by administrative personnel that have since been addressed and corrected. Subsequent completion of the missed testing, on May 22, 2011, did not reveal any issues with the batteries or related systems. | PRC-005-1 | R2; R2.1 | Lower | Lower | Texas RE determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because SMEC had a Protection System maintenance and testing program in place and performed maintenance and testing outside the defined intervals. Of the total Protection System inventory, 1.5% was impacted by the missed testing and subsequent testing produced no issues with the batteries. Between the period of September 2008 through April 2011, 11 monthly inspections were missed. These include, for 2008 – September, October, November and December, for 2009 – January, February and April, for 2010 – January, March, August and September. Analysis of the monthly maintenance procedure that was used prior to September 2011, shows that every item in the annual inspection, except visual inspection of the battery cell straps and torqueing of the strap connections, was performed in the monthly maintenance procedure. Therefore, only one element of the monthly testing was actually missed. Additionally, subsequent completion of the missed testing on May 22, 2011, did not reveal any issues with the batteries or related systems. | 9/3/2008 (when SMEC registered as a GO) | 5/22/2011 (date when the missed testing was completed) | 6000 | Self-Report | SMEC completed the following activities in accordance with the Mitigation Plan: 1) SMEC revised its Protection System maintenance and testing program to ensure that maintenance and testing are conducted on schedule and within defined intervals for station batteries. The established schedule is a minimum that must be achieved, regardless of what situations the entity may encounter that interferes with planned maintenance. 2) SMEC trained and will continue to emphasize to its employees the urgency to meet the specified time intervals. Formal annual training was presented to affected employees. 3) A formal internal compliance program (ICP) was implemented to provide a program by which each employee at SMEC is held accountable for his or her actions related to work tasks that encompass NERC Reliability Standards compliance. 4) The SMEC supervisor responsible for the equipment to be maintained and tested set up a notification calendar to signal when an item is due. The supervisor sends this information to other supervisors, lead men, manager(s) and engineer(s) so that each person is aware of the due dates. Each January, the supervisor reviews an equipment spreadsheet that lists all the equipment and the last date that maintenance was performed on the equipment. The spreadsheet also includes the time interval allowed between test dates. Each supervisor is responsible for scheduling maintenance in accordance with the due dates set forth in the spreadsheet and for tracking completion of tests and maintenance activities. | 2011-07-18 | 2012-08-31 | Neither Admits nor Denies | Texas RE observed that at the time of the violation, there was no documented ICP in place. Texas RE considered the following above and beyond measures as mitigating factors in the penalty determination: In December 2010, SMEC hired a consultant on NERC Reliability Standard compliance to assist and guide SMEC in achieving full compliance with NERC Reliability Standards. An ICP manual was produced on March 2, 2011. On November 14, 2011, SMEC created and later hired a new Reliability Compliance Manager position that would be responsible for monitoring NERC Reliability Standards and ensuring that the appropriate managers are aware of pending regulations and their enforcement dates. The consultant has assigned a Reliability Compliance Officer who ensures that SMEC’s program is on track and in full compliance with NERC Reliability Standards. This Reliability Compliance Officer and SMEC’s Reliability Compliance Manger work closely to ensure compliance. SMEC installed new task management/work flow software to improve the equipment maintenance service scheduling and SMEC made arrangements to sponsor a subject matter expert to participate at an upcoming Texas RE workshop.
Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2012010809 | Settlement Agreement | On July 31, 2012, AZPS, as a Generator Operator (GOP), submitted a Self-Report to WECC stating that it was in violation of VAR-002-1.1b R3 for failing to notify its Transmission Operator (TOP) of a change in the Automatic Voltage Regulator (AVR) status within 30 minutes. On June 30, 2012, at 9:50 a.m. MST, AZPS's Ocotillo Steam Unit 1 received an alarm caused by the Power System Stabilizer (PSS) tripping. The technician read the alarm screen, which noted "1 AVR Voltage Reg in Auto," but due to the wording of the alarm, failed to recognize this was indicating the AVR was operating in manual mode and not in automatic mode, resulting in the PSS not operating. At 9:55 a.m. MST, the PSS indication showed "PSS OFF" and "PSS ENABLE." The technician was unaware the AVR was operating in manual status, and, as a result, was not immediately aware of the change in status. Upon recognizing the AVR and PSS status were in manual mode, at 11:26 a.m. MST, the technician notified the operations manager of the change of status and subsequently the operations manager instructed the shift supervisor to notify the Energy Control Center (ECC), which is AZPS's TOP. The ECC was notified of the AVR and PSS change in status on June 30, 2012, at 11:32 a.m. MST, 102 minutes after the change occurred, and 72 minutes past the 30-minute requirement resulting in a violation of VAR-002-1.1b R3.1. | VAR-002-1.1b | R3; R3.1 | Medium | High | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AZPS's Ocotillo plant consists of four units with a combined capacity of 320 MW. During the time the AVR and PSS at Ocotillo Steam Unit 1 were operating in manual mode, the AVR and PSS equipment on the remaining three units were operating properly and, therefore, were able to respond to any system deviation. Additionally, although the result of generator voltage regulators operating with AVR in manual mode may reduce the margins of stable operation of the generating facility during unstable conditions, in this instance, however, AZPS's conditions on June 30, 2012, were stable and load conditions were low. | 6/30/2012 (when AZPS failed to notify the TOP within 30 minutes of a change in status of the AVR) | 6/30/2012 (when AZPS notified the TOP after 72 minutes of the change in status of the AVR) | 1000 | Self-Report | AZPS completed the following mitigation activities in accordance with its Mitigation Plan: 1) AZPS immediately and upon understanding notified the ECC of the change in status. 2) An AZPS Fossil Generation duty officer advised all plant managers of the June 30, 2012 event and required face-to-face meetings with all generator operators be conducted by July 12, 2012. This effort was taken to remind and reinforce with all generator operators the 30-minute notification requirement associated with any change in the status of an AVR or PSS; 3) Fossil Generation plant management issued a standing order, effective July 12, 2012, to all Fossil generator operators to verify upon startup the AVR is operating in automatic mode and the PSS is operating. The standing order provided interim guidance until existing startup procedures were modified (see below). It required all on-duty, scheduled generator operators to review and acknowledge the instruction prior to commencing their next shift. Those operators not on active duty were updated through the updated procedures upon their return to work; 4) An AZPS Fossil Generation duty officer advised all plant managers, via email, that a weakness was uncovered in operator understanding of indications associated with AVR and PSS. The email directed all plant managers to review all indications and alarms, and the required actions associated with AVR and PSS with all operators; 5) AZPS's Palo Verde Station was notified of this event to reinforce with its control room operators the importance of understanding indications and alarms, and the reporting requirements for generators; and 6) Plant managers posted an operator aid in all control rooms to remind operators of the requirements for reporting changes in the status of the AVR and PSS. | 2012-07-31 | 2012-08-10 | Does Not Contest | WECC considered AZPS’s compliance culture, namely its timely self-reporting and submission of a Mitigation Plan, to be a mitigating factor in the penalty determination. This was AZPS's second noncompliance of VAR-002-1.1b R3. Previously, WECC determined that AZPS failed to notify its TOP of a PSS change of status on October 9, 2011, when its operator failed to complete the notification process. Consequently, AZPS's TOP, ECC, was not notified of the Palo Verde Station Unit 3 PSS change in status until 24 hours later on October 10, 2011. The prior remediated issue, WECC20110008672, was filed with FERC on April 30, 2012, under Docket No. RC12-11-000. AZPS's prior noncompliance was considered an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC201102886 | Settlement Agreement | On July 22, 2011, IPCO submitted a Self-Report to WECC stating that, as a Generator Owner, it was in violation of PRC-005-1 R2.1 because it failed to maintain and test four communication devices within the interval defined in IPCO's Protection System maintenance and testing program. Specifically, IPCO did not have evidence it maintained and tested four of its 406 communication devices (1%) in 2009. Under its maintenance and testing program, IPCO was required to test these devices annually. IPCO provided documentation that it tested the devices at issue in December 2008. IPCO self-reported that, although it performed the 2009 testing for the communication equipment at issue, the testing evidence for 2009 was overwritten by the 2010 testing data, due to a database error. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). IPCO has redundant Protection Systems in place and continuously monitors relay operations. Additionally, the four communication devices at issue make up 1% of IPCO's communication devices, and were localized at one generating facility. IPCO provided evidence that it maintained and tested the devices at issue in December 2008 and in August 2010. IPCO asserted it had maintained these devices in 2009, although it did not have documentation of the testing. | 10/12/2009 (when IPCO's 2009 testing data was overwritten) | 12/31/2010 (Mitigation Plan completion) | $40,000 (for WECC201102886, WECC201102917, WECC2012009307, and WECC2011008649) | Self-Report | To mitigate this violation, IPCO modified its database to ensure that overwrite errors cannot remove yearly testing data. IPCO separated its database into multiple columns to ensure that each year of testing data is appropriately maintained. Further, IPCO tested the equipment at issue. | 2010-12-31 | 2011-09-15 | Agrees/Stipulates | WECC considered IPCO's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination. IPCO's ICP addresses each of the elements identified in FERC's Revised Statement on Enforcement. The ICP is formally documented, approved by company officers, and widely distributed to IPCO employees. IPCO dedicates staff to its ICP and administers the ICP independent of groups which are directly responsible for compliance. The ICP has the support of IPCO's senior management; IPCO's senior officers, including its CEO, can take action as necessary with regard to the ICP. WECC considered IPCO's compliance history to be an aggravating factor in the penalty determination. An Omnibus Settlement Agreement covering one violation of PRC-005-1 R2 for IPCO was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering one violation of PRC-005-1 R2 for IPCO (NOC-653) was filed with FERC under NP11-218-000 on June 29, 2011. On July 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined the prior violations should serve as a basis for aggravating the penalty.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC201102917 | Settlement Agreement | On August 23, 2011, IPCO submitted a Self-Report to WECC stating that, as a Transmission Operator (TOP), it was in violation of TOP-007-WECC-1 R2 because IPCO had a Net Scheduled Interchange for power flow over a Transmission path above the path's system operating limit (SOL) when IPCO implemented its real-time schedule for hour ending (HE) 15:00 Pacific Prevailing Time (PPT). IPCO, as TOP for the Idaho-Northwest path, is responsible for monitoring the path limits and ensuring Net Schedule power flows do not exceed the line's SOL when implementing the real-time schedules for the next hour. On July 3, 2011, the Oxbow-Lolo line, which is a component of the Idaho-Northwest path, was scheduled at 351 MW (import) with a limit of 340 MW. At 14:47, 14:48, 14:49 and 14:50 PPT, IPCO approved curtailment tags for a total reduction of 45 MW between hours 14:48 and 18:00 PPT. However, WECC determined that the integrated scheduled power flows on the Oxbow-Lolo line after the curtailments was 351 MW, 11 MW over the limit. As a result, WECC determined that IPCO was in violation of TOP-007-WECC-1 R2. | TOP-007-WECC-1 | R2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). IPCO operators recognized at the time of the violation that it was responsible for monitoring path limits, including the limits for the individual components that make up the defined path. At 14:41 and 14:51 PPT, IPCO, as the path operator, called and attempted to verify the over-schedule with a neighboring TOP but was unsuccessful. Additionally, the Oxbow-Lolo line is one of three lines that make up the Idaho-Northwest path. The path was not overscheduled for HE 15:00 PPT. Actual flow on the Idaho-Northwest path for HE 15:00 PPT was 458 MW (import), which is well under the operating limits of the major path, which has a total transfer capacity of 1,090 MW. Lastly, the Oxbow-Lolo line exceeded its limit by 11 MW. | 7/3/2011 (when IPCO implemented the schedule for power flow above the line's SOL) | 7/3/2011 (less than one hour later, when IPCO curtailed the power flow on the line) | $40,000 (for WECC201102886, WECC201102917, WECC2012009307, and WECC2011008649) | Self-Report | To mitigate this violation, IPCO informed its path operators that it is IPCO's responsibility to curtail the lines that make up the Idaho-Northwest path. IPCO trained its applicable personnel on its systems operating team, using scenario-based training during IPCO's winter session. This training lasted six weeks and addressed the components and requirements outlined in the Standard, including IPCO's responsibility regarding its transmission paths and specific operator training designed to aid the operators in becoming stronger in their curtailing skills. | 2011-11-02 | 2012-04-13 | Agrees/Stipulates | WECC considered IPCO's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination. IPCO's ICP addresses each of the elements identified in FERC's Revised Statement on Enforcement. The ICP is formally documented, approved by company officers, and widely distributed to IPCO employees. IPCO dedicates staff to its ICP and administers the ICP independent of groups which are directly responsible for compliance. The ICP has the support of IPCO's senior management; IPCO's senior officers, including its CEO, can take action as necessary with regard to the ICP. A Notice of Confirmed Violation covering one violation of TOP-STD-007-0 WR1 for IPCO was filed with FERC under NP12-5-000 on November 30, 2011. On December 30, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. TOP-STD-007-0 WR1 applied to Operating Transfer Capabilities on WECC defined paths which is distinct from TOP-007-WECC-1 R2, which deals with Net Scheduled Interchanges when TOPs implement real-time schedules for the next operating hour. Thus, WECC determined that this prior violation was not the same or similar to the instant violation and thus should not serve as a basis for aggravating the penalty.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2012009307 | Settlement Agreement | On January 20, 2012, IPCO submitted a Self-Certification to WECC stating that, as a Transmission Owner and Generator Owner, it was in violation of FAC-009-1 R1 because it failed to establish Facility Ratings for its Facilities that are consistent with its Facility Ratings Methodology. Specifically, IPCO failed to include certain substation elements, including associated bus and jumpers, in determining the operational ratings of the synchronous condensers at the Boise Bench, Brady and Kinport substations. IPCO's Facilities Rating Methodology requires that all of the associated elements be considered in determining a Facility Rating. IPCO did not include the above-listed elements when applying its Facilities Rating Methodology, resulting in an inaccurate Facility Rating for the synchronous condensers at the above-listed substations. | FAC-009-1 | R1 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). IPCO had compensating measures in place. The synchronous condensers are normally operated near unity (i.e., with maximum allowable flexibility to respond to system conditions) so that the respective voltage and reactive (VAR) capacity, in both a lead and lag direction, is available to respond to voltage variations on the system. The condensers would approach rating limits only during extreme contingency conditions. IPCO continues to operate the synchronous condensers near unity and can adjust the output to operate within the new limits that have been established. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/1/2012 (Mitigation Plan completion) | $40,000 (for WECC201102886, WECC201102917, WECC2012009307, and WECC2011008649) | Self-Certification | To mitigate this violation, IPCO reviewed its Facility Rating Methodology and systems engineering manual. IPCO re-evaluated and inspected all five synchronous condensers, identified the correct elements associated with them, and adjusted the Facility Ratings as required. IPCO added the updated Facility Ratings to the Facility Ratings database and they will be included in the next WECC base case. IPCO also updated the limit settings within IPCO's energy management system to ensure that IPCO continued to operate within its system limits. Lastly, IPCO added the updated Facility Ratings to the IPCO's single-line diagram. | 2012-05-01 | 2012-05-11 | Agrees/Stipulates | WECC considered IPCO's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination. IPCO's ICP addresses each of the elements identified in FERC's Revised Statement on Enforcement. The ICP is formally documented, approved by company officers, and widely distributed to IPCO employees. IPCO dedicates staff to its ICP and administers the ICP independent of groups which are directly responsible for compliance. The ICP has the support of IPCO's senior management; IPCO's senior officers, including its CEO, can take action as necessary with regard to the ICP. WECC considered IPCO's compliance history to be an aggravating factor with respect to this violation. IPCO has one prior violation of this Standard, in which IPCO could not prove that air switch ratings were adequately evaluated in its transmission ratings process. An Omnibus Settlement Agreement covering one violation of FAC-009-1 R1 for IPCO was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined the prior violation involved similar conduct and should serve as a basis for aggravating the penalty.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2011008649 | Settlement Agreement | On November 17, 2011, IPCO submitted a Self-Report to WECC stating that, as a Generator Owner and Generator Operator, it was in violation of EOP-009-0 R2 because it failed to submit its black start test data to WECC, the Regional Reliability Organization, in 2009 and 2010. Although IPCO completed black start testing in 2009 and 2010, IPCO did not provide WECC the testing results for 2009 and 2010, as required by the Standard. | EOP-009-0 | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the violation is limited to IPCO's black start units. Further, IPCO tested its black start units in 2007, 2008, 2009, 2010 and 2011, but only provided the results of such testing to WECC in 2007, 2008 and 2011. IPCO did coordinate with other entities, including its TOP, BA and RC, but did not submit the required information to WECC. Although failure to submit such testing records to WECC could lead to initiating a black start procedure with insufficient generation, IPCO performed its black start testing and IPCO's black start units remained available in the event a regional black start plan was required. | 1/1/2009 (when IPCO should have submitted its black start test data to WECC) | 12/13/2011 (Mitigation Plan completion) | $40,000 (for WECC201102886, WECC201102917, WECC2012009307, and WECC2011008649) | Self-Report | To mitigate this violation, IPCO completed its 2011 black start testing and submitted the 2009, 2010 and 2011 results to WECC. IPCO also contacted the appropriate personnel at WECC and established a communication process to ensure future black start testing updates and requests flow to and from the appropriate individuals and departments at IPCO and WECC. In addition, IPCO requested that the primary compliance contact be copied on the requests from WECC for black start testing results. | 2011-12-13 | 2012-01-12 | Agrees/Stipulates | WECC considered IPCO's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination. IPCO's ICP addresses each of the elements identified in FERC's Revised Statement on Enforcement. The ICP is formally documented, approved by company officers, and widely distributed to IPCO employees. IPCO dedicates staff to its ICP and administers the ICP independent of groups which are directly responsible for compliance. The ICP has the support of IPCO's senior management. IPCO's senior officers, including its CEO, can take action as necessary with regard to the ICP.