## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
ReliabilityFirst Corporation (ReliabilityFirst) | PPL - Lower Mount Bethel Energy, LLC (LMBE) | NCR00882 | RFC2011001116 | Settlement Agreement | On September 9, 2011, LMBE, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying a violation of VAR-002-1.1a R2 for failing to maintain generator voltage as directed by its Transmission Operator (TOP) in the voltage schedule. On September 20, 2011, LMBE submitted a revised Self-Report. LMBE follows a voltage schedule provided by PJM Interconnection, LLC (PJM), its TOP, that varies based upon the operation of the LMBE generating units and the operations of the adjacent generating station, PPL Martins Creek, L.L.C. (PPL MC). On April 20, 2010 and April 16, 2011, LMBE operated its generating units above the voltage schedule, which during those times was 233 kV, ± 4 kV. On April 20, 2010, LMBE operated between 237 kV and 241 kV for approximately ten hours (seven hours between 12:00 a.m. and 7:00 a.m., and three hours between 9:00 p.m. and 11:59 p.m.). On April 16, 2011, LMBE operated between 237 kV and 239 kV for approximately four hours. In addition, LMBE conducted an extent of condition review and discovered a total of 38 voltage excursions between March 26, 2010 and August 28, 2011. LMBE did not receive a revised voltage schedule from its TOP. | VAR-002-1.1a | R2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. On average, LMBE’s voltage excursions did not exceed 1.0% of the voltage schedule, with the greatest excursion being 2.3% of the voltage schedule. In addition, during these excursions, LMBE was operating its automatic voltage regulator (AVR) in automatic voltage control mode. PPL requested and received a letter from PJM confirming that the PPL Entities (LMBE, PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL MC, and PPL Montour, L.L.C (PPL Montour)) "have not caused any reliability concerns on the PJM Bulk Electric System with respect to their operating within the PJM voltage criteria outlined in PJM Manual 14D.” This confirmation covered the period from June 18, 2007 to November 15, 2011. | 3/26/2010 (when LMBE first exceeded its voltage schedule) | 8/28/2011 (when LMBE resumed operating within its voltage schedule) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Self-Report | To mitigate this violation, LMBE: 1) Set up local plant alarms to provide notification when voltage schedule limits are approached or exceeded; 2) Advised LMBE combined cycle technicians (CCTs) of the VAR-002 issue, ensured that the CCTs understood the procedure to notify the generation power dispatch if the voltage schedule cannot be met or the plant is at a VAR limit; 3) Performed testing to verify or adjust VAR limits, and submitted new limits to PJM; 4) Set the distributed control system to automatically change the AVR's voltage set points based on changes in the voltage schedule due to the number of PPL MC units being in service; 5) Conducted an internal review of sample operating data to identify the extent of voltage excursions that were not within Facility Rating constraints; and 6) Revised voltage schedules and/or bandwidths as appropriate, based on internal reviews of VAR limits and voltage schedules and coordination with its Transmission Owner and TOP. | 2012-06-30 | 2012-10-22 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the fact that it discovered this violation through Self-Report, and applied mitigating credit. ReliabilityFirst did not apply mitigating credit for the violation, RFC2011001116, self-reported three days prior to the start of the Compliance Audit. ReliabilityFirst considered the fact that it discovered 11 of the violations during the Compliance Audit, rather than through a Self-Report and did not apply mitigating credit. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering a violation of VAR-002-1 R3 for PPL Montana, LLC was filed with FERC under NP10-59-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of VAR-002-1.1b.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL - Lower Mount Bethel Energy, LLC (LMBE) | NCR00882 | RFC2011001194 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that LMBE, as a Generator Owner, failed to clearly specify a maintenance and testing interval and basis, and a summary of maintenance and testing procedure for associated communications systems in its Protection System maintenance and testing program, as required by PRC-005-1 R1.1 and R1.2. ReliabilityFirst also determined that LMBE failed to cross-reference the basis documents for maintenance and testing intervals for relays and direct current (DC) control circuitry in its Protection System maintenance and testing program. ReliabilityFirst also determined that LMBE failed to include valid maintenance and testing intervals and their basis for voltage for current sensing devices in its Protection System maintenance and testing program. During the Compliance Audit, ReliabilityFirst discovered violations of PRC-005-1 R1 by the PPL Entities (LMBE, PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour, L.L.C. (PPL Montour)). ReliabilityFirst discovered that PPL BI, Holtwood, PPL MC, and PPL Montour’s Protection System maintenance and testing program did not include valid maintenance and testing intervals for voltage and current sensing devices and their basis in their maintenance and testing program. Instead, the program stated that periodic maintenance for voltage and current sensing devices was not performed, but that PPL BI, PPL Holtwood, PPL MC, and PPL Montour would conduct visual inspections when accessible. PPL BI, PPL Holtwood, PPL MC, and PPL Montour presented evidence of maintenance and testing performed on voltage and current sensing devices during the time period of the violation. Nevertheless, PPL BI, PPL Holtwood, PPL MC, and PPL Montour failed to include maintenance and testing intervals and their basis, and a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.1 During the Compliance Audit, ReliabilityFirst found that LMBE utilized the same maintenance and testing program as its affiliates, PPL BI, PPL Holtwood, PPL MC, and PPL Montour. Subsequently, ReliabilityFirst determined that LMBE performed maintenance and testing under a different program that included maintenance and testing intervals and their basis and summaries of maintenance and testing procedures for voltage and current sensing devices. ReliabilityFirst determined there was an insufficient basis to proceed with the aspect of the violation related to LMBE. In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, the PPL Entities, including LMBE, did not correlate their basis documentation with the maintenance and testing intervals for relays and DC control circuitry. During the Compliance Audit, ReliabilityFirst found that the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for batteries as well. The PPL Entities previously completed a mitigation plan related to the maintenance and testing of batteries, wherein ReliabilityFirst reviewed their battery maintenance and testing procedure. As a result, ReliabilityFirst determined there was an insufficient basis to proceed with the aspect of the violation related to batteries. Specifically, the PPL Entities used a study performed by a PPL-affiliated entity, PPL Susquehanna, L.L.C., the 2001 Susquehanna Protective Relaying Study, as the basis for their maintenance and testing intervals for relays and direct current control circuitry. However, the PPL Entities failed to cross-reference the 2001 Susquehanna study in their Protection System maintenance and testing program document as the basis for their intervals. In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, PPL BI and LMBE included a general term, “control equipment,” to describe the maintenance and testing interval of associated communications systems. However, the program did not define “control equipment” to specifically include associated communications systems. As a result, PPL BI and LMBE failed to clearly specify a maintenance and testing interval and basis and a summary of maintenance and testing procedures for associated communications systems in their Protection System maintenance and testing program, as required by PRC-005-1 R1.1 and R1.2. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The PPL Entities performed all maintenance and testing within defined intervals. In addition, the PPL Entities performed maintenance and testing on voltage and current sensing devices despite the lack of a periodic maintenance and testing interval. Also, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/30/2012 (when the PPL Entities revised their Protection System maintenance and testing program) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities: 1) Restructured their Protection System maintenance and testing program by developing a new organization that is responsible for Protection System maintenance and testing; 2) Drafted new procedures for DC control circuitry, and voltage and current sensing devices. The maintenance and testing interval is 12 years, and the basis for the interval is included in the program; and 3) Prepared a PRC-005 summary table as part of their overall PRC-005 maintenance and training program. The summary table identified the intervals and cross-referenced the basis for the intervals with the PRC-005 categories of equipment, including associated communications systems. This summary table format listed all the required information that was included in various program documents in a single-page format. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL - Lower Mount Bethel Energy, LLC (LMBE) | NCR00882 | RFC2011001195 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that LMBE, as a Generator Owner, failed to provide sufficient evidence that it performed Protection System maintenance and testing on certain Protection System devices as required by PRC-005-1 R2.1. ReliabilityFirst discovered violations of PRC-005-1 R2 during a Compliance Audit of the PPL Entities (LMBE, PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour, L.L.C. (PPL Montour)) because the PPL Entities failed to provide sufficient evidence that they performed maintenance and testing on their direct current (DC) control circuitry, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that the PPL Entities failed to include the last date they performed maintenance and testing on their DC control circuitry. Subsequently, ReliabilityFirst discovered that the PPL Entities did provide such dates, so ReliabilityFirst determined there was an insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in the PPL Entities’ evidence of maintenance and testing is reflected in this violation of PRC-005-1 R2.1. The number of DC control circuits at issue and the total number of Protection System devices for each entity are as follows: Entity (PPL Holtwood; LMBE; PPL MC; and PPL Montour); DC circuits 1 (0.2%); 4 (2.3%); 3 (0.6%); and 4 (1.3%); Total Protection System devices 528; 172; 473; and 297. During the Compliance Audit, ReliabilityFirst discovered a violation for PPL BI regarding maintenance and testing of DC control circuitry. However, PPL BI submitted adequate evidence to ReliabilityFirst that it performed maintenance and testing on DC control circuitry. As a result, ReliabilityFirst did not find a violation for PPL BI for DC control circuitry. Second, PPL BI and LMBE failed to provide evidence that they performed maintenance and testing on their associated communications systems, which constitute 4 of 528 total (0.76%) Protection System devices for PPL BI and 1 of 172 total (0.58%) Protection System devices for LMBE, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that PPL BI and LMBE failed to include the last date they performed maintenance and testing on their associated communications systems. Subsequently, ReliabilityFirst discovered that PPL BI and LMBE did provide such dates, so ReliabilityFirst determined there was an insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in PPL BI and LMBE’s evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. For their Protection System devices, PPL Holtwood, LMBE, PPL MC, and PPL Montour enter a date into an integrated database to indicate that they performed maintenance and testing. The test they perform on DC control circuitry is a “pass” or “fail” test. PPL Holtwood, LMBE, PPL MC, and PPL Montour would not have entered dates into the database if the device had “failed” the test. By virtue of entering a date into the database, it is implied that PPL Holtwood, LMBE, PPL MC, and PPL Montour performed testing on its DC control circuitry. Although that does not rise to the level of evidence of performing maintenance and testing, it reduces the likelihood that PPL Holtwood, LMBE, PPL MC, and PPL Montour did not perform maintenance and testing on these devices. In addition, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/14/2012 (Mitigation Plan completion date) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities revised testing procedures and associated test forms for DC control circuitry and communications devices. These new forms document the completion of testing. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Montour, L.L.C. (PPL Montour) | NCR00888 | RFC2011001196 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL Montour, as a Generator Owner, failed to include valid maintenance and testing intervals and their basis for voltage and current sensing devices in their Protection System maintenance and testing program as required by PRC-005-1 R1.1 and R1.2. ReliabilityFirst also determined that PPL Montour failed to cross-reference the basis documents for maintenance and testing intervals for relays and direct current (DC) control circuitry in its Protection System maintenance and testing program. During the Compliance Audit, ReliabilityFirst discovered violations of PRC-005-1 R1 by the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour). ReliabilityFirst discovered that PPL BI, PPL Holtwood, PPL MC, and PPL Montour’s Protection System maintenance and testing program did not include valid maintenance and testing intervals for voltage and current sensing devices and their basis in their maintenance and testing program. Instead, the program stated that periodic maintenance for voltage and current sensing devices was not performed, but that PPL BI, PPL Holtwood, PPL MC, and PPL Montour would conduct visual inspections when accessible. Nevertheless, PPL BI, PPL Holtwood, PPL MC, and PPL Montour failed to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.1 In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for relays and DC control circuitry. During the Compliance Audit, ReliabilityFirst found that the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for batteries as well. The PPL Entities previously completed a Mitigation Plan related to the maintenance and testing of batteries, wherein ReliabilityFirst reviewed its battery maintenance and testing procedure. As a result, ReliabilityFirst determined there was an insufficient basis to proceed with the aspect of the violation related to batteries). Specifically, the PPL Entities used a study, the 2001 Susquehanna Protective Relaying Study, performed by a PPL affiliated entity, PPL Susquehanna, L.L.C., as the basis for their maintenance and testing intervals for relays and DC control circuitry. However, the PPL Entities failed to cross-reference the 2001 Susquehanna study in their Protection System maintenance and testing program document as the basis for their intervals. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The PPL Entities performed all maintenance and testing within defined intervals. In addition, the PPL Entities performed maintenance and testing on voltage and current sensing devices despite the lack of a periodic maintenance and testing interval. In addition, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/30/2012 (when the PPL Entities revised their Protection System maintenance and testing program) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, PPL Montour: 1) Restructured its Protection System maintenance and testing program by developing a new organization that is responsible for Protection System maintenance and testing; 2) The new organization drafted new procedures for DC control circuitry and voltage and current sensing devices. The maintenance and testing interval is 12 years, and the basis for the interval is included in the program; and 3) The PPL Entities prepared a PRC-005 summary table as part of their overall PRC-005 maintenance and training program. The summary table identified the intervals and cross-referenced the basis for the intervals with the PRC-005 categories of equipment, including communications systems. This summary table format listed all the required information that was included in various program documents in a single page format. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Montour, L.L.C. (PPL Montour) | NCR00888 | RFC2011001197 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL Montour, as a Generator Owner, failed to provide sufficient evidence that it performed Protection System maintenance and testing on certain Protection System devices as required by PRC-005-1 R2.1. ReliabilityFirst discovered violations of PRC-005-1 R2 during a Compliance Audit of the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour). PPL Holtwood, LMBE, PPL MC, and PPL Montour failed to provide sufficient evidence that they performed maintenance and testing on their direct current (DC) control circuitry, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that the PPL Entities failed to include the last date they performed maintenance and testing on their DC control circuitry. Subsequently, ReliabilityFirst discovered that the PPL Entities did provide such dates, so ReliabilityFirst determined there was an insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in the PPL Entities’ evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. The number of DC control circuits at issue and the total number of Protection System devices for each entity are as follows: Entity (PPL Holtwood; LMBE; PPL MC; and PPL Montour); DC circuits 1 (0.2%); 4 (2.3%); 3 (0.6%); and 4 (1.3%); Total Protection System devices 528; 172; 473; and 297. During the Compliance Audit, ReliabilityFirst discovered a violation for PPL BI regarding maintenance and testing of DC control circuitry. However, PPL BI submitted adequate evidence to ReliabilityFirst that it performed maintenance and testing on DC control circuitry. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. For their Protection System devices, PPL Holtwood, LMBE, PPL MC, and PPL Montour enter a date into an integrated database to indicate that they performed maintenance and testing. The test they perform on DC control circuitry is a “pass” or “fail” test. PPL Holtwood, LMBE, PPL MC, and PPL Montour would not have entered dates into the database if the device had “failed” the test. By virtue of entering a date into the database, it is implied that PPL Holtwood, LMBE, PPL MC, and PPL Montour performed testing on its DC control circuitry. Although that does not rise to the level of evidence of performing maintenance and testing, it reduces the likelihood that PPL Holtwood, LMBE, PPL MC, and PPL Montour did not perform maintenance and testing on these devices. In addition, the PPL Entities had alarms that alert the control room when a Protection System operates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/14/2012 (Mitigation Plan completion) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities included revised testing procedures and associated test forms for DC control circuitry and communications devices. These new forms document the completion of testing. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Holtwood, L.L.C. (PPL Holtwood) | NCR00886 | RFC2011001199 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL Holtwood, as a Generator Owner, failed to include valid maintenance and testing intervals and their basis for voltage and current sensing devices in their Protection System maintenance and testing program as required by PRC-005-1 R1.1 and R1.2. ReliabilityFirst also determined that PPL Holtwood failed to cross-reference the basis documents for maintenance and testing intervals for relays and direct current (DC) control circuitry in its Protection System maintenance and testing program. During the Compliance Audit, ReliabilityFirst discovered violations of PRC-005-1 R1 by the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour, L.L.C. (PPL Montour)). ReliabilityFirst discovered that PPL BI, PPL Holtwood, PPL MC, and PPL Montour’s Protection System maintenance and testing program did not include valid maintenance and testing intervals for voltage and current sensing devices and their basis in their maintenance and testing program. Instead, the program stated that periodic maintenance for voltage and current sensing devices was not performed, but that PPL BI, PPL Holtwood, PPL MC, and PPL Montour would conduct visual inspections when accessible. PPL BI, PPL Holtwood, PPL MC, and PPL Montour presented evidence of maintenance and testing performed on voltage and current sensing devices during the time period of the violation. Nevertheless, PPL BI, PPL Holtwood, PPL MC, and PPL Montour failed to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.1 In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for relays and DC control circuitry. During the Compliance Audit, ReliabilityFirst found that the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for batteries as well. The PPL Entities previously completed a mitigation plan related to the maintenance and testing of batteries, wherein ReliabilityFirst reviewed its battery maintenance and testing procedure. As a result, ReliabilityFirst determined there was an insufficient basis to proceed with the aspect of the violation related to batteries. Specifically, the PPL Entities used a study, the 2001 Susquehanna Protective Relaying Study, performed by a PPL affiliated entity, PPL Susquehanna, L.L.C., as the basis for their maintenance and testing intervals for relays and DC control circuitry. However, the PPL Entities failed to cross-reference the 2001 Susquehanna study in their Protection System maintenance and testing program document as the basis for their intervals. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The PPL Entities performed all maintenance and testing within defined intervals. In addition, the PPL Entities performed maintenance and testing on voltage and current sensing devices despite the lack of a periodic maintenance and testing interval. In addition, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/30/2012 (when the PPL Entities revised their Protection System maintenance and testing program) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, PPL Holtwood: 1) Restructured its Protection System maintenance and testing program by developing a new organization that is responsible for Protection System maintenance and testing; 2) The new organization drafted new procedures for DC control circuitry and voltage and current sensing devices. The maintenance and testing interval is 12 years, and the basis for the interval is included in the program; and 3) The PPL Entities prepared a PRC-005 summary table as part of their overall PRC-005 maintenance and training program. The summary table identified the intervals and cross-referenced the basis for the intervals with the PRC-005 categories of equipment, including communications systems. This summary table format listed all the required information that was included in various program documents in a single page format. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Holtwood, L.L.C. (PPL Holtwood) | NCR00886 | RFC2011001200 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL Holtwood, as a Generator Owner, failed to provide sufficient evidence that it performed Protection System maintenance and testing on certain Protection System devices as required by PRC-005-1 R2.1. ReliabilityFirst discovered violations of PRC-005-1 R2 during a Compliance Audit of the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island (PPL BI), PPL Holtwood, PPL Martins Creek (PPL MC), and PPL Montour, L.L.C. (PPL Montour)). PPL Holtwood, LMBE, PPL MC, and PPL Montour failed to provide sufficient evidence that they performed maintenance and testing on their direct current (DC) control circuitry, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that the PPL Entities failed to include the last date they performed maintenance and testing on their DC control circuitry. Subsequently, ReliabilityFirst discovered that the PPL Entities did provide such dates, so ReliabilityFirst determined there was an insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in the PPL Entities’ evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. The number of DC control circuits at issue and the total number of Protection System devices for each entity are as follows: Entity (PPL Holtwood; LMBE; PPL MC; and PPL Montour); DC circuits 1 (0.2%); 4 (2.3%); 3 (0.6%); and 4 (1.3%); Total Protection System devices 528; 172; 473; and 297. During the Compliance Audit, ReliabilityFirst discovered a violation for PPL BI regarding maintenance and testing of DC control circuitry. However, PPL BI submitted adequate evidence to ReliabilityFirst that it performed maintenance and testing on DC control circuitry. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. For their Protection System devices, PPL Holtwood, LMBE, PPL MC, and PPL Montour enter a date into an integrated database to indicate that they performed maintenance and testing. The test they perform on DC control circuitry is a “pass” or “fail” test. PPL Holtwood, LMBE, PPL MC, and PPL Montour would not have entered dates into the integrated database if the device had “failed” the test. By virtue of entering a date into an integrated database, it is implied that PPL Holtwood, LMBE, PPL MC, and PPL Montour performed testing on its DC control circuitry. Although that does not rise to the level of evidence of performing maintenance and testing, it reduces the likelihood that PPL Holtwood, LMBE, PPL MC, and PPL Montour did not perform maintenance and testing on these devices. In addition, the PPL Entities had alarms that alert the control room when a Protection System operates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/14/2012 (Mitigation Plan completion ) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities included revised testing procedures and associated test forms for DC control circuitry and communications devices. These new forms document the completion of testing. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Brunner Island, L.L.C. (PPL BI) | NCR00883 | RFC2011001201 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL BI, as a Generator Owner, failed to clearly specify a maintenance and testing interval and basis and a summary of maintenance and testing procedures for associated communications systems in its Protection System maintenance and testing program, as required by PRC-005-1 R1.1 and R1.2. ReliabilityFirst also determined that PPL BI failed to cross-reference the basis documents for maintenance and testing intervals for relays and direct current (DC) control circuitry in its Protection System maintenance and testing program. ReliabilityFirst also determined that PPL BI failed to include valid maintenance and testing intervals and their basis for voltage and current sensing devices in its Protection System maintenance and testing program. During the Compliance Audit, ReliabilityFirst discovered violations of PRC-005-1 R1 by the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL BI, PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour, L.L.C. (PPL Montour)). ReliabilityFirst discovered that PPL BI, PPL Holtwood, PPL MC, and PPL Montour’s Protection System maintenance and testing program did not include valid maintenance and testing intervals for voltage and current sensing devices and their basis in their maintenance and testing program. Instead, the program stated that periodic maintenance for voltage and current sensing devices was not performed, but that PPL BI, PPL Holtwood, PPL MC, and PPL Montour would conduct visual inspections when accessible. PPL BI, PPL Holtwood, PPL MC, and PPL Montour presented evidence of maintenance and testing performed on voltage and current sensing devices during the time period of the violation. Nevertheless, PPL BI, PPL Holtwood, PPL MC, and PPL Montour failed to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.1. In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for relays and DC control circuitry. During the Compliance Audit, ReliabilityFirst found that the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for batteries as well. The PPL Entities previously completed a mitigation plan related to the maintenance and testing of batteries, wherein ReliabilityFirst reviewed its battery maintenance and testing procedure. As a result, ReliabilityFirst determined there was insufficient basis to proceed with the aspect of the violation related to batteries. Specifically, the PPL Entities used a study, the 2001 Susquehanna Protective Relaying Study, performed by a PPL affiliated entity, PPL Susquehanna, L.L.C., as the basis for their maintenance and testing intervals for relays and DC control circuitry. However, the PPL Entities failed to cross-reference the 2001 Susquehanna study in their Protection System maintenance and testing program document as the basis for their intervals. In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, PPL BI and LMBE included a general term, “control equipment” to describe the maintenance and testing interval of associated communications systems. However, the program did not define “control equipment” to specifically include associated communications systems. As a result, PPL BI and LMBE failed to clearly specify a maintenance and testing interval and basis and a summary of maintenance and testing procedures for associated communications systems in their Protection System maintenance and testing program, as required by PRC-005-1 R1.1 and R1.2. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The PPL Entities performed all maintenance and testing within defined intervals. In addition, the PPL Entities performed maintenance and testing on voltage and current sensing devices despite the lack of a periodic maintenance and testing interval. In addition, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/30/2012 (when the PPL Entities revised their Protection System maintenance and testing program) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, PPL BI: 1) Restructured its Protection System maintenance and testing program by developing a new organization that is responsible for Protection System maintenance and testing; 2) The new organization drafted new procedures for DC control circuitry and voltage and current sensing devices. The maintenance and testing interval is 12 years, and the basis for the interval is included in the program; and 3) The PPL Entities prepared a PRC-005 summary table as part of their overall PRC-005 maintenance and training program. The summary table identified the intervals and cross-referenced the basis for the intervals with the PRC-005 categories of equipment, including communications systems. This summary table format listed all the required information that was included in various program documents in a single page format. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Brunner Island, L.L.C. (PPL BI) | NCR00883 | RFC2011001202 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL BI, as a Generator Owner, failed to provide sufficient evidence that it performed Protection System maintenance and testing on certain Protection System devices as required by PRC-005-1 R2.1. ReliabilityFirst discovered violations of PRC-005-1 R2 during a Compliance Audit of the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL BI, PPL Holtwood, L.L.C. (PPL Holtwood), PPL Martins Creek, L.L.C. (PPL MC), and PPL Montour, L.L.C. (PPL Montour)). PPL Holtwood, LMBE, PPL MC, and PPL Montour failed to provide sufficient evidence that they performed maintenance and testing on their direct current (DC) control circuitry, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that the PPL Entities failed to include the last date they performed maintenance and testing on their DC control circuitry. Subsequently, ReliabilityFirst discovered that the PPL Entities did provide such dates, so ReliabilityFirst determined there was insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in the PPL Entities’ evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. The number of DC control circuits at issue and the total number of Protection System devices for each entity are as follows: Entity (PPL Holtwood; LMBE; PPL MC; and PPL Montour); DC circuits 1 (0.2%); 4 (2.3%); 3 (0.6%); and 4 (1.3%); Total Protection System devices 528; 172; 473; and 297. During the Compliance Audit, ReliabilityFirst discovered a violation for PPL BI regarding maintenance and testing of DC control circuitry. However, PPL BI submitted adequate evidence to ReliabilityFirst that it performed maintenance and testing on DC control circuitry. As a result, ReliabilityFirst did not determine a violation for PPL BI for DC control circuitry. Second, PPL BI and LMBE failed to provide evidence that they performed maintenance and testing on their associated communications systems, which constitute 4 of 528 total (0.76%) Protection System devices for PPL BI and 1 of 172 total (0.58%) Protection System devices for LMBE, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that PPL BI and LMBE failed to include the last date they performed maintenance and testing on their associated communications systems. Subsequently, ReliabilityFirst discovered that PPL BI and LMBE did provide such dates, so ReliabilityFirst determined there was an insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in PPL BI and LMBE’s evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. For their Protection System devices, PPL Holtwood, LMBE, PPL MC, and PPL Montour enter a date into an integrated database to indicate that they performed maintenance and testing. The test they perform on DC control circuitry is a “pass” or “fail” test. PPL Holtwood, LMBE, PPL MC, and PPL Montour would not have entered dates into the integrated database if the device had “failed” the test. By virtue of entering a date into an integrated database, it is implied that PPL Holtwood, LMBE, PPL MC, and PPL Montour performed testing on its DC control circuitry. Although that does not rise to the level of evidence of performing maintenance and testing, it reduces the likelihood that PPL Holtwood, LMBE, PPL MC, and PPL Montour did not perform maintenance and testing on these devices. In addition, the PPL Entities had alarms that alert the control room when a Protection System operates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 10/31/2012 (proposed Mitigation Plan completion date) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities included revised testing procedures and associated test forms for DC control circuitry and communications devices. These new forms document the completion of testing. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Brunner Island, L.L.C. (PPL BI) | NCR00883 | RFC2011001203 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL BI, as a Generator Owner, failed to maintain generator voltage as directed by the Transmission Operator (TOP) in the voltage schedule as required by VAR-002-1.1a R2. Until March 25, 2011 when PPL BI’s TOP, PJM Interconnection LLC (PJM), revised its voltage schedule, PPL BI was required to operate its generating units following a variable voltage schedule. This variable schedule included three voltage levels for weekdays and two levels for weekends and holidays, with a voltage tolerance bandwidth of ±4.0 kV. However, PPL BI operated its generating units outside of that variable voltage schedule 22 times between January 1, 2010 and March 25, 2011 when the TOP revised the voltage schedule. When PPL BI compared the operating data for January 1, 2010 through March 25, 2011 to the revised voltage schedule, all data was within the bandwidth of the new voltage schedule. | VAR-002-1.1a | R2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. On average, PPL BI’s voltage excursions did not exceed 1.0% of the voltage schedule. In addition, PPL BI operated with its automatic voltage regulator (AVR) in automatic mode during this period. PPL requested and received a letter from PJM confirming that the PPL Generation entities “have not caused any reliability concerns on the PJM Bulk Electric System with respect to their operating within the PJM voltage criteria outlined in PJM Manual 14D.” This confirmation covered the period from June 18, 2007 to November 15, 2011. | 1/1/2010 (when PPL BI first exceeded its voltage schedule) | 10/3/2010 (when PPL BI last exceeded its voltage schedule) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, PPL BI reviewed the voltage operating data and, as necessary, requested revised voltage schedules from the Transmission Operator. PPL BI determined that no changes to its voltage schedule were required. | 2012-06-30 | 2012-10-22 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst did not apply mitigating credit for the violation, RFC2011001116, because self-reported three days prior to the start of the Compliance Audit. ReliabilityFirst considered the fact that it discovered 11 of the violations during the Compliance Audit, rather than through a Self-Report and did not apply mitigating credit. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering a violation of VAR-002-1 R3 for PPL Montana, LLC was approved filed with FERC under NP10-59-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of VAR-002-1.1b.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Martins Creek, L.L.C. (PPL MC) | NCR00887 | RFC2011001204 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL MC, as a Generator Owner, failed to include valid maintenance and testing intervals and their basis for voltage and current sensing devices in their Protection System maintenance and testing program as required by PRC-005-1 R1.1 and R1.2. ReliabilityFirst also determined that LMBE failed to cross-reference the basis documents for maintenance and testing intervals for relays and direct current (DC) control circuitry in its Protection System maintenance and testing program. During the Compliance Audit, ReliabilityFirst discovered violations of PRC-005-1 R1 by the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL MC, and PPL Montour, L.L.C. (PPL Montour)). ReliabilityFirst discovered that PPL BI, PPL Holtwood, PPL MC, and PPL Montour’s Protection System maintenance and testing program did not include valid maintenance and testing intervals for voltage and current sensing devices and their basis in their maintenance and testing program. Instead, the program stated that periodic maintenance for voltage and current sensing devices was not performed, but that PPL BI, PPL Holtwood, PPL MC, and PPL Montour would conduct visual inspections when accessible. PPL BI, PPL Holtwood, PPL MC, and PPL Montour presented evidence of maintenance and testing performed on voltage and current sensing devices during the time period of the violation. Nevertheless, PPL BI, PPL Holtwood, PPL MC, and PPL Montour failed to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.1 In addition, in their Protection System maintenance and testing program in effect until August 1, 2010, the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for relays and DC control circuitry. During the Compliance Audit, ReliabilityFirst found that the PPL Entities did not correlate their basis documentation with the maintenance and testing intervals for batteries as well. The PPL Entities previously completed a Mitigation Plan related to the maintenance and testing of batteries, wherein ReliabilityFirst reviewed its battery maintenance and testing procedure. As a result, ReliabilityFirst determined there was insufficient basis to proceed with the aspect of the violation related to batteries. Specifically, the PPL Entities used a study performed by a PPL affiliated entity, PPL Susquehanna, L.L.C., the 2001 Susquehanna Protective Relaying Study, as the basis for their maintenance and testing intervals for relays and DC control circuitry. However, the PPL Entities failed to cross-reference the 2001 Susquehanna study in their Protection System maintenance and testing program document as the basis for their intervals. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The PPL Entities performed all maintenance and testing within defined intervals. In addition, the PPL Entities performed maintenance and testing on voltage and current sensing devices despite the lack of a periodic maintenance and testing interval. In addition, the PPL Entities have alarms that alert the control room when a Protection System misoperates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/30/2012 ( when the PPL entities revised their Protection System maintenance and testing program) | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, PPL MC: 1) Restructured its Protection System maintenance and testing program by developing a new organization that is responsible for Protection System maintenance and testing; 2) The new organization drafted new procedures for DC control circuitry and voltage and current sensing devices. The maintenance and testing interval is 12 years, and the basis for the interval is included in the program; and 3) The PPL Entities prepared a PRC-005 summary table as part of their overall PRC-005 maintenance and training program. The summary table identified the intervals and cross-referenced the basis for the intervals with the PRC-005 categories of equipment, including communications systems. This summary table format listed all the required information that was included in various program documents in a single-page format. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the fact that it discovered one of the violations through Self-Report, and applied mitigating credit. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC , a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Martins Creek, L.L.C. (PPL MC) | NCR00887 | RFC2011001205 | Settlement Agreement | During a Compliance Audit, conducted from September 12, 2011 through September 30, 2011, ReliabilityFirst determined that PPL MC, as a Generator Owner, failed to provide sufficient evidence that it performed Protection System maintenance and testing on certain Protection System devices as required by PRC-005-1 R2.1. ReliabilityFirst discovered violations of PRC-005-1 R2 during a Compliance Audit of the PPL Entities (PPL - Lower Mount Bethel Energy, LLC (LMBE), PPL Brunner Island, L.L.C. (PPL BI), PPL Holtwood, L.L.C. (PPL Holtwood), PPL MC, and PPL Montour, L.L.C. (PPL Montour)). PPL Holtwood, LMBE, PPL MC, and PPL Montour failed to provide sufficient evidence that they performed maintenance and testing on their direct current (DC) control circuitry, as required by PRC-005-1 R2.1. During the Compliance Audit, ReliabilityFirst found that the PPL Entities failed to include the last date they performed maintenance and testing on their DC control circuitry. Subsequently, ReliabilityFirst discovered that the PPL Entities did provide such dates, so ReliabilityFirst determined there was insufficient basis to proceed with this aspect of the violation. It was unclear, however, what occurred on those dates, and as a result, the lack of clarity in the PPL Entities’ evidence of maintenance and testing is reflected in the violation of PRC-005-1 R2.1. The number of DC control circuits at issue and the total number of Protection System Devices for each entity are as follows: Entity (PPL Holtwood; LMBE; PPL MC; and PPL Montour); DC circuits 1 (0.2%); 4 (2.3%); 3 (0.6%); and 4 (1.3%); Total Protection System devices 528; 172; 473; and 297. During the Compliance Audit, ReliabilityFirst discovered a violation for PPL BI regarding maintenance and testing of DC control circuitry. However, PPL BI submitted adequate evidence to ReliabilityFirst that it performed maintenance and testing on DC control circuitry. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. For their Protection System devices, PPL Holtwood, LMBE, PPL MC, and PPL Montour enter a date into an integrated database to indicate that they performed maintenance and testing. The test they perform on DC control circuitry is a “pass” or “fail” test. PPL Holtwood, LMBE, PPL MC, and PPL Montour would not have entered dates into the integrated database if the device had “failed” the test. By virtue of entering a date into an integrated database, it is implied that PPL Holtwood, LMBE, PPL MC, and PPL Montour performed testing on its DC control circuitry. Although that does not rise to the level of evidence of performing maintenance and testing, it reduces the likelihood that PPL Holtwood, LMBE, PPL MC, and PPL Montour did not perform maintenance and testing on these devices. In addition, the PPL Entities had alarms that alert the control room when a Protection System operates. Furthermore, the PPL Entities have backup and redundant protection in place for all Protection System devices except the PPL MC units, which do not have 100% redundancy. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/14/2012 (Mitigation Plan completion | $0 (for RFC2011001116, RFC2011001194, RFC2011001195, RFC2011001196, RFC2011001197, RFC2011001199, RFC2011001200, RFC2011001201, RFC2011001202, RFC2011001203, RFC2011001204, and RFC2011001205) | Compliance Audit | To mitigate this violation, the PPL Entities included revised testing procedures and associated test forms for DC control circuitry and communications devices. These new forms document the completion of testing. | 2012-09-14 | 2012-11-06 | Admits | ReliabilityFirst considered certain aspects of the PPL Corporation's (PPL) internal compliance program (ICP) as a mitigating factor in the penalty determination. PPL's ICP governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region. PPL’s chief compliance officer has independent access to the CEO as well as the Board of Directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered the positive degree and quality of the PPL Entities’ cooperation and remedial action during the enforcement processes and applied mitigating credit. The PPL Entities were cooperative throughout their interaction with ReliabilityFirst in connection with these violations. When assessing the penalty for the instant violations, ReliabilityFirst considered whether the facts of these violations evidenced any: (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL BI, LMBE, PPL Holtwood, PPL MC, and PPL Montour was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Electric Utilities was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In addition, a Settlement Agreement covering violations of PRC-005-1 R2.1 for PPL Montana, LLC, a PPL affiliated entity, was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. As a result, ReliabilityFirst considered the PPL Entities’ violation history as an aggravating factor in the penalty determination for the violations of PRC-005-1.
SERC Reliability Corporation (SERC) | Calpine Energy Services (Calpine) | NCR01189 | SERC2011008223 | Settlement Agreement | On September 28, 2011, a SERC Compliance Investigation (CI) team reported a violation of EOP-004-1 R3 because Calpine Energy Services (Calpine), as a Generator Operator (GOP), failed to submit a preliminary written report to NERC within 24 hours of a disturbance at one of its generation stations. On August 25, 2007, Calpine experienced a disturbance at one of its generation stations. The disturbance initiated at the Broad River Energy Center (BREC), which is operated by Calpine and interconnected to the Riverview Substation (Riverview) and transmission system owned and operated by Entity A. The disturbance did not involve a loss of load, but did involve the tripping offline of eight generation units (the loss of approximately 900 MW of generation) and the temporary de-energizing of five 230 kV transmission lines (collectively, the Event). The Event occurred at approximately 1100 EDST on Saturday, August 25, 2007. A 230 kV bushing associated with BREC’s Unit 5 generator step-up transformer cracked, causing an electrical fault. The transformer differential relay detected the fault and signaled the lockout relay. The lockout relay failed to operate due to burnt coil, preventing local isolation of the fault. The lockout relay was a single point of protection system failure - when inoperable; it prevented two layers of protection system response from functioning. Entity A's transmission-side protection system responded to the Event because BREC’s protection system failed to isolate the fault. Entity A’s protection system responded with remote breakers, which isolated both BREC and Riverview from Entity A’s transmission system. The relays at BREC’s generating units opened the synchronizing breakers due to low voltage. This action took the generating units off of the system. Once the BREC generation units were offline, the reclosers re-energized the interconnecting transmission lines. Attachment 1 of EOP-004-1 R3 contains eight events which qualify as reportable disturbances. SERC determined the violation description in event 1 adequately categorizes the nature of this violation for the following reasons. Disturbance 1 is “The loss of a bulk power transmission component that significantly affects the integrity of interconnected system operations…” According to one-line diagrams of the BREC interconnection facility, the bus lines terminate into breaker positions in the 230 kV yard. As a result, they can affect the operation of the remaining 230 kV yard and lines, especially during a stuck breaker condition or a breaker on maintenance condition, as was demonstrated during the Event. Because such a fault is cleared by the operation of a transmission Protection System, the bus lines are transmission elements, and therefore the Standard and requirement are applicable. Also, since the Event began as a loss of transmission component at BREC and then involved a number of Bulk Power System (BPS) Facilities beyond BREC, it affected the integrity of the interconnected system's operation. As a result, the Event meets the criteria above and a disturbance report should have been submitted by Calpine. SERC determined that Calpine was in violation of EOP-004-1 R3 because it experienced a reportable incident that required it to provide a preliminary written report to its Regional Reliability Organization and NERC and did not submit that report. | EOP-004-1 | R3 | Lower | Severe | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) There were other processes and actors in place that reduced the risk of Calpine's failure. The event was reported to the Region and NERC by Entity A, whose transmission system was affected. Therefore, any benefit that could result from studying the submission and understanding the circumstances in order to minimize the likelihood of similar events in the future was available; and 2) An event analysis was initiated, resulting in the completion of the purpose of the Reliability Standard. | 8/25/2007 (the date Calpine was required to submit a Disturbance Report on the Event) | 8/26/2007 (when Calpine failed to submit the preliminary written report) | $5,000 (for SERC2011008223 and SERC2011008226) | Compliance Investigation | Calpine completed the following mitigating actions: 1) Developed a procedure to address EOP-004 event analysis and reporting requirements; and 2) Trained the applicable personnel on the procedure. | 2007-12-31 | 2012-10-19 | Neither Admits nor Denies | Since June 2007, Calpine has had a documented internal compliance program (ICP) for compliance with NERC Reliability Standards at the corporate level and at each plant. Corporate regulatory compliance policies are signed by the CEO while operations-specific policies and procedures are approved by Calpine’s Chief Compliance Officer (CCO). Generating Facility and Generation Desk Managers are responsible for implementing the NERC procedures and ensuring their staff members are adequately trained on compliance as appropriate to their respective roles. The CCO reports directly to the Chief Legal Officer and the Audit Committee of the Board of Directors. The CCO has also has independent access to the CEO. SERC determined that the existence of Calpine's compliance program was a mitigating factor in determining the penalty.
SERC Reliability Corporation (SERC) | Calpine Energy Services (Calpine) | NCR01189 | SERC2011008226 | Settlement Agreement | On September 28, 2011, a SERC Compliance Investigation (CI) team reported a violation of EOP-004-1 R3 because Calpine Energy Services (Calpine), as a Generator Operator (GOP), failed to submit a preliminary written report to NERC within 24 hours of a disturbance at one of its generation stations. On August 25, 2007, Calpine experienced a disturbance at one of its generation stations. The disturbance initiated at the Broad River Energy Center (BREC), which is operated by Calpine and interconnected to the Riverview Substation (Riverview) and transmission system owned and operated by Entity A. The disturbance did not involve a loss of load, but did involve the tripping offline of eight generation units (the loss of approximately 900 MW of generation) and the temporary de-energizing of five 230 kV transmission lines (collectively, the Event). The Event occurred at approximately 1100 EDST on Saturday, August 25, 2007. A 230 kV bushing associated with BREC’s Unit 5 generator step-up transformer cracked, causing an electrical fault. The transformer differential relay detected the fault and signaled the lockout relay. The lockout relay failed to operate due to burnt coil, preventing local isolation of the fault. The lockout relay was a single point of protection system failure – when inoperable; it prevented two layers of protection system response from functioning. Entity A’s transmission-side protection system responded to the Event because BREC’s protection system failed to isolate the fault. Entity A’s protection system responded with remote breakers, which isolated both BREC and Riverview from Entity A’s transmission system. The relays at BREC’s generating units opened the synchronizing breakers due to low voltage. This action took the generating units off of the system. Once the BREC generation units were offline, the re-closers re-energized the interconnecting transmission lines. SERC requested that Calpine provide evidence that the operators in the control room had a level of familiarity with the purpose and limitations of the protection system schemes at BREC. On January 4, 2012, Calpine provided training records, a procedure addressing compliance with PRC-001, and lesson materials related to protection systems. SERC staff reviewed these materials and confirmed that none were dated prior to the Event. Because Calpine could not produce pre-Event records of classroom or on-the-job training that would have provided the familiarity required by the Standard, SERC staff concluded that the operators were not familiar with the purpose and limitations of the protection system schemes. SERC determined that Calpine was in violation of PRC-001-1 R1 because it is unable to provide evidence that it was familiar with the purpose and limitations of protection system schemes applied in its area. | PRC-001-1 | R1 | High | Severe | SERC determined that the issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system bulk power system. Lack of familiarity with the protection system schemes at BREC could have resulted in operators taking actions affecting personnel and equipment safety as well as reliability. However, in this case, all of the protective actions occurred automatically and the system was restored to a stable condition in a matter of seconds during which operators familiar with the system would not have had time to analyze and respond to the situation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/31/2007 (Mitigation Plan completion) | $5,000 (for SERC2011008223 and SERC2011008226) | Compliance Investigation | Calpine completed the following mitigating actions: 1) Created a system protection coordination procedure; 2) Trained the applicable personnel on the procedure; and 3) Created a central engineering group that supports plants with Protection System design and coordination. | 2007-12-31 | 2012-10-19 | Neither Admits nor Denies | Since June 2007, Calpine has had a documented internal compliance program (ICP) for compliance with NERC Reliability Standards at the corporate level and at each plant. Corporate regulatory compliance policies are signed by the CEO while operations-specific policies and procedures are approved by Calpine’s Chief Compliance Officer (CCO). Generating Facility and Generation Desk Managers are responsible for implementing the NERC procedures and ensuring their staff members are adequately trained on compliance as appropriate to their respective roles. The CCO reports directly to the Chief Legal Officer and the Audit Committee of the Board of Directors. The CCO has also has independent access to the CEO. SERC determined that the existence of Calpine's compliance program was a mitigating factor in determining the penalty.
SERC Reliability Corporation (SERC) | Dynegy Midwest Generation, LLC (DMG) | NCR11187 | SERC2012010333 | Settlement Agreement | On May 24, 2012, DMG, as a Generator Owner, self-reported a violation of PRC-005-1 R2, stating that there were several instances in which it conducted late monthly battery testing at its Baldwin Energy Complex. SERC reviewed the DMG Protection System procedures and DMG-compiled spreadsheets, which are a complete inventory of the DMG Protection System devices, with defined intervals and maintenance and test dates for the most current and previous dates listed for each Protection System device. Based on this review, SERC determined that DMG was missing test and maintenance records for 71 out of 603 voltage and current sensing devices (11.8%) and had tested 3 out of 14 station batteries (21.4%) outside of the defined intervals. All of the noncompliant Protection System devices were located at DMG’s Baldwin Energy Complex. In total, SERC determined that DMG had 74 out of 995 Protection System devices (7.4%) that were not compliant with PRC-005-1 R2. | PRC-005-1 | R2; R2.1; R2.2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) DMG had conducted the monthly inspection maintenance and testing for the three missed batteries in each of the prior and subsequent months and found no issues; 2) DMG tests the integrity of the three batteries weekly via DC power testing to the emergency turbine lube oil pumps; 3) Each of the three missed batteries has alarms which are time and date stamped in the control room (e.g., battery charger trouble, grounds, low DC voltage). If the control room receives an alarm, DMG staff are dispatched to the specific battery to inspect it; and 4) If a voltage or current sensing device were to fail, the lack of a signal would be detected by the relay and the relay would trip, which would prompt the plant staff to investigate. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/28/2013 (approved Mitigation Plan completion) | $20,000 (for SERC2012010333 and SERC2012010789) | Self-Report | To mitigate this violation, DMG will: 1) Modify preventative maintenance work orders (PMs) to reclassify battery testing PMs as “Regulatory/Compliance” thus increasing their priority level. These “Regulatory Compliance” PMs are scrutinized weekly by both the plant manager and maintenance manager; 2) Develop and use a tracking report to monitor monthly, quarterly, annual, and five-year maintenance and testing performed in accordance with DMG procedures; 3) Re-train and refresh Baldwin Energy Complex leadership personnel on testing of Protection System devices addressed by DMG procedures; 4) Complete testing of the voltage and current sensing devices on Baldwin Unit 2 and the Reserve Auxiliary Transformer during the scheduled Fall 2012 outage; 5) Verify that no forced outages of sufficient length have occurred on Baldwin Unit 1 and Unit 3 to allow testing of the remaining voltage and current sensing devices; and 6) Complete testing of the voltage and current sensing devices on Baldwin Unit 1 and Unit 3 during the next scheduled outage in Spring 2013 unless an unscheduled forced outage allows testing sooner. | 5/28/2013 (approved completion date) | TBD | Neither Admits nor Denies | DMG has had an internal compliance program (ICP) since September 15, 2007, which SERC considered to be a mitigating factor in the penalty determination. The ICP outlines employee training requirements, ICP approval policy, and responsibilities for reporting known or suspected NERC violations. The ICP is maintained and issued by the Director for Electric Systems Operations and Compliance and is approved by the Executive Vice President and Chief Operating Officer. Compliance information is readily available on the company’s intranet and is distributed to applicable DMG personnel. Employees of DMG are also required to participate in annual online NERC compliance training. DMG has a compliance officer who reports directly to the Executive Vice President and General Counsel. The ICP has the full support and participation of senior management. DMG’s ICP is regularly reviewed by senior management and is subject to internal audit every three years. DMG regularly reviews the performance of individual employees and employees are subject to discipline if they do not follow the ICP. A DMG affiliate, Dynegy Power, LLC, formerly registered as Dynegy Inc., has a prior violation of PRC-005-1 R2 in the SERC Region, which was filed with FERC under NP10-152-000 on July 30, 2010. Dynegy Inc. also has two prior PRC-005-1 R2 violations in other regions: one in the ReliabilityFirst Corporation region, which was filed with FERC under NP10-178-000 on September 30, 2010, and the second in the Western Electricity Coordinating Council region, which was filed with FERC under NP10-183-000 on September 30, 2010. SERC considered Dynegy Inc.'s three prior violations of PRC-005-1 R2 to be an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Dynegy Midwest Generation, LLC (DMG) | NCR11187 | SERC2012010789 | Settlement Agreement | On July 26, 2012, DMG, as a Generator Operator, self-reported a violation of VAR-002-1.1b R3, stating that it failed to notify its Transmission Operator (TOP) of a status or capability change of the automatic voltage regulator (AVR) within 30 minutes. DMG's Wood River Unit 5 (Unit 5) is a cross-compound unit with a high pressure generator and a low pressure generator, with AVRs for both generators. DMG replaced both AVRs with new AVRs during the Spring 2012 outage of Unit 5. DMG brought Unit 5 back online on June 1, 2012. On June 26, 2012, Unit 5 tripped offline at 2:29 a.m., while operating at 160 MW (out of 368 MW capacity), due to a malfunction in the new AVR for the low pressure generator. After Unit 5 tripped, both AVRs were off and Wood River control room personnel notified DMG’s Houston control center (HCC), which in turn notified the TOP at 2:30 a.m. of the change in the status of the AVRs. DMG brought Unit 5 back online at 8:01 a.m., with the AVRs in manual control mode during start-up. DMG’s HCC notified the TOP at 8:17 a.m. that the AVRs were in manual control mode. At 8:21 a.m., the TOP issued a directive to Wood River to maintain voltage manually within the voltage schedule. At 9:25 a.m., Wood River control room personnel placed the Unit 5 AVRs in automatic voltage control mode and attempted to call HCC using the Unit 5 dedicated ring-down phone. The line rang several times with no answer and, due in part to multiple activities necessary to start up Unit 5, Wood River control room personnel made no additional attempts to call the HCC. At 10:03 a.m., 38 minutes after placing the AVRs in automatic voltage control mode, Wood River control room personnel reported increasing Unit 5’s output to the HCC. The HCC then inquired if the AVRs were still in the manual mode controlling voltage. Wood River control room personnel indicated that they had placed the AVRs in automatic voltage control mode at 9:25 a.m. but were unable to contact the HCC on the Unit 5 dedicated ring-down phone. At 10:03 a.m., the HCC notified the TOP that Wood River personnel had placed the AVRs in automatic voltage control mode at 9:25 a.m. DMG’s policies require DMG personnel to notify the TOP of any change in the AVR mode of operation while connected to the interconnected transmission system, regardless of the expected duration of the change in AVR status, within 30 minutes. This notification is performed by Wood River control room personnel contacting HCC personnel who then contact the TOP. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) The TOP was aware that the AVR for the low pressure generator on Unit 5 had malfunctioned that day, causing the unit trip, and DMG maintained the voltage at the point of interconnection within the applicable voltage schedule during the time period; 2) The incident lasted eight minutes beyond the required notification time, during which the AVR was on and in automatic voltage control mode; and 3) Unit 5 represents 368 MW out of DMG’s total generation of 3,067 MW in the SERC region. | 6/26/2012 at 9:55 a.m. (when DMG should have notified the TOP, 30 minutes after DMG personnel put the AVR at Unit 5 into automatic voltage control mode) | 6/26/2012 at 10:03 a.m. (when DMG personnel notified the TOP that DMG had put the AVR at Unit 5 into automatic voltage control mode) | $20,000 (for SERC2012010333 and SERC2012010789) | Self-Report | To mitigate this violation, DMG: 1) Developed a list of alternate HCC phone numbers that Wood River control room personnel should use until HCC personnel are reached; 2) Updated the Wood River Power Station SERC Reporting Rules to emphasize that control room personnel need to continue calling HCC until someone answers, and required Wood River control room personnel to review the updated SERC Reporting Rules; 3) Requested a blanket notification from the TOP allowing an exemption for DMG plants from notifying the TOP of every instance that DMG operated in a mode other than automatic voltage control mode during start-up and shut-down; and 4) Provided training to personnel at DMG plants for VAR-002-1.1b. | 2012-08-02 | 2012-11-07 | Neither Admits nor Denies | DMG has had an internal compliance program (ICP) since September 15, 2007, which SERC considered to be a mitigating factor in the penalty determination. The ICP outlines employee training requirements, ICP approval policy, and responsibilities for reporting known or suspected NERC violations. The ICP is maintained and issued by the Director for Electric Systems Operations and Compliance and is approved by the Executive Vice President and Chief Operating Officer. Compliance information is readily available on the company’s intranet and is distributed to applicable DMG personnel. Employees of DMG are also required to participate in annual online NERC compliance training. DMG has a compliance officer who reports directly to the Executive Vice President and General Counsel. The ICP has the full support and participation of senior management. DMG’s ICP is regularly reviewed by senior management and is subject to internal audit every three years. DMG regularly reviews the performance of individual employees and employees are subject to discipline if they do not follow the ICP. A DMG affiliate, Dynegy Power, LLC, formerly registered as Dynegy Inc., has a prior violation of VAR-002-1 R3 in the SERC Region, which was filed with FERC under NP11-266-000 on August 31, 2011. Dynegy Inc. also has a prior VAR-002-1.1b R3 violation in the Northeast Power Coordinating Council, Inc region, which was filed with FERC under NP11-241-000 on July 28, 2011. SERC considered Dynegy Inc.'s two prior violations of VAR-002-1 R3 to be an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Entergy Corporation (Entergy) | NCR01234 | SERC2011006478 | Settlement Agreement | On March 24, 2011, Entergy, as a Transmission Operator (TOP), self-reported a violation of NUC-001-2 R3 because the mutually agreed upon voltage limits in Entergy’s plant procedure were not fully implemented in Entergy's planning analyses. On March 24, 2010, Entergy issued Rev. 5 of its procedure which includes Nuclear Plant Interface Requirements (NPIRs). SERC reviewed the revised version of the procedure and confirmed that the lower and upper voltage limits for the River Bend Nuclear Station constituted NPIR changes and should have been incorporated into Entergy’s planning analyses. Entergy uses two models for its planning analyses. One is a long term planning model and the other is a next day model. SERC confirmed the implementation of NPIR changes to the long term model on March 24, 2010. However, Entergy only incorporated the lower voltage limit into its next day model on March 24, 2010. The upper voltage limit was not incorporated into the next day model until March 22, 2011. In addition, SERC learned that Entergy had not communicated any of the results from the analyses to the Nuclear Plant Generator Operator (NPGO). SERC determined that Entergy was in violation of NUC-001-2 R3 because it failed to fully incorporate the NPIRs into its planning analyses of the electric system and failed to communicate the results of the analyses to the NPGO. | NUC-001-2 | R3 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Generally, the voltage limits set by the NPIR do not change significantly because they are governed by a plant’s operating requirements, including plant safety equipment, which falls under the jurisdiction of the Nuclear Regulatory Commission. Since the changes are typically small, a NPIR change requiring a TOP to modify its transmission operation plan would be rare. In this instance, the analysis performed for the NPIR resulted in no operational change to the transmission system. | 4/1/2010 (when the Standard became mandatory and enforceable) | 10/3/2011 (Mitigation Plan completion) | $34,000 (for SERC2011006478, SERC2011006479, SERC2011007809 and SERC2011008456) | Self-Report | To mitigate this violation, Entergy: 1) Amended the procedure that includes NPIRs to include the personnel responsible for reviewing and jointly approving revisions; and 2) Revised the other applicable procedures to address actions that are to be performed when there are changes to the NPIR. | 2011-10-03 | 2012-08-16 | Neither Admits nor Denies | SERC reviewed Entergy's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty assessment. Entergy has a documented ICP, which consists of multiple system policies for all areas of compliance including NERC Reliability Standards. The ICP is reviewed on an as-needed basis. The last review took place in the fourth quarter of 2011. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. The Corporate Compliance Committee (CCC) oversees the ongoing development and maintenance of Entergy’s policies and procedures concerning legal compliance issues and business ethics and oversees activities undertaken to promote adherence with such policies and procedures. The CCC meets quarterly and is responsible for the development and the promotion of Entergy’s compliance and business ethics policies and procedures. Entergy’s Corporate Compliance Officer, the Vice-President, Ethics & Compliance, reports directly to the Senior Vice-President & General Counsel, and has independent access to Entergy’s Board of Directors Audit Committee and is a member of the Corporate Compliance Committee.
SERC Reliability Corporation (SERC) | Entergy Corporation (Entergy) | NCR01234 | SERC2011006479 | Settlement Agreement | On March 24, 2011, Entergy, as a Transmission Operator (TOP), self-reported a violation of NUC-001-2 R4.1 because the mutually agreed upon voltage limits in Entergy’s plant procedure were not fully implemented in Entergy's operating analyses. On September 21, 2011, Entergy submitted an additional Self-Report stating that Nuclear Plant Interface Requirements (NPIRs) values were incorporated into its models on March 23, 2011, but were later overwritten with pre-existing incorrect values during a model changeover on March 31, 2011. On March 24, 2010, Entergy issued Rev. 5 of procedure which included some NPIR changes. SERC reviewed the revised version of the procedure and confirmed that the changes of voltage limits for the River Bend Nuclear Station constituted NPIR changes and should have been incorporated into Entergy’s real time models, which are used for its operating analyses. On March 23, 2011, Entergy updated its models with the new NPIR values. However, it was discovered on August 22, 2011, that the values had been overwritten during a model changeover on March 31, 2011. Entergy has two sets of operating models, one in “use” and one in “standby.” The models are exchanged every two weeks. This process allows Entergy to incorporate any changes to the “standby” model and place it in the “use” mode at the next two-week cycle. In this case, Entergy failed to update one of the models prior to placing it into production. SERC determined that Entergy was in violation of NUC-001-2 R4.1 because it failed to incorporate all of the NPIRs into its operating analyses of the electric system. | NUC-001-2 | R4.1 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Generally, the voltage limits set by the NPIR do not change significantly because they are governed by a plant’s operating requirements, including plant safety equipment, which falls under the jurisdiction of the Nuclear Regulatory Commission. Since the changes are typically small, a NPIR change requiring a TOP to modify its transmission operation plan would be rare. In this instance, the analysis performed for the NPIR resulted in no operational change to the transmission system. | 4/1/2010 (when the Standard became mandatory and enforceable) | 10/3/2011 (Mitigation Plan completion) | $34,000 (for SERC2011006478, SERC2011006479, SERC2011007809 and SERC2011008456) | Self-Report | To mitigate this violation, Entergy: 1) Amended the procedure that includes NPIRs to include the personnel responsible for reviewing and jointly approving revisions; and 2) Revised the other applicable procedures to address actions that are to be performed when there are changes to the NPIR. | 2011-10-03 | 2012-08-16 | Neither Admits nor Denies | SERC reviewed Entergy's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty assessment. Entergy has a documented ICP, which consists of multiple system policies for all areas of compliance including NERC Reliability Standards. The ICP is reviewed on an as-needed basis. The last review took place in the fourth quarter of 2011. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. The Corporate Compliance Committee (CCC) oversees the ongoing development and maintenance of Entergy’s policies and procedures concerning legal compliance issues and business ethics and oversees activities undertaken to promote adherence with such policies and procedures. The CCC meets quarterly and is responsible for the development and the promotion of Entergy’s compliance and business ethics policies and procedures. Entergy’s Corporate Compliance Officer, the Vice-President, Ethics & Compliance, reports directly to the Senior Vice-President & General Counsel, and has independent access to Entergy’s Board of Directors Audit Committee and is a member of the Corporate Compliance Committee.
SERC Reliability Corporation (SERC) | Entergy Corporation (Entergy) | NCR01234 | SERC2011007809 | Settlement Agreement | On August 4, 2011, Entergy, as a Transmission Operator (TOP), self-reported a violation of PRC-001-1 R2.2 because it failed to notify the affected entities or take corrective action in a timely manner on June 4, 2011, when a coupling capacitor voltage transformer (CCVT) on a 500 kV line at the Keo substation failed and the line remained in-service. The violation was discovered on July 26, 2011, during the investigation into events associated with a June 16, 2011 fault on the 500 kV Keo-West Memphis line. The line had remained in service until the June 16, 2011 fault. On June 4, 2011, the CCVT for the Keo-West Memphis line failed, resulting in a loss of voltage inputs to all the associated line relays – two redundant primary relays and a back-up relay. The CCVT failure was recorded in the Entergy operator’s log. The loss of potential input also caused an alarm at the transmission operating center (TOC). Following the failure of the CCVT, the Loss-Of-Potential (LOP) logic blocked the distance element of the two redundant primary relays and the backup relay. As a result, when the Keo-West Memphis line faulted on June 16, 2011, none of the relays tripped to clear the line, which caused two adjacent lines (Keo-Wrightsville and Keo-White Bluff) to trip. The tripping of the two adjacent lines disabled the LOP logic for the backup relay, which tripped and cleared the faulted line. This permitted the two adjacent lines to successfully re-close. Based on this sequence of events involving high capacity 500 kV lines, the failure of the CCVT challenged system reliability. Because of this, Entergy should have notified its Reliability Coordinator (RC) and the affected TOPs and Balancing Authorities (BA) when the CCVT failed. However, Entergy indicated that there was no loss of load or generation as a result of the lines tripping. SERC determined that Entergy was in violation of PRC-001-1 R2.2 because it failed to notify its Reliability Coordinator and affected TOPs and Balancing Authorities about a protective equipment failure that reduced system reliability. | PRC-001-1 | R2.2 | High | Severe | This issue posed a moderate risk to the reliability of the bulk power system. The failure to inform the RC and TOP was compensated for by the automatic operation of the protective scheme. The protective scheme at Keo worked as it was designed; however, the failure of the CCVT challenged the protective scheme because it had to go to the second tier of protection. A CCVT failure could lead to physical damage of the CCVT and surrounding equipment, which could result in a Misoperation of other protective relaying within the substation. In this instance, two additional lines were tripped momentarily but there was no loss of load and no generation tripped off-line. | 6/4/2011 (when the equipment failure occurred) | 6/23/2011 (when the equipment was repaired) | $34,000 (for SERC2011006478, SERC2011006479, SERC2011007809 and SERC2011008456) | Self-Report | To mitigate this violation, Entergy: 1) Established a work management process measures report that will be reviewed on an as-needed basis; 2) Revised the in-service Protection System maintenance procedure to include relaying and Protection System components that require corrective maintenance; 3) Provided refresher training to applicable personnel regarding the work management process responsibilities; 4) Implemented a Protection System response procedure for equipment that alters the normal configurations of the system; and 5) Formalized the training program for the work management process. | 2012-03-26 | 2012-11-05 | Neither Admits nor Denies | SERC reviewed Entergy's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty assessment. Entergy has a documented ICP, which consists of multiple system policies for all areas of compliance including NERC Reliability Standards. The ICP is reviewed on an as-needed basis. The last review took place in the fourth quarter of 2011. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. The Corporate Compliance Committee (CCC) oversees the ongoing development and maintenance of Entergy’s policies and procedures concerning legal compliance issues and business ethics and oversees activities undertaken to promote adherence with such policies and procedures. The CCC meets quarterly and is responsible for the development and the promotion of Entergy’s compliance and business ethics policies and procedures. Entergy’s Corporate Compliance Officer, the Vice-President, Ethics & Compliance, reports directly to the Senior Vice-President & General Counsel, and has independent access to Entergy’s Board of Directors Audit Committee and is a member of the Corporate Compliance Committee.
SERC Reliability Corporation (SERC) | Entergy Corporation (Entergy) | NCR01234 | SERC2011008456 | Settlement Agreement | On October 25, 2011, Entergy, as a Transmission Operator (TOP), self-reported a violation of PRC-001-1 R2.2 because it did not notify the appropriate reliability entities when the Mabelvale substation Auto-Transformer #2 500 kV bus differential relay failed on April 14, 2011. Based on documents provided by Entergy, SERC confirmed that the relay failed on April 14, 2011. At that time, Entergy evaluated the back-up relaying and concluded that it was adequate backup protection. The conclusion was based on a visual inspection of the applicable equipment and drawings. On August 4, 2011, following an engineering study of Protection System response with the primary bus differential relay out of service, Entergy concluded that the back-up protection was not adequate to timely isolate a three-phase fault on the bus section between Auto-Transformer #2 and the 500 kV breaker bay. The back-up relay was incapable of providing instantaneous back-up protection. Entergy also performed system stability studies to simulate this fault condition and concluded that system instability was possible. Because the bus differential relay failure could affect the system reliability, Entergy should have notified its Reliability Coordinator (RC) and affected TOPs and Balancing Authorities (BAs) and taken corrective action as soon as possible. Entergy provided an attestation stating that it had reviewed all necessary documents and determined that there were no other similar issues that had not been reported. SERC determined that Entergy was in violation of PRC-001-1 R2.2 because it failed to notify its RC, and affected TOPs and BAs about the failure of the bus differential relay and did not take corrective action as soon as possible. | PRC-001-1 | R2.2 | High | Severe | This issue posed a moderate risk to the reliability of the bulk power system (BPS). First, failure to communicate a protection system device failure to the RC and affected TOPs and BAs could have resulted in the uninformed functions taking actions that, in combination with the failed device, could have put the BPS into an unanalyzed condition resulting in a more severe transient. However, the failure to inform the RC and TOP was compensated for by the automatic operation of the protective scheme. Second, if a three-phase to ground fault had occurred while the main protective device was not in operation, the back-up protection would not have operated, which could have caused instability. Three-phase to ground faults, however, are rare. Finally, this was not a reportable event and no losses were experienced. | 4/14/2011 (when the equipment failure occurred) | 8/5/2011 (when the equipment was repaired) | $34,000 (for SERC2011006478, SERC2011006479, SERC2011007809 and SERC2011008456) | Self-Report | To mitigate this violation, Entergy: 1) Developed a technical scheme for prioritizing the impact of Protection System issues and trained the appropriate grid personnel; 2) Revised the in-service Protection System maintenance procedure to include criteria for evaluating Protection System risk and the required approval levels; 3) Performed a review of dual instantaneous local protection for 345 kV and above high side buses connected to autotransformers in order to identify if there were any additional issues; 4) Performed a review of dual instantaneous local protection for 345 kV and above high side buses connected to generator step-up transformers in order to identify if there were any additional issues; and 5) Performed system reliability studies for faults on the high side buses that do not have dual instantaneous local protection. | 2012-05-22 | 2012-11-05 | Neither Admits nor Denies | SERC reviewed Entergy's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty assessment. Entergy has a documented ICP, which consists of multiple system policies for all areas of compliance including NERC Reliability Standards. The ICP is reviewed on an as-needed basis. The last review took place in the fourth quarter of 2011. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. The Corporate Compliance Committee (CCC) oversees the ongoing development and maintenance of Entergy’s policies and procedures concerning legal compliance issues and business ethics and oversees activities undertaken to promote adherence with such policies and procedures. The CCC meets quarterly and is responsible for the development and the promotion of Entergy’s compliance and business ethics policies and procedures. Entergy’s Corporate Compliance Officer, the Vice-President, Ethics & Compliance, reports directly to the Senior Vice-President & General Counsel, and has independent access to Entergy’s Board of Directors Audit Committee and is a member of the Corporate Compliance Committee.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2012009094 | Settlement Agreement | On December 30, 2011, IPCO submitted a Self-Report to WECC stating that, as a Balancing Authority (BA), Generator Operator (GOP) and Transmission Operator (TOP), it was in violation of COM-002-2 R2. Specifically, IPCO reported that on December 9, 2009, NV Energy North, a BA, called IPCO's grid operator and requested emergency assistance during an energy emergency alert (EEA). The grid operator, in turn, issued a clear, concise directive via an instant message to IPCO's power supply merchant (PSM). The grid operator did not, however, ensure that the PSM repeated the information back correctly. Although the PSM did schedule 100 MW, as requested in the directive, the PSM did not repeat the directive back to the grid operator. WECC determined that the grid operator failed to ensure the recipient of the directive repeated back the correct information, in violation of COM-002-2 R2. | COM-002-2 | R2 | Medium | High | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the PSM did not repeat to the directive as required by the Standard, the PSM and grid operators were in contact before, during, and after the directive was implemented. Further, in the event the PSM did not carry out the directive, IPCO's grid operators had approved an emergency electricity transaction (emergency tag) which would have been implemented within ten minutes and would have addressed the emergency. IPCO grid operators, not the PSM, are responsible to NV Energy North for implementing the energy schedule. Failure of the PSM to carry out the directive, therefore, would not have affected the implementation of the energy schedule. The grid operator has full control of the energy schedule implementation into IPCO's automatic generation control (AGC) and would have overridden any inaction by the PSM. Lastly, the directive called for an additional 100 MW, which was ultimately scheduled. | 12/9/2009 (when the communications at issue took place) | 12/9/2009 (when the communications at issue took place) | 7000 | Self-Report | To mitigate this violation, IPCO revised its grid operations procedure and re-trained the grid operations staff on COM-002-2 R2 communication requirements. | 2010-07-20 | 2012-05-25 | Does Not Contest | WECC reviewed IPCO's internal compliance program (ICP), which was in place at the time of the violation, and determined it to be a mitigating factor in the penalty determination. IPCO has a comprehensive, established, and documented ICP, which identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change. IPCO (a) has identified and assigned responsibility and accountability to a compliance officer or other high ranking official with independent access to the CEO or equivalent; (b) has one position dedicated to FERC/NERC compliance; (c) has dedicated adequate resources to support its ICP; (d) has fully implemented its program; (e) reviews its ICP at least annually; and (f) participates in outreach compliance program activities. IPCO's ICP (a) is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; (b) has the support and participation of senior management; (c) includes measurable, specific compliance performance targets; (d) requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; (e) has been distributed to all employees and, if applicable, contractors and vendors; (f) includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; (g) includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; and (h) includes a process to prevent recurrence of NERC Reliability Standard Violations.
Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2012010181 | Notice of Confirmed Violation | On May 8, 2012, PGAE submitted a Self-Report to WECC stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1.1b R2 because it failed to follow a voltage order from its Transmission Operator (TOP). PGAE failed to follow its TOP’s voltage control schedule for 3.5 hours on February 1, 2012 from 9:30 a.m. to 1:00 p.m. On January 30, 2012 at 5:57 a.m., PGAE’s Grid Control Center (GCC), PGAE’s TOP, issued a special voltage order to the PGAE operator located at the Drum Hydro Switching Center to maintain 239 kV on the Middle Fork Powerhouse 230 kV bus until further notice. The special voltage order was given to avoid high voltage on the 230 kV system in the area. On February 1, 2012 at 7:00 a.m., the switching center operator assumed his first shift since the special voltage order of 239 kV was issued. At 9:00 a.m., the switching center operator inadvertently increased the voltage on the Middle Fork bus to 245 kV, which was in excess of the order given by the TOP two days prior. The PGAE operator inappropriately operated generating units on the default schedule when PGAE’s TOP’s special voltage orders were to maintain a high voltage of 239 kV. At 1:00 p.m. on February 1, 2012, the switching center operator notified the GCC of the excessive voltage on the 230 kV system. At the direction of the GCC, the switching center operator returned voltage to the special voltage order of 239 kV. | VAR-002-1.1b | R2; R2.1; R2.2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The deviation occurred during low-demand morning load hours for a short time and lasted 3.5 hours before it was corrected. The hydro generation project involved in this violation is small, consisting of two units rated at 61 MVA for a total of 122 MVA. In addition, the entity disciplined the employee involved and instituted a process to prevent recurrence. | 2/1/2012 (when the voltage was increased in excess of the order given by the TOP) | 2/1/2012 (3.5 hours later, when voltage was returned within the range given by the TOP) | 12500 | Self-Report | To mitigate this violation PGAE: 1) Disciplined the employee involved in accordance with PGAE policy and the bargaining unit contract; 2) Established a procedure to review GOP voltage schedule activities regarding: (a) Three-way communication with the GCC; (b) Determination of the current voltage schedule (identifying the actual set point on the Automatic Voltage Regulator, the tolerance band for compliance, and the duration of the current schedule; (c) Verification of the proper response to deviations to the specified voltage schedule; and (d) Set up periodic review of: i) Weekly compliance reviews of voltage-related entries in the Generation Unit Status Scheduling (GUSS) log; and ii) Quality assurance spot check of the GUSS log related to voltage control; and iii) Quarterly spot check of voice recordings. 3) Reviewed the documentation associated with the implementation of focused reviews. Verified that supervisors have implemented the reviews. Validated the results with spot checks and detailed log reviews. | 2012-12-07 | 2013-01-04 | Does Not Contest | WECC reviewed PGAE’s internal compliance program (ICP) and considered it a mitigating factor in the penalty determination. WECC found that: PGAE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGAE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; the ICP has the support and participation of senior management; PGAE reviews and modifies its ICP regularly; and PGAE’s ICP includes formal and internal self-auditing for compliance with all Reliability Standards on a periodic basis. PGAE’s prior violation of VAR-002-1.1b R2 was considered an aggravating factor in the penalty determination. Previously, WECC determined that PGAE failed to maintain a voltage specified by its TOP. This violation was filed on June 30, 2011 as an Administration Citation Notice of Penalty in Docket No. NP11-228-000.