## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC (Altona) | NCR10366 | NPCC2012010202 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Altona, as a Generator Owner (GO) did not have a documented generator Facility Ratings Methodology as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Altona had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Altona’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Altona’s interconnection agreement with the Transmission Owner. The interconnection is between Altona, NYPA, and New York ISO. Furthermore, Altona is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 8/14/2009 (when Altona registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $6,000 (for NPCC2012010202, NPCC2012010204, NPCC2012010493, and NPCC2012010495) | Compliance Audit | To mitigate the violation, Altona developed a Facility Rating Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Altona's internal compliance program was considered to be a neutral factor because although Altona had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC (Altona) | NCR10366 | NPCC2012010204 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Altona, as a Generator Owner (GO) did not have a documented generator Facility Ratings Methodology and therefore did not establish Facility Ratings consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Altona had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Altona’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Altona’s interconnection agreement with the Transmission Owner. The interconnection is between Altona, NYPA, and New York ISO. Furthermore, Altona is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 8/14/2009 (when Altona registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010202, NPCC2012010204, NPCC2012010493, and NPCC2012010495) | Compliance Audit | To mitigate the violation, Altona: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility rating to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Altona's internal compliance program was considered to be a neutral factor because although Altona had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC (Altona) | NRC10366 | NPCC2012010493 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Altona, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES) as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Altona did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, it did have a spreadsheet that provided testing intervals for their relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Altona is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 8/14/2009 (when Altona registered as a GO) | 6/29/2012 (when Altona documented its Protection System maintenance and testing program) | $6,000 (for NPCC2012010202, NPCC2012010204, NPCC2012010493, and NPCC2012010495) | Compliance Audit | To mitigate the violation, Altona developed a comprehensive Protection System maintenance and testing program which included maintenance testing intervals and their basis, and maintenance and testing procedures. The program provides relay types, testing to be performed, testing intervals, and their basis. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Altona's internal compliance program was considered to be a neutral factor because although Altona had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC (Altona) | NRC10366 | NPCC2012010495 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Altona, as a Generator Owner (GO), failed to provide evidence of testing for monthly visual inspections and annual testing for its batteries as required by its Protection System maintenance and testing program, resulting in a violation of PRC-005-1 R2. This violation comprises 100% of the applicable devices. Altona was able to provide testing data for 34.5 kV current transformers (CTs) and relays and after review and additional documentation the CTs/ potential transformers (PTs) and relay testing was verified. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Altona could not provide evidence of visual inspections of the batteries, it was able to provide evidence of battery testing for July 2008 during commissioning of the Altona generating facility. Also Altona's batteries are 125 volt sealed recombination type batteries, sealed units, and described as maintenance-free type units by the manufacturer. Furthermore, Altona is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 8/14/2009 (when Altona registered as a GO) | 10/5/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010202, NPCC2012010204, NPCC2012010493, and NPCC2012010495) | Compliance Audit | To mitigate the violation, Altona completed maintenance and testing of Protection System components, provided sufficient documentation that the Protection System maintenance and testing was performed, and provided evidence of the last test date or maintenance date of Protection System components. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Altona's internal compliance program was considered to be a neutral factor because although Altona had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC (Bliss) | NCR10271 | NPCC2012010209 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Bliss, as a Generator Owner (GO) did not have a documented generator Facility Rating Methodology as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Bliss had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Bliss’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Bliss's interconnection agreement with the Transmission Owner. The interconnection is between Bliss, NYPA, and Village of Arcade. Furthermore, Bliss is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Bliss registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $5,000 (for NPCC2012010209, NPCC2012010211, and NPCC2012010481) | Compliance Audit | To mitigate the violation, Bliss developed a Facility Rating Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Bliss's internal compliance program was considered to be a neutral factor because although Bliss had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC (Bliss) | NCR10271 | NPCC2012010211 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Bliss, as a Generator Owner (GO) did not have a documented generator Facility Rating Methodology and therefore did not establish Facility Ratings consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Bliss had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Bliss’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Bliss's interconnection agreement with the Transmission Owner. The interconnection is between Bliss, NYPA, and Village of Arcade. Furthermore, Bliss is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Bliss registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $5,000 (for NPCC2012010209, NPCC2012010211, and NPCC2012010481) | Compliance Audit | To mitigate the violation, Bliss completed the following activities: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility ratings to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Bliss's internal compliance program was considered to be a neutral factor because although Bliss had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC (Bliss) | NCR10271 | NPCC2012010481 |  | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Bliss, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES) as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Bliss did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, it had a spreadsheet that provided testing intervals for its relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Bliss is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 10/15/2008 (when Bliss registered as a GO) | 6/29/2012 (when Bliss documented its Protection System maintenance and testing program) | $5,000 (for NPCC2012010209, NPCC2012010211, and NPCC2012010481) | Compliance Audit | To mitigate the violation, Bliss developed a comprehensive Protection System maintenance and testing program which includes maintenance testing intervals and their basis, and maintenance and testing procedures. The program provides relay types, testing to be performed, testing intervals, and their basis. | 2012-10-05 | 2012-10-19 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Bliss's internal compliance program was considered to be a neutral factor because although Bliss had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC (Chateaugay) | NCR10367 | NPCC2012010216 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Chateaugay, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology, as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Chateaugay had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2007, as part of the commissioning of the unit, to evaluate the impact of Chateaugay’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Chateaugay's interconnection agreement with the Transmission Owner. The interconnection is between Chateaugay, NYPA, and New York ISO. Furthermore, Chateaugay is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Chateaugay registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $6,000 (for NPCC2012010216, NPCC2012010218, NPCC2012010708, and NPCC2012010486) | Compliance Audit | To mitigate the violation, Chateaugay developed a Facility Ratings Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Chateaugay's internal compliance program was considered to be a neutral factor because although Chateaugay had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC (Chateaugay) | NCR10367 | NPCC2012010218 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Chateaugay, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology and therefore did not establish Facility Ratings consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Chateaugay had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2007, as part of the commissioning of the unit, to evaluate the impact of Chateaugay’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Chateaugay's interconnection agreement with the Transmission Owner. The interconnection is between Chateaugay, NYPA, and New York ISO. Furthermore, Chateaugay is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Chateaugay registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010216, NPCC2012010218, NPCC2012010708, and NPCC2012010486) | Compliance Audit | To mitigate the violation, Chateaugay: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility rating to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Chateaugay's internal compliance program was considered to be a neutral factor because although Chateaugay had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC (Chateaugay) | NCR10367 | NPCC2012010708 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Chateaugay, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES), as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Chateaugay did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, it did have a spreadsheet that provided testing intervals for its relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Chateaugay is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Chateaugay registered as a GO) | 6/29/2012 (when Chateaugay documented its Protection System maintenance and testing program) | $6,000 (for NPCC2012010216, NPCC2012010218, NPCC2012010708, and NPCC2012010486) | Compliance Audit | To mitigate the violation, Chateaugay developed a comprehensive Protection System maintenance and testing program which included maintenance testing intervals and their basis, and maintenance and testing procedures. The program provides relay types, testing to be performed, testing intervals, and their basis. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Chateaugay's internal compliance program was considered to be a neutral factor because although Chateaugay had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC (Chateaugay) | NCR10367 | NPCC2012010486 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Chateaugay, as a Generator Owner (GO), failed to provide evidence of monthly visual inspections and annual testing for its batteries, as required by its Protection System maintenance and testing program, resulting in a violation of PRC-005-1 R2. This violation comprises 100% of the applicable devices. Chateaugay was able to provide testing data for 34.5 kV current transformers (CTs) and relays and after review and additional documentation the CTs/ potential transformers (PTs) and relay testing was verified. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Chateaugay could not provide evidence of annual testing and monthly visual inspections for its batteries, they were tested during commissioning and again in July, 2010. Testing included measurement of specific gravity, cell voltage, intercell resistance, and water level check. All test results were satisfactory. Furthermore, Chateaugay is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Chateaugay registered as a GO) | 10/5/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010216, NPCC2012010218, NPCC2012010708, and NPCC2012010486) | Compliance Audit | To mitigate the violation, Chateaugay completed maintenance and testing of Protection System components, provided sufficient documentation that the Protection System maintenance and testing was performed, and provided evidence of the last test date or maintenance date of Protection System components. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Chateaugay's internal compliance program was considered to be a neutral factor because although Chateaugay had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC (Clinton) | NCR10272 | NPCC2012010195 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Clinton, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Clinton had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Clinton’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Clinton’s interconnection agreement with the Transmission Owner. The interconnection is between Clinton, NYPA, and New York ISO. Furthermore, Clinton is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Clinton registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $6,000 (for NPCC2012010195, NPCC2012010197, NPCC2012010483, and NPCC2012010487) | Compliance Audit | To mitigate the violation, Clinton developed a Facility Rating Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Clinton's internal compliance program was considered to be a neutral factor because although Clinton had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC (Clinton) | NCR10272 | NPCC2012010197 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Clinton, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology and therefore did not establish Facility Ratings consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Clinton had not documented a Facility Ratings Methodology, it conducted a System Reliability Impact Study in 2006, as part of the commissioning of the unit, to evaluate the impact of Clinton’s generating facility on the reliability of the New York State Transmission System. This study was made in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Clinton’s interconnection agreement with the Transmission Owner. The interconnection is between Clinton, NYPA, and New York ISO. Furthermore, Clinton is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Clinton registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010195, NPCC2012010197, NPCC2012010483, and NPCC2012010487) | Compliance Audit | To mitigate the violation, Clinton: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility rating to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Clinton's internal compliance program was considered to be a neutral factor because although Clinton had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC (Clinton) | NCR10272 | NPCC2012010483 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Clinton, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES) as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Clinton did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, they did have a spreadsheet that provided testing intervals for their relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Clinton is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Clinton registered as a GO) | 6/29/2012 (when Clinton documented its Protection System maintenance and testing program) | $6,000 (for NPCC2012010195, NPCC2012010197, NPCC2012010483, and NPCC2012010487) | Compliance Audit | To mitigate the violation, Clinton developed a comprehensive Protection System maintenance and testing program which included maintenance testing intervals and their basis, and maintenance and testing procedures. The program provides relay types, testing to be performed, testing intervals, and their basis. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Clinton's internal compliance program was considered to be a neutral factor because although Clinton had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC (Clinton) | NCR10272 | NPCC2012010487 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Clinton, as a Generator Owner (GO), failed to provide evidence of testing for monthly visual inspections and annual testing for its batteries as required by its Protection System maintenance and testing program, resulting in a violation of PRC-005-1 R2. This violation comprises 100% of the applicable devices. Clinton was able to provide testing data for 34.5 kV current transformers (CTs) and relays and after review and additional documentation the CTs/ potential transformers (PTs) and relay testing was verified. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Clinton could not provide evidence of visual inspections of the batteries, it was able to provide evidence of battery testing for July 2008 during commissioning of the Clinton generating facility. Also, Clinton's batteries are 125 volt sealed recombination type batteries, sealed units, and described as maintenance-free type units by the manufacturer. Furthermore, Clinton is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | 10/15/2008 (when Clinton registered as a GO) | 10/5/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010195, NPCC2012010197, NPCC2012010483, and NPCC2012010487) | Compliance Audit | To mitigate the violation, Clinton completed maintenance and testing of Protection System components, provided sufficient documentation that the Protection System maintenance and testing was performed, and provided evidence of the last test date or maintenance date of Protection System components. | 2012-10-05 | 2012-10-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Clinton's internal compliance program was considered to be a neutral factor because although Clinton had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC (Ellenburg) | NCR10273 | NPCC2012010223 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Ellenburg, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Ellenburg had not documented a Facility Ratings Methodology, it conducted a system reliability impact study in 2007, as part of the commissioning of the unit, to evaluate the impact of Ellenburg’s generating facility on the reliability of the New York State Transmission System. This study was conducted in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Ellenburg’s interconnection agreement with the Transmission Owner. The interconnection is between Ellenburg, NYPA, and New York ISO. Furthermore, Ellenburg is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 10/15/2008 (when Ellenburg registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $6,000 (for NPCC2012010223, NPCC2012010225, NPCC2012010484, and NPCC2012010488) | Compliance Audit | To mitigate the violation, Ellenburg developed a Facility Ratings Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Ellenburg's internal compliance program was considered to be a neutral factor because although Ellenburg had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC (Ellenburg) | NCR10273 | NPCC2012010225 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Ellenburg, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology and therefore could not have facility ratings consistent with the methodology as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Ellenburg had not documented a Facility Ratings Methodology, it conducted a system reliability impact study in 2007, as part of the commissioning of the unit, to evaluate the impact of Ellenburg’s generating facility on the reliability of the New York State Transmission System. This study was conducted in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Ellenburg’s interconnection agreement with the Transmission Owner. The interconnection is between Ellenburg, NYPA, and New York ISO. Furthermore, Ellenburg is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 10/15/2008 (when Ellenburg registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010223, NPCC2012010225, NPCC2012010484, and NPCC2012010488) | Compliance Audit | To mitigate the violation, Ellenburg: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility rating to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Ellenburg's internal compliance program was considered to be a neutral factor because although Ellenburg had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC (Ellenburg) | NCR10273 | NPCC2012010484 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Ellenburg, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES) as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Ellenburg did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, they did have a spreadsheet that provided testing intervals for their relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Ellenburg is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 10/15/2008 (when Ellenburg registered as a GO) | 6/29/2012 (when Ellenburg documented its Protection System maintenance and testing program) | $6,000 (for NPCC2012010223, NPCC2012010225, NPCC2012010484, and NPCC2012010488) | Compliance Audit | To mitigate the violation, Ellenburg developed a comprehensive Protection System maintenance and testing program document which included maintenance testing intervals and their basis, and maintenance testing procedures. The program provides relay types, testing to be performed, testing intervals, and their basis. | 2012-10-05 | 2013-01-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Ellenburg's internal compliance program was considered to be a neutral factor because although Ellenburg had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC (Ellenburg) | NCR10273 | NPCC2012010488 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Ellenburg, as a Generator Owner (GO), failed to provide evidence for complete testing of their batteries as required by its Protection System maintenance and testing program, resulting in a violation of PRC-005-1 R2. This comprises 100% of the applicable devices. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system Although Ellenburg could not provide evidence of monthly visual inspections for their batteries, they were tested during commissioning and again in July, 2010. Testing included measurement of specific gravity, cell voltage, intercell resistance, and water level check. All tests were satisfactory. Furthermore, Ellenburg is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 10/15/2008 (when Ellenburg registered as a GO) | 10/5/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010223, NPCC2012010225, NPCC2012010484, and NPCC2012010488) | Compliance Audit | To mitigate the violation, Ellenburg completed testing and visual inspection of batteries, provided sufficient documentation that the Protection System maintenance and testing was performed, and provided evidence of the last test date or maintenance date for the batteries. | 2012-10-05 | 2013-01-18 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Ellenburg's internal compliance program was considered to be a neutral factor because although Ellenburg had compliance mechanisms in place, it did not have a formalized compliance program or documentation of that program until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC (Wethersfield) | NCR10368 | NPCC2012010230 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Wethersfield, as a Generator Owner (GO), did not have a documented generator Facility Ratings Methodology as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Wethersfield had not documented a Facility Ratings Methodology, it conducted a system reliability impact study in 2007, as part of the commissioning of the unit, to evaluate the impact of Wethersfield’s generating facility on the reliability of the New York State Transmission System. This study was conducted in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Wethersfield’s interconnection agreement with the Transmission Owner. The interconnection is between Wethersfield, NYPA, and New York ISO. Furthermore, Wethersfield is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Wethersfield registered as a GO) | 9/25/2011 (Mitigation Plan completion) | $6,000 (for NPCC2012010230, NPCC2012010232, NPCC2012010485, and NPCC2012010489) | Compliance Audit | To mitigate the violation, Wethersfield developed a Facility Rating Methodology document. | 2011-09-25 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Wethersfield's internal compliance program was considered to be a neutral factor because although Wethersfield had compliance mechanisms in place, it did not have a formalized Compliance Program or documentation of that program in place until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC (Wethersfield) | NCR10368 | NPCC2012010232 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Wethersfield, as a Generator Owner (GO), did not have a documented generator Facility Rating Methodology and therefore did not establish Facility Ratings consistent with the associated Facility Ratings Methodology as required by FAC-009-1 R1. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Wethersfield had not documented a Facility Ratings Methodology, it conducted a system reliability impact study in 2007, as part of the commissioning of the unit, to evaluate the impact of Wethersfield’s generating facility on the reliability of the New York State Transmission System. This study was conducted in accordance with the applicable NERC, NPCC, New York State Reliability Council, L.L.C., New York Power Authority (NYPA), and affected system(s) reliability and design standards. Facility ratings were established per Wethersfield’s interconnection agreement with the Transmission Owner. The interconnection is between Wethersfield, NYPA, and New York ISO. Furthermore, Wethersfield is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Wethersfield registered as a GO) | 7/27/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010230, NPCC2012010232, NPCC2012010485, and NPCC2012010489) | Compliance Audit | To mitigate the violation, Wethersfield: 1) Developed a Facility Rating Methodology document; and 2) Completed the review of individual equipment ratings and determined the most limiting component and provided the facility rating to the Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator as appropriate. | 2012-07-27 | 2012-10-23 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Wethersfield's internal compliance program was considered to be a neutral factor because although Wethersfield had compliance mechanisms in place, it did not have a formalized Compliance Program or documentation of that program in place until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC (Wethersfield) | NCR10368 | NPCC2012010485 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Wethersfield, as a Generator Owner (GO), did not have a documented Protection System maintenance and testing program for Protection Systems that affect the reliability of the Bulk Electric System (BES) as required by PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Wethersfield did not have a documented Protection System maintenance and testing program for Protection Systems that affect the BES, they did have a spreadsheet that provides testing intervals for their relays and batteries. The interval criteria were established utilizing American National Standards Institute/ InterNational Electrical Testing Association standards and NPCC Directory D-3 "Maintenance Criteria for Bulk Power Systems." Furthermore, Wethersfield is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Wethersfield registered as a GO) | 6/29/2012 (when Wethersfield documented its Protection System maintenance and testing program) | $6,000 (for NPCC2012010230, NPCC2012010232, NPCC2012010485, and NPCC2012010489) | Compliance Audit | To mitigate the violation, Wethersfield developed a comprehensive Protection System maintenance and testing program which included maintenance testing intervals and their basis, and maintenance testing procedures. The program provides relay types, testing to be provided, testing intervals, and their basis. | 2012-10-05 | 2012-10-24 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Wethersfield's internal compliance program was considered to be a neutral factor because although Wethersfield had compliance mechanisms in place, it did not have a formalized Compliance Program or documentation of that program in place until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC (Wethersfield) | NCR10368 | NPCC2012010489 | Settlement Agreement | During an off-site Compliance Audit conducted from May 16, 2011 to July 1, 2011, NPCC determined that Wethersfield, as a Generator Owner (GO), failed to provide evidence for complete testing of their DC circuits as required by its Protection System maintenance and testing program, resulting in a violation of PRC-005-1 R2. This comprises fewer than 10% of the applicable devices. | PRC-005-1 | R2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Wethersfield could not provide documentation for complete testing of their DC circuits, documentation of testing was provided for major components of the tripping circuit. Also, testing was conducted on the entire relay systems as part of the commissioning of the facility in 2008. Furthermore, Wethersfield is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | 8/14/2009 (when Wethersfield registered as a GO) | 10/5/2012 (Mitigation Plan completion) | $6,000 (for NPCC2012010230, NPCC2012010232, NPCC2012010485, and NPCC2012010489) | Compliance Audit | To mitigate the violation, Wethersfield completed maintenance and testing of Protection System components and provided sufficient documentation that the Protection System maintenance and testing was performed and provided evidence of the last test date or maintenance date of Protection System components. | 2012-10-05 | 2012-10-24 | Does Not Contest | NPCC considered the following factors in the penalty determination: 1) This was the first violation for this Standard and Requirement; 2) Cooperation of entity in Mitigation Plan process; and 3) Wethersfield's internal compliance program was considered to be a neutral factor because although Wethersfield had compliance mechanisms in place, it did not have a formalized Compliance Program or documentation of that program in place until 2012. Five Spreadsheet Notices of Penalty (SNOP) are being filed concurrently with the instant SNOP. One for each of the Noble Environmental Power windparks in NPCC.
SERC Reliability Corporation (SERC) | East Texas Electric Cooperative Inc. (ETEC) | NCR01227 | SERC2011007373 | Settlement Agreement | On May 27, 2011, ETEC, as a Generator Owner (GO), self-reported two violations of PRC-005-1 R1. Specifically, the Protection System maintenance and testing program for two of its generation facilities did not include a summary of maintenance and testing procedures for station batteries, maintenance and testing intervals or the basis for the intervals for any of the elements of the Protection System. Prior to 2009, ETEC had only partial ownership in several generation units. Another entity, the majority owner of the units, performed all the GO and Generator Operator (GOP) functions. ETEC later became the sole owner of two generating units: 1) the San Jacinto County Peaking Facility, which went into commercial operation on July 19, 2009; and 2) the Hardin County Peaking Facility, which went into commercial operation on January 16, 2010. During a mock audit the week of April 14, 2011, ETEC was unable to locate a Protection System maintenance and testing procedure in its files. Instead, it located a procedure for the startup and commissioning of electrical equipment which was used to conduct the initial commissioning tests of all of ETEC’s Protection System devices at its San Jacinto and Hardin facilities. SERC determined that this procedure was not an adequate Protection System maintenance and testing procedure. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated by the following: 1) All of ETEC’s Protection System devices were tested upon commissioning; 2) The intervals in the startup and commissioning procedure for DC control circuitry, relays and instrument transformers were 6, 8, and 12 years, respectively. Therefore, none of these devices have come due for testing since commissioning. In addition, ETEC does not have any associated communication devices; 3) The batteries at San Jacinto are checked on a daily basis as part of the plant operator’s walk down procedure. The batteries at Hardin are checked on a weekly basis as part of the plant operator’s walk down procedure; The plant operators at both units check the battery bank voltage and current at the battery chargers and verify that the water levels are above the low fill lines; 4) The relays are alarmed back through the distributed control system to the operator’s console. There have been no trouble alarms indicating problems with the relays themselves at either plant since commissioning. In addition, plant personnel perform daily rounds to observe relays for any abnormal conditions and note anomalies to be followed up on; and 5) These facilities are peaking units and have had annual capacity factors ranging from a low of 4.4% to a high of 14.7% since 2010. | 7/19/2009 (when the San Jacinto facility became commercially operational) | 3/16/2012 (Mitigation Plan completion) | 0 | Self-Report | To mitigate this violation, ETEC: 1) Developed a generation Protection System maintenance and testing program using NERC guidance documents and national standards and incorporated it into an existing ETEC policy, guideline, and procedure ((PGP)) document addressing Protection System maintenance and testing; 2) Reviewed the modified PGP document with the Internal Compliance Committee ((ICC)), ETEC, and GOP personnel and made changes as necessary; 3) Received approval from the ICC and implemented the updated PGP at the San Jacinto and Hardin generating facilities; 4) Provided training to the GOP and ETEC personnel on the updated PGP document; and 5) The GOP updated the computerized maintenance management system to include all elements of the ETEC generation Protection System maintenance and testing program. | 2012-03-16 | 2012-12-10 | Admits | According to ETEC’s August 4, 2011 response to SERC’s Compliance Culture Questionnaire, ETEC has had an Internal Compliance Program (ICP) since July 26, 2010. SERC considered ETEC's ICP a mitigating factor in penalty determination. The ICP names an ICC which serves as the overall governing group for ETEC's compliance activities. The ICC includes the Compliance Officer, Compliance Manager, and subject matter experts representing all of ETEC’s NERC registration types. The ICP and any subsequent revisions are distributed electronically to all ETEC employees, contractors, and consultants who are responsible for ensuring ETEC’s compliance with all NERC Reliability Standards. ETEC's Compliance Manager reports to the Compliance Officer who reports directly to the General Manager. Both the Compliance Manager and Compliance Officer have direct access to the General Manager if needed. The ICP is reviewed at least annually by ETEC staff and is approved by the General Manager. The ICP also requires that ETEC hold annual NERC Reliability Standards training for employees responsible for compliance, and ETEC employees are subject to disciplinary action, consistent with ETEC disciplinary policies, for failure to carry out job duties in a manner consistent with the ICP. ETEC has a prior violation of PRC-005-1 R1 which was filed with FERC under NP08-17-000 on June 4, 2008. SERC did not consider ETEC's prior violation of PRC-005-1 R1 an aggravating factor in the penalty determination because the prior violation occurred under ETEC's Transmission Owner function, for which ETEC is no longer registered.
SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC201000624 | Settlement Agreement | On September 24, 2010, PEC, as a Generator Operator (GOP), self-reported a violation of VAR-002-1 R3 after it had discovered 14 occasions when PEC had failed to notify the Transmission Operator (TOP) of a status or capability change of its automatic voltage regulators (AVR) and the expected duration of the change in status or capability. According to PEC, the discoveries were made through an internal review of generation plant and Energy Control Center (ECC) manual logs and voice recordings. As part of its assessment, SERC staff discussed with PEC the circumstances surrounding the 14 occasions. In addition to the change of status of the AVRs, PEC had not notified the TOP regarding the power system stabilizer (PSS) status change for those units with a PSS. SERC staff also reviewed PEC’s VAR-002 reporting procedures and determined that the procedures were not contributing factors to the violation. Rather, the cause of the violation was inadequate operator training resulting in operator uncertainty of whether or not to report various unique situations. In an effort to assess the risk to the bulk power system (BPS), SERC questioned PEC regarding its system configuration, its historical records, as well as its procedures and processes for coordination between PEC and the TOP. PEC reported that no outages or loss of load, no system voltage or stability issues, and no damage to equipment resulted from any of the 14 occasions. The PEC System is supported by 18 generating plants dispersed across its transmission system. At these plants, PEC has a total of 71 units. The overall PEC system is capable of generating more than 11,500 MW. Such a design reduces the impact to the overall system voltage in the event of the loss of an individual AVR control. According to PEC, each morning its TOP calls all of the PEC GOPs. The focus of these calls is to discuss the status of each plant, with specific discussion on current operations as well as the projected operations for the next seven days. During these calls the TOPs and GOPs discuss any concerns involving system voltage or system stability as applicable. SERC determined that PEC was in violation of VAR-002-1 R3 because it failed to notify the TOP within 30 minutes of the change in status of Reactive Power resources and the expected duration of the change, as required. | VAR-002-1 | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because: 1) PEC has daily calls between its TOP and GOPs that provide the TOP with the current and the expected status of all of the plants and the associated generator Reactive Power resources. These calls should have identified any voltage regulation concerns had they existed; 2) Half of the reported instances were associated with units that are less than 75 MW in size; 3) PEC reported that no outages or loss of load from any of the 14 occasions; 4) The PEC System is supported by 18 generating plants, consisting of 71 units, that are dispersed across its transmission system. The overall PEC system is capable of generating more than 11,500 MW. Such a design reduces the impact to the overall system voltage in the event of the loss of an individual AVR control; and 5) PEC has had no reported instances of noncompliance with VAR-002 R2, indicating that it is able to maintain voltage per the TOP provided voltage schedule. | 5/3/2008 (when the 2008 Compliance Audit was completed) | Present | 12000 | Self-Report | PEC completed the following mitigating activities: 1) Issued a corrective action to all plants reinforcing and verifying the existing VAR-002 procedures; 2) Issued required reading to applicable nuclear plant personnel regarding VAR-002 requirements; 3) Issued a standing order to all plant control room operators clarifying and reinforcing the VAR-002 requirements; 4) Performed a structured diagnostic of the existing VAR-002 procedures, processes and training in order to identify possible gaps and identify solutions to those gaps; 5) Created and implemented a new module for VAR-002 reporting and communications; 6) Created training materials and trained applicable personnel on the new module; and 7) Performed a survey of all generating units regarding PSS status. PEC will complete the following mitigating activities: 1) Enter a contract with a vendor to upgrade the VAR-002 module with PSS status change (March 31, 2013); 2) Develop training materials that address the modification to the VAR-002 module (May 15, 2013); 3) Train the operators on the modification (August 1, 2013); and 4) Deploy the updated VAR-002 module (August 15, 2013). | 8/15/2013 (approved completion date) | TBD | Neither Admits nor Denies | At the time of the violation and self-reporting, PEC followed the documented internal compliance program (ICP) of its parent company, Progress Energy. The existence of the ICP was a mitigating factor in determining the penalty. The ICP was initially approved on December 13, 2007, and was developed to formally document and drive existing compliance business practices. PEC’s ICP was disseminated to all organizations within PEC that must comply with NERC Standards. Progress Energy’s ICP was prepared for and approved by Progress Energy’s electric reliability organization (ERO) Steering Committee. The ERO Steering Committee was comprised of officers of PEC and Progress Energy Florida and was chaired by the ERO Compliance Officer, who is Progress Energy’s Executive Vice President – General Counsel and Corporate Secretary. The ERO Compliance Officer was independent of all PEC organizations that must comply with NERC Standards. The ERO Compliance Officer reported directly to the Chairman/President/CEO and had direct access to the Board of Directors. Company officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments.
SERC Reliability Corporation (SERC) | Southern Company Services, Inc. - Gen (SCS-Gen) | NCR01319 | SERC2012010573 | Settlement Agreement | On June 22, 2012, SCS-Gen, as a Generator Operator, self-reported a violation of VAR-002-1.1b R3 because the automatic voltage regulator (AVR) on Hammond Unit 4 operated in manual mode without appropriate notification to the Transmission Operator (TOP). SERC learned that the AVR on the Hammond Unit 4 generator tripped from automatic voltage control mode to manual mode at 9:19 a.m. on May 30, 2012 and remained in manual mode throughout the day shift for approximately 11 hours. The evening shift operator identified the issue, changed the AVR to "Auto," and provided notification to the TOP. According to SCS-Gen, the distributed control system (DCS) at Hammond Unit 4 had been replaced with a new DCS. At the time of the violation, the new DCS controls were being tuned so the operator relied on the audible alarm for changes in AVR status however, the alarm was not yet configured in the new DCS. SERC verified that Hammond Unit 4 maintained its voltage schedules throughout the time period. SERC determined that SCS-Gen was in violation of VAR-002-1.1b R3.1 for failing to notify its TOP within 30 minutes of a status or capability change of the AVR, as required. | VAR-002-1.1b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) The Bowen Unit 1 (754 MW) and Rocky Mountain Units 1, 2 and 3 (collectively 897 MW) were online in the area and managing 230 kV voltage during the time the AVR was in manual mode; 2) When the AVR was operating in manual mode, it did not deviate from the established voltage schedule; and 3) The plant operator was not directed by the TOP to adjust voltage during the period the AVR was in manual mode. | 5/30/2012 (30 minutes after the AVR changed from "Auto" to "Manual" mode) | 5/30/2012 (when notification to the TOP was made) | 5000 | Self-Report | To mitigate this violation, SCS-Gen: 1) Added a telemetered data point for real-time indication of AVR status from Hammond Unit 4 to the Energy Management System; 2) Configured an audible alarm for a change in AVR status in the Hammond Unit 4 DCS; and 3) Conducted an assessment of all generating plants (not exempt from voltage schedule) to ensure that each unit that had experienced a DCS conversion/replacement since June 2007, and did not have an audible DCS alarm configured for AVR status change to “Manual,” had some other compensating measure in place. | 2012-06-22 | 2012-09-24 | Admits | SERC reviewed SCS-Gen's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SCS-Gen follows Southern Company’s Compliance Framework Manual, which has been in place since January 8, 2001. Details of the compliance program are available internally through the intra-company web site. Compliance related information is regularly communicated through various means including, e-mail, newsletters, web-based, and classroom training sessions. SCS-Gen has a Compliance Officer, who reports directly to the Senior Vice-President & General Counsel and has direct access to Southern Company's Chief Operating Officer. Southern Company’s compliance program is fully supported by company officers and senior management. Southern Company's compliance program is regularly reviewed by senior management and is subject to internal audit. The individual performance of employees is evaluated on a regular basis. These evaluations include an assessment of how the employee complied with laws, regulations and company policies. A Settlement Agreement covering violations of VAR-002-1.1b R3 and VAR-002-1 R3.1 for SGS-Gen was filed with FERC under NP12-27-000 on May 30, 2012. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that SCS-Gen’s previous violations constituted prior violations but were not considered aggravating factors in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Independence Power & Light (Independence, Missouri) (Independence) | NCR01072 | SPP201000215 | Settlement Agreement | During a Compliance Audit conducted from March 15, 2010 through March 18, 2010, SPP RE determined that Independence, as a Distribution Provider, Generator Owner and Transmission Owner, had a violation of PRC-005-1 R1. SPP RE determined that Independence's documented Protection System maintenance and testing program did not have a procedure in place to address DC control circuitry, in violation of PRC-005-1 R1.2. Furthermore, although the Protection System maintenance and testing program had a procedure which indicated that instrument transformers were to be tested upon commissioning and "for cause" in the event of an incorrect operation, the procedure failed to define a testing interval for instrument transformers. Additionally, the Protection System maintenance and testing program document failed to indicate the basis for any of the identified testing intervals, in violation of R1.1. Independence's failure to implement a Protection System maintenance and testing program consistent with the requirements of PRC-005-1 resulted in its failure to document maintenance and testing of 183 of its 333 (55.0%) Protection System devices. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | SPP RE determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Over half of Independence's Protection System devices were not included in its Protection System maintenance and testing program. As a result, those devices were more likely to be in a condition that would prevent them from operating properly to perform their intended function which is to limit the effects of disturbances. Although Independence's DC control circuitry was omitted from the PRC-005-1 procedure and instrument transformers were not assigned testing intervals, Independence did have assigned intervals for protective relays, associated communication devices, and station batteries that were consistent with the intervals set forth in the NERC Protection System Maintenance - A Technical Reference dated September 13, 2007 (Technical Reference). Independence's procedure called for three-year intervals for functional testing and five-year intervals for calibration testing, which are both under the maximum allowable interval of five years for unmonitored protective relays per the Technical Reference. All of Independence's communications systems associated with its Protection Systems qualify as partially monitored pursuant to the categories set forth in the Technical Reference, which provides that the maximum allowable interval for such systems is seven years, while Independence's procedure provided for four-year intervals. For station batteries, the Technical Reference provides for one-month intervals for unmonitored batteries and seven years for partially monitored batteries, while Independence, which owns four monitored batteries and three unmonitored batteries, had its intervals set at one year. Additionally, at the time of the violation, Independence had a peak load of 315 MW and owned only three transmission lines at 100 kV or above. These three lines totaled 23 miles serving a 46-mile looped 69 kV transmission system. | 6/18/2007 (when the Standard became mandatory and enforceable) | 7/5/2010 (Mitigation Plan completion) | $18,000 (for SPP201000215 and SPP201000216) | Compliance Audit | In accordance with its Mitigation Plan, Independence revised its Protection System maintenance and testing procedure to include all required devices and provided the basis for the intervals that were set. | 2010-07-05 | 2010-09-08 | Neither Admits nor Denies | SPP RE observed that Independence did not have a documented internal compliance program (ICP) at the time of the violation, however, it was established in writing on August 17, 2011. SPP RE considered Independence's ICP as a neutral factor in the penalty determination. Independence created the position of NERC Compliance Officer in 2009 to handle compliance duties. Before that time, NERC compliance had been assigned to a task force of managers and supervisors, with many duties assigned to the System Operations Supervisor. A second supervisory control and data acquisition/energy management system technician was added to System Operations. This person has been charged with CIP compliance. SPP RE observed that the NERC Compliance Officer reports to the Power Engineering Manager/Chief Security Officer who reports jointly to the Power & Light Director and Deputy Director. The NERC Compliance Officer oversees compliance efforts which include the development, implementation and management of a program of action designed to effectively collect, review and store documentation of all compliance measures being implemented by Independence. Managers are kept informed of NERC requirements on a regular basis through monthly Security Work Group meetings and by forwarding emails regarding NERC activities. Program requirements are presently disseminated directly to all senior management, managers, supervisors, and System Operations personnel through presentations, training, and informational emails.
Southwest Power Pool Regional Entity (SPP RE) | Independence Power & Light (Independence, Missouri) (Independence) | NCR01072 | SPP201000216 | Settlement Agreement | During a Compliance Audit conducted from March 15, 2010 through March 18, 2010, SPP RE determined that Independence, as a Distribution Provider, Generator Owner and Transmission Owner, had a violation of PRC-005-1 R2. Independence had a documented Protection System maintenance and testing program in place, but was not adhering to the testing intervals set forth in the program. Independence had 141 of 161 (87.6%) protective relays that had not been tested within the established testing intervals as required by PRC-005-1 R2.1, and no evidence of the last test date could be provided for 11 of these 141 Protection System relays, as required by PRC-005-1 R2.2. For 9 of 9 associated communications systems, 131 of 131 instrument transformers, 7 of 7 station batteries, and 25 of 25 DC control circuits, Independence was unable to provide evidence of the last date each device was tested, as required by R2.2. As a result, Independence also could not demonstrate adherence to testing intervals for those devices. In the case of instrument transformers and DC control circuitry, Independence’s PRC-005 testing program failed to define intervals within which the devices were to be tested. The Protection System devices that were either out of testing intervals or had missing test data represented 94% of the 333 Protection System devices. | PRC-005-1 | R2 R2.1; R2.2 | High | Severe | SPP RE determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A total of 94% of Independence's Protection System devices were not compliant with PRC-005-1 R2. As a result, those devices were more likely to be in a condition that would prevent them from operating properly to perform their intended function which is to limit the effects of disturbances. The Independence PRC-005 testing program for protective relays required a functional test every five years and a calibration test every three years. Independence adhered to these intervals for 20 of its 161 relays (12.4%). Of the 130 out-of-interval relays for which evidence of the last test date existed, 71 received functional and calibration testing within four years, 83 within five years, 111 within six years, 124 within seven years, 129 within eight years, and all 130 within ten years. As a result, 64% of Independence’s 161 protective relays had testing records demonstrating that they were tested within five years, and 81.4% within six years. According to the NERC Protection System Maintenance - A Technical Reference dated September 13, 2007 (Technical Reference), the maximum allowable interval for unmonitored protective relays (Independence’s protective relays were all unmonitored electromechanical or solid state relays) is five years. Furthermore, version 2 of PRC-005 provides a table of maximum maintenance intervals, and the maximum interval provided for unmonitored protective relays is six years. Additionally, all of Independence’s associated communications systems were remotely monitored. Upon failure, an alarm would have been sent to a control center and would have received immediate attention. Although no testing records were provided for the communications systems, Independence periodically performs coordinated communications tests with neighboring utilities. Such tests involve one utility sending a signal from their substation, and the utility on the other end confirming receipt of the signal and then reciprocating. Although, no records were provided to verify annual battery testing, Independence, as part of routine substation inspections, performs informal visual inspections of the station batteries. Such inspections would have identified mechanical failures of battery racks, leaking or damaged battery cells, corroded battery terminals, etc. Upon observance of such conditions, proper maintenance would be performed to resolve the issue. Lastly, at the time of the violation, Independence had a peak load of 315 MW and owned only three transmission lines at 100 kV or above. These three lines totaled 23 miles, serving a 46-mile looped 69 kV transmission system. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $18,000 (for SPP201000215 and SPP201000216) | Compliance Audit | In accordance with its Mitigation Plan, the following activities will be completed: 1) Test all Protection System devices pursuant to Independence's PRC-005 testing program; 2) Purchase a new testing and tracking software system; and 3) Form internal compliance committees and implement the tracking software system. To prevent or minimize the probability of incurring further violations of the same or similar standards requirements, a System Protection Engineer position was created and filled to ensure continuation of proper testing. | 3/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | SPP RE observed that Independence did not have a documented internal compliance program (ICP) at the time of the violation, however, it was established in writing on August 17, 2011. SPP RE considered Independence's ICP as a neutral factor in the penalty determination. Independence created the position of NERC Compliance Officer in 2009 to handle compliance duties. Before that time, NERC compliance had been assigned to a task force of managers and supervisors, with many duties assigned to the System Operations Supervisor. A second supervisory control and data acquisition/energy management system technician was added to System Operations. This person has been charged with CIP compliance. SPP RE observed that the NERC Compliance Officer reports to the Power Engineering Manager/Chief Security Officer who reports jointly to the Power & Light Director and Deputy Director. The NERC Compliance Officer oversees compliance efforts which include the development, implementation and management of a program of action designed to effectively collect, review and store documentation of all compliance measures being implemented by Independence. Managers are kept informed of NERC requirements on a regular basis through monthly Security Work Group meetings and by forwarding emails regarding NERC activities. Program requirements are presently disseminated directly to all senior management, managers, supervisors, and System Operations personnel through presentations, training, and informational emails.