## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC201100419 | Settlement Agreement | PEF, as a Generator Owner, self-certified on February 8, 2011 that it failed to maintain its batteries as required by its Protection System maintenance and testing program (Program) at seven of 16 generating sites (totaling 28 lead acid battery banks). The 28 battery banks represented 16.75% of PEF's 167 total system devices. Specifically, PEF failed to test 100% of battery cell voltages during quarterly maintenance and testing from June 30, 2009 to December 6, 2011. In addition, another generating site did not have complete annual maintenance and testing as required by PEF's Program by failing to test negative post terminal temperatures in 2008, 2009, and 2010. | PRC-005-1 | R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because the violation period was for up to three years and because eight generating sites connected to the BPS were involved. Also, PEF was performing all other tests required but had voltage readings for only 10% instead of 100% of the batteries cells. However, PEF's generator operators inspected the batteries on a daily or weekly basis on rounds and would have alerted the control room of battery voltage or chargers issues. In addition, some sites had fail alarm, charger fail alarm, and DC battery voltage analog reading technology installed that was displayed at the operator's display console in the control room. Testing of 10% of the cell voltages and overall bank voltage was recorded even though PEF did not record 100% of the battery cell voltages. Other testing that was required by PEF's Program was performed within interval and per procedure. For the annual maintenance and testing required, battery string testing was performed to read temperature, although the temperature readings were not performed per procedure. | 12/9/2008 (the date of the 2008 test which did not follow PEF procedure) | 12/6/2011 (the date all quarterly tests were performed per PEF procedure) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Certification | In accordance with its Mitigation Plan, PEF: 1) Determined the number of battery inspections that were out of compliance by performing an internal audit; 2) Reviewed and revised its quarterly and annual maintenance procedures MNT-POGX-00001, MNT-POGX-00002, and field data collection forms FRM-POGX-00722, FRM-POGX-00723, FRM-POGX-00736, and FRM-POGX-00737; 3) Developed a passport battery completion checklist to be completed prior to the approval of the work order completion; 4) Communicated and trained facility personnel on the requirements of the quarterly and annual forms; and 5) Performed an annual and quarterly test using the revised forms. | 2011-12-06 | 2012-06-01 | Neither Admits nor Denies | This violation was determined to be a repeat violation of PRC-005-1 R2 and was considered to be an aggravating factor in the penalty determination. PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 (FRCC201100431) for PEF was filed with FERC under RC12-6-000 on December 30, 2011. The 60-day review period has passed. A Settlement Agreement covering two violations of PRC-005-1 R2.1 (FRCC200900256 and FRCC200900285 ) for PEF was filed with FERC under NP11-256-000 on August 11, 2011. September 9, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. PEF's prior compliance history was considered an aggravating factor in the penalty determination. Also, the instant violation FRCC201100419 was an aggravating factors in the penalty determination of the instant violations FRCC2011007388, FRCC2011007995, and FRCC2012009750 because all of these violations involved a same or similar Reliability Standard, and because FRCC201100419 was discovered and self-reported prior to the remaining three violations. FRCC considered the violation history of Progress Energy Carolinas, an affiliate of PEF, but only applied an aggravating factor to the penalty based on the prior violations of PEF that occurred within the FRCC region.
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2011007388 | Settlement Agreement | On June 7, 2011, PEF, as a Transmission Owner, self-reported a violation of PRC-005-1 R2.1. PEF allowed the maintenance and testing intervals required by its Protection System maintenance and testing program on six capacitive coupled voltage transformers (CCVTs) to lapse at two locations (three at Ross Prairie and three at Brooksville West). The CCVTs were incorrectly labeled in the field and in PEF's database as potential transformers (PTs), which had a different interval for testing and maintenance. The CCVTs had a 12-month interval and the PTs had a 72-month interval. The violation involved 6 CCVTs out of a total of 961 devices (0.62%). | PRC-005-1 | R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PEF had electronic monitoring of the substation components designed to alert the operators to any malfunction of the CCVTs (loss of potential settings on the relays would have alerted the electric system operators (ESOs)). In addition, only six CCVTs out of a total of 961 (0.62%) were affected, and when tested, the CCVTs passed testing. | 11/11/2009 (the date the first CCVTs testing was missed) | 12/17/2011 (the date all testing was completed) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Report | In accordance with its Mitigation Plan, PEF: 1) Performed CCVT in-service testing; 2) Performed an incident investigation; 3) Took disciplinary action on three individuals that were found responsible for the incident; 4) Provided awareness training on the importance of compliance and field equipment validation; 5) Developed inspection templates; and 6) Completed 100% of the inventory verification. | 2012-01-31 | 2012-04-10 | Neither Admits nor Denies | This violation was determined to be a repeat violation of PRC-005-1 R2 and was considered to be an aggravating factor in the penalty determination. PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 (FRCC201100431) for PEF was filed with FERC under RC12-6-000 on December 30, 2011. The 60-day review period has passed. A Settlement Agreement covering two violations of PRC-005-1 R2.1 (FRCC200900256 and FRCC200900285 ) for PEF was filed with FERC under NP11-256-000 on August 11, 2011. September 9, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. PEF's prior compliance history was considered an aggravating factor in the penalty determination. Also, the instant violation FRCC201100419 was an aggravating factors in the penalty determination of the instant violations FRCC2011007388, FRCC2011007995, and FRCC2012009750 because all of these violations involved a same or similar Reliability Standard, and because FRCC201100419 was discovered and self-reported prior to the remaining three violations. FRCC considered the violation history of Progress Energy Carolinas, an affiliate of PEF, but only applied an aggravating factor to the penalty based on the prior violations of PEF that occurred within the FRCC region.
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2011007995 | Settlement Agreement | On September 14, 2011, PEF, as a Transmission Owner (TO), self-reported a violation of PRC-005-1 R2.1. PEF reported that it had missed performing a six-month inspection on batteries at its Dallas Substation in 2008 and was 116 days late performing an annual battery test in 2011. In addition, PEF completed a 100% inventory of PEF battery banks on April 13, 2012 and did not find any additional batteries that required testing. However, PEF did find that as a Generator Owner (GO), it was noncompliant because its Bartow Plant #1 was missing battery installation testing records (installed 2008) and 2008 and 2009 six-month inspection records. Bartow Plant #2 was missing 2008 and 2009 six-month inspection records, and Northeast #2 was missing installation testing records (installed 2008) and six-month inspection records for 2008 and 2009. PEF does not have records detailing testing results, but dates of testing entries for the three sites are present in PEF's maintenance and testing database. Evidence that Protection System devices were maintained and tested within the defined intervals was missing for 1 out of 167 (0.60%) total devices are the Dallas Substation and 6 out of 167 (3.59%) devices at the Bartow Plant. FRCC determined that PEF, as a TO and GO, was in violation of PRC-005-1 R2.1. | PRC-005-1 | R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The TO batteries were maintained on an annual basis, though not on the six-month interval as defined in PEF's transmission Protection System maintenance and testing program effective until October 1, 2009. At that time, the battery maintenance program was changed to require both inspection and maintenance on an annual basis. In addition, the battery bank at the Dallas substation supplies three direct current (DC) distribution panels. All protection and non-protection elements are connected to these panels, which are continuously monitored. If a DC failure is detected in any circuit or in the main feeder, an alarm is automatically initiated to the Energy Control Center for immediate corrective action. In addition, the alternating current (AC) supply used by the battery charger is continuously monitored. Also, although PEF could not show records with testing results for the three sites, it does have dates in its database of testing during the violation period. | 7/28/2008 (the date PEF first missed testing at its Dallas site) | 8/22/2011 (the date PEF completed battery testing) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Report | In accordance with its Mitigation Plan, PEF: 1) Performed maintenance on batteries; 2) Developed and implemented a process to initiate a review for batteries during the engineering phase for projects that transition substations to a PRC-005 Standard requirement; 3) Reviewed 30% of the data in Cascade database to determine other instances where the NERC testing flag is incorrectly set for batteries; 4) Communicated and trained the staff on the new process to review batteries during the engineering phase for projects that transition substations to a PRC-005 Standard requirement; 5) Reviewed 70% of the data in Cascade database to determine other instances where the NERC testing flag is incorrectly set for batteries; and 6) Performed inspection and maintenance on all batteries found to be out of interval. | 2012-04-13 | 2012-05-24 | Neither Admits nor Denies | This violation was determined to be a repeat violation of PRC-005-1 R2 and was considered to be an aggravating factor in the penalty determination. PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 (FRCC201100431) for PEF was filed with FERC under RC12-6-000 on December 30, 2011. The 60-day review period has passed. A Settlement Agreement covering two violations of PRC-005-1 R2.1 (FRCC200900256 and FRCC200900285 ) for PEF was filed with FERC under NP11-256-000 on August 11, 2011. September 9, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. PEF's prior compliance history was considered an aggravating factor in the penalty determination. Also, the instant violation FRCC201100419 was an aggravating factors in the penalty determination of the instant violations FRCC2011007388, FRCC2011007995, and FRCC2012009750 because all of these violations involved a same or similar Reliability Standard, and because FRCC201100419 was discovered and self-reported prior to the remaining three violations. FRCC considered the violation history of Progress Energy Carolinas, an affiliate of PEF, but only applied an aggravating factor to the penalty based on the prior violations of PEF that occurred within the FRCC region.
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2011008525 | Settlement Agreement | On November 10, 2011, PEF, as a Transmission Owner (TO), self-reported a violation of PRC-023-1 R1. During a review of applicable transformer load responsive relays, it was determined that five overcurrent relays on five 500 kV/230 kV transformers were not set to operate above 150% of maximum transformer nameplate rating, as required by the Standard. The violation involves the following transformers: Lake Tarpon #1, Lake Tarpon #2, Brookridge, Central Florida #4, and Kathleen. Relay settings were calculated between 1992 and 2002, and at that time, settings were chosen based on taps available in the installed electromechanical relays which provided coverage closest to 150% of maximum transformer nameplate rating. In addition, during the completion of its Mitigation Plan for this violation, PEF found that settings were incorrect for 30 other relays including: 11 out-of-step (OOS) relays, Zone 3 reach on 11 relays, load encroachment on 4 relays, relay angle error on 1 relay, and overcurrent backup on 3 relays. FRCC determined that PEF had a total of 644 230 kV relays, and a total of 959 500 kV and 115 kV relays. | PRC-023-1 | R1; R1.1; R1.10 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was moderate because the following line relays had settings that deviated noticeably from the required rating: 19 (out of approximately 959 line protection relays, or 1.98%) and 11 load response distance elements (Zone 3/4) were between 115.3% and 148.8% of line rating; 4 relays with load encroachment settings were set between 99.8% and 129.6% of line rating; 1 relay set at an erroneous angle of 64 degrees with load response distance element was set at 115.5%; and 3 overcurrent functions were set between 106.7% and 121.95% of line rating. No misoperations were experienced due to these relays being set under 150% of the maximum transformer nameplate rating. The relay settings that were incorrectly set for the five overcurrent relays (out of approximately a total of 96 transformer relays, or 5.21%) are between 147.2% and 148.7% of maximum transformer nameplate rating. The settings are under the requirement by a minimal margin (all less than 3%) based on available taps in electromechanical relays that provided coverage closest to 150% of maximum transformer nameplate rating. This results in limiting the loadability of the transformers by either 59A (for 147.2%) or 24A (for 148.7%) respectively. No misoperations were experienced due to these relays being set under 150% of the maximum transformer nameplate rating. In addition, initial review with respect to compliance with PRC-023-2 R2 (out of step blocking) found eleven (11) relays in violation. A more detailed analysis, finalized on 8/31/2012, concluded that all the aforementioned 11 locations are in compliance. Only 19 out of the total 644 230 kV (2.95%) relays were affected, and of those, PEF studies showed that the original relay settings would not have been exceeded under N-0, N-1 and N-2 contingencies, therefore reducing the risk to the BPS. | 7/1/2010 (the date the Standard became mandatory and enforceable) | 8/31/2012 (Mitigation Plan completion) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Report | In accordance with its Mitigation Plan, PEF: 1) Issued and installed revised relay settings for all applicable transformer overcurrent relays; 2) Reviewed relay settings for all applicable line relays; 3) Issued, installed and coordinated any necessary setting revisions for identified line relays; 4) Reviewed relay settings for all applicable 500 kV OOS blocking relays; 5) Issued, installed and coordinated any necessary setting revisions for identified 500 kV OOS blocking relays; 6) Reviewed relay settings for all applicable 230 kV OOS blocking relays; and 7) Issued, installed and coordinated any necessary setting revisions for identified 230 kV OOS blocking relays. | 2012-08-31 | 2012-11-19 | Neither Admits nor Denies | PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2012009643 | Settlement Agreement | On January 24, 2012, PEF, as a Transmission Operator, self-reported a violation of MOD-028-1 R4.1. PEF had specified in its Available Transfer Capability Implementation Document (ATCID) that transformers with a primary voltage of 230 kV or above (excluding generator step-up transformers) are determined to be appropriate contingencies to be used in the Total Transfer Capabilities (TTCs) calculations. These 100 transformer contingencies were unintentionally omitted by PEF's calculation of TTCs for Available Transfer Capabilities (ATC) Paths, as required by R4.1. | MOD-028-1 | R4.1 | Lower | Pending | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation may have raised ATC and transactions may have been approved which could have caused overloads, but all the transformers that were excluded from the TTC calculation were modeled in the AREVA energy management system (EMS). The weekly, daily and real-time contingency analysis all used the AREVA EMS model, and the subject transformer contingencies were accurately and completely modeled in the EMS. The real-time contingency analysis program would have detected any risk to the Bulk Electric System and alerted system operators of this possible risk in advance. This would have allowed the system operators to prepare an effective operational mitigation plan in the event the contingency occurred. Further, FRCC determined that PEF's AREVA EMS and the FRCC ATC engine calculations are separate and are not dependent on each other. In real-time, the banks have always been included in the EMS for the operators to respond to. The transformer banks have been modeled in the AREVA EMS since it was placed in service in 2006 or when the banks were placed in service. In addition, a sample ATC calculation analysis was reviewed and transformers were not evidenced to be limiting elements. The omission of the transformers from the contingency list did not result in transactions being incorrectly approved, and as a result, overloading of the grid did not occur. | 4/1/2011 (the date the Standard became mandatory and enforceable) | 4/24/2012 (Mitigation Plan completion) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Report | According to its Mitigation Plan, PEF: 1) Corrected its contingency file and tested these changes in the ATC engine development system; 2) Corrected its contingency file to include the specified transformer contingencies during the next scheduled ATC engine bulk file upload to the ATC engine production system; 3) Developed a procedure for maintaining the ATC engine input files consistent with the ATCID document and Standard MOD-028; and 4) Completed training on the ATC maintenance procedure for the two employees responsible for maintaining PEF’s ATC engine input files. | 2012-04-24 | 2012-06-18 | Neither Admits nor Denies | PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2012009750 | Settlement Agreement | On February 23, 2012, PEF, as a Transmission Operator, self-reported a violation of PRC-005-1a R2.1. PEF failed to test two transmission system components (Wilcox and Newberry carrier units) within the defined intervals in its Protection System maintenance and testing program. The two units at issue represent less than 1% of PEF's 3,386 transmission system components. PEF was six days late in testing the transmission system components at issue. | PRC-005-1a | R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The carrier scheme used in the Wilcox to Newberry 230 kV line is a frequency shift keying (FSK) scheme which provides a continuous guard signal to monitor the communication path between the line terminals. A loss of this guard signal or the loss of the communication path initiates an energy control center (ECC) alarm. The numerical protective relay associated with this pilot relaying scheme also provides step distance protection regardless of the status and/or condition of the carrier unit. Additionally, this line is equipped with a second protective (step distance) relay and breaker failure relays associated with each breaker of this transmission line. A failure of this carrier would have been immediately captured by the ECC operators, and the backup relays would have provided the necessary protection for this line. In addition, the violation was for six days, thereby further reducing the risk to the BPS. | 2/4/2012 (the date the carrier units were due for testing) | 2/10/2012 (the date testing of the carrier units was complete) | $30,000 (for FRCC201100419, FRCC2011007388, FRCC2011007995, FRCC2011008525, FRCC2012009643, and FRCC2012009750) | Self-Report | In accordance with its Mitigation Plan, PEF: 1) Performed required maintenance on the carrier on the Wilcox to Newberry 230 kV line; 2) Reviewed its carrier database to identify any other carriers with incorrect maintenance intervals; 3) Developed and implemented a process for validating preventive maintenance frequencies applied to all equipment records flagged as PRC-005, PRC-008, PRC-0011, PRC-017 and PRC-018 in the Cascade equipment database; 4) Trained data management personnel responsible for applying maintenance frequencies on new verification process referenced in PEF's procedure ADM-TRMX-00045; and 5) Completed validation of preventive maintenance frequencies applied to all equipment records flagged as PRC-005, PRC-008, PRC-0011, PRC-017 and PRC-018 in the Cascade equipment database. | 2012-06-28 | 2012-08-22 | Neither Admits nor Denies | PEF has implemented an internal compliance program (ICP) that was reviewed but considered to be a neutral factor because FRCC determined that the documented ICP needed improvements. FRCC gave credit for PEF's self-assessment and self-reporting elements of the ICP program. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 (FRCC201100431) for PEF was filed with FERC under RC12-6-000 on December 30, 2011. The 60-day review period has passed. A Settlement Agreement covering two violations of PRC-005-1 R2.1 (FRCC200900256 and FRCC200900285 ) for PEF was filed with FERC under NP11-256-000 on August 11, 2011. September 9, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. PEF's prior compliance history was considered an aggravating factor in the penalty determination. Also, the instant violation FRCC201100419 was an aggravating factor in the penalty determination of the instant violations FRCC2011007388, FRCC2011007995, and FRCC2012009750 because all of these violations involved a same or similar Reliability Standard, and because FRCC201100419 was discovered and self-reported prior to the remaining three violations. FRCC considered the violation history of Progress Energy Carolinas, an affiliate of PEF, but only applied an aggravating factor to the penalty based on the prior violations of PEF that occurred within the FRCC region.
ReliabilityFirst Corporation (ReliabilityFirst) | Buckeye Power, Inc. (Buckeye Power) | NCR00700 | RFC2012011211 | Settlement Agreement | On September 28, 2012, Buckeye Power, as a Generator Owner, self-reported a violation of PRC-005-1a R2 to ReliabilityFirst for failing to implement its Protection System maintenance and testing program (Program). Specifically, during the fall of 2011, Buckeye Power conducted three installation projects on a generator that impacted its protective relays and control circuits. When these installation projects were initiated, Revision F of Buckeye Power’s Program was in effect. Revision F of the Program only required Buckeye Power to test the relays that were changed or installed and their associated control circuitry paths, and to verify that the output contacts of the new or replaced relays energize their associated lockout relays. During the course of completing these installation projects, Buckeye Power implemented Revision G of the Program. Revision G required Buckeye Power to test the relays that it changed, their associated control circuitry paths, and all other input paths of the associated lockout relays. However, Buckeye Power did not apply Revision G of its Program during these installation projects, and therefore returned the generator into service without testing certain parallel input paths to the associated lockout relay. Buckeye Power’s violation applies to less than 5% of the total Protection System devices at the Cardinal Plant facility. | PRC-005-1a | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the course of completing the installation projects, Buckeye Power testing Protection System devices were tested under Revision F of the Program, which included all new relays and associated control circuits that may have been affected by the installation project. No generating unit outage or equipment failure occurred during the time period of the alleged violation. Also, no known deviations from device manufacturer recommendations were made during the pendency of this violation. Testing according to Revision G was completed during the generator unit's next outage that began on February 7, 2012. As of March 21, 2012, all maintenance and testing work of circuitry paths was completed and documented according to the revised program requirements. | 1/21/2012 (when Buckeye Power returned a relay to service without conducting the required testing) | 5/31/2013 (Mitigation Plan completion) | 0 | Self-Report | To mitigate this violation, Buckeye Power: 1) Completed testing of the missed parallel input paths; 2) Implemented a process to review and track approved procedures; 3) Developed a procedure for maintaining and tracking evidence related to PRC-005 compliance; 4) Performed a follow-up comprehensive review of the PRC-005 elements to ensure that fleetwide, it has not omitted any other elements or paths according to Revision G of its Protection System maintenance and testing program; and 5) Completed additional testing, in the event any elements or paths have been omitted and not tested according to Revision G. | 2013-05-31 | TBD | Agrees/Stipulates | ReliabilityFirst reviewed Buckeye Power’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The program is documented and widely disseminated within Buckeye Power through distribution to all employees who work with NERC Compliance related activities. Buckeye Power annually reviews the program. The program is supervised by the vice president of engineering and power supply and chief operating officer, who reports to the chief executive officer and president and has independent access to the Board of Directors. Compliance is fully supported by senior management personnel, who are actively involved in compliance efforts. Furthermore, Buckeye Power’s program includes compliance adherence training for all relevant staff, which is provided through monthly meetings, annual workshops hosted by a consulting firm, quarterly webinars hosted by a consulting firm, attendance at ReliabilityFirst Workshops, and attendance at NERC Workshops. Finally, Buckeye Power has incorporated compliance related activities into new employee position descriptions, as well as existing employee position descriptions to ensure its commitment to the compliance program. A Settlement Agreement covering a violation of PRC-005-1 R1 for Buckeye Power was filed with FERC under NP11-270-000 on September 30, 2011. On October 28, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst did not consider the instant violation a repeat violation, as the previous and current violations involve different facts and circumstances. Specifically, the previous violation concerned Buckeye Power’s failure to include intervals, their basis, and a summary of procedures for current and sensing devices within its Program. The current violation concerns Buckeye Power’s failure to implement a new version of the Program when this Program changed in the middle of Buckeye Power’s performance of maintenance and testing of relays in accordance with the requirements of the previous program. ReliabilityFirst also considered the fact that Buckeye Power self-reported the violation of PRC-005-1a R2 to ReliabilityFirst. Therefore, ReliabilityFirst considered this Self-Report as warranting mitigating credit to the associated violation. ReliabilityFirst considered Buckeye Power’s identification of the self-reported violation to be the result of a healthy and robust compliance culture, which evidenced Buckeye Power’s strong controls and depth of understanding of activities at Buckeye Power. Buckeye promptly identified and reported the violation at issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst imposed no monetary penalty due to the self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Northeast Management Company (GenOn Northeast) | NCR11137 | RFC2011001134 | Settlement Agreement | From September 12, 2011, through September 30, 2011, ReliabilityFirst conducted a Compliance Audit of GenOn Northeast, during which ReliabilityFirst discovered that GenOn Northeast, as a Generator Owner, had a violation of PRC-005-1 R1. GenOn Northeast and GenOn Power Midwest (collectively, the GenOn Entities) have identical Protection System maintenance and testing programs. In the programs, GenOn Northeast included a variable maintenance and testing interval for voltage and current sensing devices until the first maintenance and testing was performed after June 18, 2007. Thereafter, GenOn Northeast defined a 12-year maintenance and testing interval for voltage and current sensing devices. For most of its voltage and current sensing devices, maintenance and testing did not occur after June 18, 2007. As a result of the variable interval, GenOn Northeast failed to define a maintenance and testing interval, as required by PRC-005-1 R1.1. In addition, GenOn Northeast failed to include a basis for the interval for voltage and current sensing devices in its program, as required by PRC-005-1 R1.2. GenOn Northeast included a narrative description concerning characteristics of voltage and current sensing devices that did not constitute a basis for a maintenance and testing interval. | PRC-005-1 | R1 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of PRC-005-1 R1 has the potential to affect the reliable operation of the BPS by allowing important Protection System devices to remain unmaintained and untested. The risk was mitigated because there was redundant and backup protection in place at the generating stations. Also, the current sensing devices connected to differential relays had alarms that enabled GenOn Northeast to monitor their performance. Operating personnel were able to detect issues with voltage sensing devices through routine voltage checks or through voltage unbalance detection relays and alarms. In addition, failure of major pieces of equipment would initiate an alarm in the control room. The major elements of generator Protection Systems were protected by differential relays that inherently self-check operation of the current transformers. | 10/4/2007 (when the Standard became mandatory and enforceable) | 2/29/2012 (Mitigation Plan completion) | $0 (for RFC2011001134, RFC2011001136, RFC2011001135, and RFC2011001137) | Compliance Audit | To mitigate this violation, GenOn Northeast: 1) revised its internal process procedures to incorporate the elements necessary for the transition from a condition-based system program to time-based intervals; 2) obtained the necessary internal approvals from upper management of the revised company documents; 3) introduced the process procedures to the stations including any necessary explanations regarding their implementation; and 4) coordinated the schedule for upcoming required testing based upon future outage schedules and funding with each station. | 2012-02-29 | 2013-02-11 | Admits | ReliabilityFirst considered as a mitigating factor the positive degree and quality of the GenOn Entities’ cooperation and remedial action during the enforcement process. ReliabilityFirst seeks to encourage the type of remedial action the GenOn Entities are undertaking, characterized by comprehensive short-term risk mitigation and long-term prevention of future recurrence, by imposing no monetary penalty for these violations. ReliabilityFirst considered certain aspects of the GenOn Entities’ compliance program as mitigating factors. The GenOn Entities were subject to a corporate-level shared internal compliance program (ICP) administered by RRI Energy, Inc. and are now subject to the GenOn ICP. The GenOn Entities’ ICP is operated and managed independently from those responsible for work execution, and the NERC compliance team has independent access to the CEO through normal communication channels. The NERC compliance team holds monthly NERC compliance education and informational calls with relevant personnel, and provides other periodic presentations with management and staff. The NERC compliance team also monitors the controls associated with each of the Reliability Standards and self-assesses the current state of compliance. In addition, the NERC compliance team has the authority to enforce compliance activities where necessary. As a result, the GenOn Entities have a responsive mitigation process enabling the quick identification and mitigation of any issues. ReliabilityFirst also considered it discovered the violations during the Compliance Audit and did not apply mitigating credit. When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The GenOn Entities and their affiliates have not previously violated PRC-005-1. As a result, ReliabilityFirst did not consider the GenOn Entities’ violation history in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Power Midwest (GenOn Midwest) | NCR11136 | RFC2011001136 | Settlement Agreement | From September 12, 2011, through September 30, 2011, ReliabilityFirst conducted a Compliance Audit of GenOn Midwest, during which ReliabilityFirst discovered that GenOn Midwest, as a Generator Owner, had a violation of PRC-005-1 R1. GenOn Midwest and GenOn Northeast Management Company (collectively, the GenOn Entities) have identical Protection System maintenance and testing programs. In the programs, GenOn Midwest included a variable maintenance and testing interval for voltage and current sensing devices until the first maintenance and testing after June 18, 2007. Thereafter, GenOn Midwest defined a 12-year maintenance and testing interval for voltage and current sensing devices. For most of its voltage and current sensing devices, maintenance and testing did not occur after June 18, 2007. As a result of the variable interval, GenOn Midwest failed to define a maintenance and testing interval, as required by PRC-005-1 R1.1. In addition, GenOn Midwest failed to include a basis for the interval for voltage and current sensing devices in its program, as required by PRC-005-1 R1.2. GenOn Midwest included a narrative description concerning characteristics of voltage and current sensing devices that did not constitute a basis for a maintenance and testing interval. | PRC-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of PRC-005-1 R1 has the potential to affect the reliable operation of the BPS by allowing important Protection System devices to remain unmaintained and untested. The risk was mitigated because there was redundant and backup protection in place at the generating stations. Also, the current sensing devices connected to differential relays had alarms that enabled GenOn Midwest to monitor their performance. Operating personnel were able to detect issues with voltage sensing devices through routine voltage checks or through voltage unbalance detection relays and alarms. In addition, failure of major pieces of equipment would initiate an alarm in the control room. The major elements of generator Protection Systems were protected by differential relays that inherently self-check operation of the current transformers. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2/22/2012 (Mitigation Plan completion) | $0 (for RFC2011001134, RFC2011001136, RFC2011001135, and RFC2011001137) | Compliance Audit | To mitigate this violation, GenOn Midwest: 1) revised its internal process procedures to incorporate the elements necessary for the transition from a condition-based system program to time-based intervals; 2) obtained the necessary internal approvals from upper management of the revised company documents; 3) introduced the process procedures to the stations including any necessary explanations regarding their implementation; and 4) coordinated the schedule for upcoming required testing based upon future outage schedules and funding with each station. | 2012-02-22 | 2013-02-11 | Admits | ReliabilityFirst considered as a mitigating factor the positive degree and quality of the GenOn Entities’ cooperation and remedial action during the enforcement process. ReliabilityFirst seeks to encourage the type of remedial action the GenOn Entities are undertaking, characterized by comprehensive short-term risk mitigation and long-term prevention of future recurrence, by imposing no monetary penalty for these alleged violations. ReliabilityFirst considered certain aspects of the GenOn Entities’ compliance program as mitigating factors. The GenOn Entities were subject to a corporate-level shared internal compliance program (ICP) administered by RRI Energy, Inc. and are now subject to the GenOn ICP. The GenOn Entities’ ICP is operated and managed independently from those responsible for work execution, and the NERC compliance team has independent access to the CEO through normal communication channels. The NERC compliance team holds monthly NERC compliance education and informational calls with relevant personnel, and provides other periodic presentations with management and staff. The NERC compliance team also monitors the controls associated with each of the Reliability Standards and self-assesses the current state of compliance. In addition, the NERC compliance team has the authority to enforce compliance activities where necessary. As a result, the GenOn Entities have a responsive mitigation process enabling the quick identification and mitigation of any issues. ReliabilityFirst also considered it discovered the violations during the Compliance Audit and did not apply mitigating credit. When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The GenOn Entities and their affiliates have not previously violated PRC-005-1. As a result, ReliabilityFirst did not consider the GenOn Entities’ violation history in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Northeast Management Company (GenOn Northeast) | NCR11137 | RFC2011001135 | Settlement Agreement | From September 12, 2011, through September 30, 2011, ReliabilityFirst conducted a Compliance Audit of GenOn Northeast, during which ReliabilityFirst discovered that GenOn Northeast, as a Generator Owner, had a violation of PRC-005-1 R2. GenOn Northeast and GenOn Power Midwest (collectively, the GenOn Entities) have identical Protection System maintenance and testing programs. GenOn Northeast is transitioning from a condition-based maintenance approach to a time-based maintenance approach for performing maintenance and testing on its voltage and current sensing devices. Condition-based maintenance required GenOn Northeast to perform maintenance and testing when the need arose. GenOn Northeast switched to time-based maintenance on November 9, 2009, and where the need did not arise, GenOn Northeast did not have the date that it last performed maintenance and testing on voltage and current sensing devices. As a result of not performing the maintenance and testing, GenOn Northeast failed to provide the date it last performed maintenance and testing on 172 of its 307 (56.0%) voltage and current sensing devices. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of PRC-005-1 R2 has the potential to affect the reliable operation of the BPS by allowing important Protection System devices to remain unmaintained and untested. The risk posed was mitigated because there was redundant and backup protection in place at the generating stations. Also, the current sensing devices connected to differential relays had alarms that enabled GenOn Northeast to monitor their performance. Operating personnel are able to detect issues quickly with voltage sensing devices through routine voltage checks or through voltage unbalance detection relays and alarms. In addition, failure of major pieces of equipment would initiate an alarm in control room. The major elements of generator Protection Systems were protected by differential relays that inherently self-check operation of the current transformers. | 10/4/2007 (when the Standard became mandatory and enforceable) | 12/17/2012 (Mitigation Plan Completion) | $0 (for RFC2011001134, RFC2011001136, RFC2011001135, and RFC2011001137) | Compliance Audit | To mitigate this violate, GenOn Northeast will: 1) perform visual inspections on all voltage and current sensing device; and, 2) perform maintenance and testing on all voltage and current sensing devices pursuant to their Protection System maintenance and testing program. | 2012-12-17 | 2013-01-24 | Admits | ReliabilityFirst considered as a mitigating factor the positive degree and quality of the GenOn Entities’ cooperation and remedial action during the enforcement process. ReliabilityFirst seeks to encourage the type of remedial action the GenOn Entities are undertaking, characterized by comprehensive short-term risk mitigation and long-term prevention of future recurrence, by imposing no monetary penalty for these alleged violations. ReliabilityFirst considered certain aspects of the GenOn Entities’ compliance program as mitigating factors. The GenOn Entities were subject to a corporate-level shared internal compliance program (ICP) administered by RRI Energy, Inc and are now subject to the GenOn ICP. The GenOn Entities’ ICP is operated and managed independently from those responsible for work execution, and the NERC compliance team has independent access to the CEO through normal communication channels. The NERC compliance team holds monthly NERC compliance education and informational calls with relevant personnel, and provides other periodic presentations with management and staff. The NERC compliance team also monitors the controls associated with each of the Reliability Standards and self-assesses the current state of compliance. In addition, the NERC compliance team has the authority to enforce compliance activities where necessary. As a result, the GenOn Entities have a responsive mitigation process enabling the quick identification and mitigation of any issues. ReliabilityFirst also considered it discovered the violations during the Compliance Audit and did not apply mitigating credit. When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The GenOn Entities and their affiliates have not previously violated PRC-005-1. As a result, ReliabilityFirst did not consider the GenOn Entities’ violation history in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Power Midwest (GenOn Midwest) | NCR11136 | RFC2011001137 | Settlement Agreement | From September 12, 2011 through September 30, 2011, ReliabilityFirst conducted a Compliance Audit of GenOn Northeast, during which ReliabilityFirst discovered that GenOn Northeast, as a Generator Owner, had a violation of PRC-005-1 R2. The GenOn Entities GenOn Northeast and GenOn Power Midwest (collectively, the GenOn Entities) have identical Protection System maintenance and testing programs. GenOn Power Midwest is transitioning from a condition-based maintenance approach to a time-based maintenance approach for performing maintenance and testing on its voltage and current sensing devices. Condition-based maintenance required GenOn Midwest to perform maintenance and testing when the need arose. GenOn Midwest switched to time-based maintenance as of November 9, 2009, and where the need did not arise, GenOn Midwest did not have the date that it last performed maintenance and testing on voltage and current sensing devices. As a result of not performing the maintenance and testing, GenOn Midwest failed to provide the date it last performed maintenance and testing on 853 of its 877 (97.3%) voltage and current sensing devices. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of PRC-005-1 R1 has the potential to affect the reliable operation of the BPS by allowing important Protection System devices to remain unmaintained and untested. The risk posed was mitigated because there was redundant and backup protection in place at the generating stations. Also, the current sensing devices connected to differential relays had alarms that enabled GenOn Northeast to monitor their performance. Operating personnel were able to detect issues quickly with voltage sensing devices through routine voltage checks or through voltage unbalance detection relays and alarms. In addition, failure of major pieces of equipment would initiate an alarm in control room. The major elements of generator Protection Systems were protected by differential relays that inherently self-check operation of the current transformers. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2/28/2013 (Mitigation Plan Completion) | $0 (for RFC2011001134, RFC2011001136, RFC2011001135, and RFC2011001137) | Compliance Audit | To mitigate this violation, GenOn Midwest will: 1) perform visual inspections on all voltage and current sensing devices; and, 2) perform maintenance and testing on all voltage and current sensing devices pursuant to their Protection System maintenance and testing program. | 2013-02-28 | TBD | Admits | ReliabilityFirst considered as a mitigating factor the positive degree and quality of the GenOn Entities’ cooperation and remedial action during the enforcement process. ReliabilityFirst seeks to encourage the type of remedial action the GenOn Entities are undertaking, characterized by comprehensive short-term risk mitigation and long-term prevention of future recurrence, by imposing no monetary penalty for these alleged violations. ReliabilityFirst considered certain aspects of the GenOn Entities’ compliance program as mitigating factors. The GenOn Entities were subject to a corporate-level shared internal compliance program (ICP) administered by RRI Energy, Inc. and are now subject to the GenOn ICP. The GenOn Entities’ ICP is operated and managed independently from those responsible for work execution, and the NERC compliance team has independent access to the CEO through normal communication channels. The NERC compliance team holds monthly NERC compliance education and informational calls with relevant personnel, and provides other periodic presentations with management and staff. The NERC compliance team also monitors the controls associated with each of the Reliability Standards and self-assesses the current state of compliance. In addition, the NERC compliance team has the authority to enforce compliance activities where necessary. As a result, the GenOn Entities have a responsive mitigation process enabling the quick identification and mitigation of any issues. ReliabilityFirst also considered it discovered the violations during the Compliance Audit and did not apply mitigating credit. When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The GenOn Entities and their affiliates have not previously violated PRC-005-1. As a result, ReliabilityFirst did not consider the GenOn Entities’ violation history in the penalty determination.
SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2011006476 | Settlement Agreement | On March 18, 2011, Duke, as a Transmission Owner, self-reported that it discovered protective relay settings that did not meet the requirements of PRC-023-1 R1. According to Duke, as it was preparing data for a May 2011 SERC Compliance Audit, transmission lines were evaluated to ensure that proper evidence existed to demonstrate compliance with PRC-023-1. A discrepancy was noted on a Facility Ratings spreadsheet for a transmission line. It showed that the existing overcurrent relays did not meet the criteria of PRC-023-1 R1. Further investigation revealed issues at similar facilities; therefore, a complete system review was performed. Duke owns and operates 1,015 PRC-023-1 applicable relays. During its evaluation, Duke discovered that 130 of the relays were not properly set to meet the criteria established in PRC-023-1 R1. These relays limited loadability on 65 terminals associated with 45 circuits. SERC requested and reviewed a complete inventory spreadsheet of PRC-023 applicable relays. SERC also requested historical loading data for the circuits impacted identified as not meeting PRC-023 criteria in order to assess the risk to reliability associated with the findings. SERC verified that the following relays did not meet the criteria of PRC-023-1 R1: 1) 101 relays were set based on R1.1 criteria. On average, the relays were set to operate at 124% of the highest seasonal Facility Rating of the circuit. Based on a review of the historical loading for these circuits, on average the setpoints were 317% of the maximum historical load and never less than 157%; 2) 13 relays were set based on R1.6 criteria. On average the relays were set to operate at 178% of the aggregated generation nameplate capability. Based on a review of the historical loading for these circuits, on average the setpoints were 240% of the maximum aggregate generation and never less than 167%; 3) 5 relays were set based on R1.10 criteria. On average these relays were set to operate at 143% of the applicable maximum transformer nameplate rating. Based on a review of the historical loading for these circuits, on average the setpoints were 214% of the maximum historical load and never less than 199%; 4) 9 relays were set based on R1.10 criteria. On average these relays were set to operate at 109% of the highest operator established emergency transformer rating. Based on a review of the historical loading for these circuits, on average the setpoints were 216% of the maximum historical load and never less than 124%; and 5) 2 relays were set based on R1.12 criteria but had the maximum torque angle (MTA) set to 75 degrees rather than to 90 degrees, which resulted in a calculated Facility Rating of 4,632 amps. When the MTA was corrected to 90 degrees, the resulting Facility Rating was 4,557 amps and System Planning was notified. The maximum historical loading for these terminals was 1,428 amps and 1,470 amps; significantly below the revised Facility Rating. SERC determined that Duke was in violation of PRC-023-1 R1 because it failed to set 130 relay set-points in accordance with PRC-023-1 R1 criteria (R1.1 through R1.13), which limited transmission system loadability for 65 terminals associated with 45 circuits. | PRC-023-1 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to provide enough margin between relay setpoints and the associated Facility Rating could result in facilities being automatically removed from service without providing operators enough time to mitigate overload conditions. The risk to the BPS was mitigated by the following factors: 1) For the 106 relays classified as R1.1 or R1.10, which should have been set at the applicable maximum transformer nameplate rating, on average the relay setpoints were 314% of the maximum historical loads and never less than 157%, indicating the unlikeliness the setpoints would have limited loadability; 2) For the nine relays classified as R1.10, which should have been set at or above 115% of the highest operator established emergency transformer rating, on average the relay setpoints were 216% of the maximum historical loads and never less than 124%, indicating the unlikeliness the setpoints would have limited loadability; 3) For the 13 relays classified as R1.6, on average the relay setpoints were 240% of the maximum historical loads and never less than 167%, indicating the unlikeliness the setpoints would have limited loadability; and 4) For the two relays classified as R1.12, the maximum historical loading for these circuits was 1,428 amps and 1,470 amps, significantly below the revised Facility Rating of 4,557 amps. | 7/1/2010 (when the Standard became mandatory and enforceable) | 5/8/2012 (Mitigation Plan completion) | $20,000 | Self-Report | To mitigate this violation, Duke: 1) Implemented solutions for each relay at issue; 2) Formalized the procedure between system planning and system protection to ensure relay settings are in compliance with PRC-023 prior to rating increases being published; 3) Created a new PRC-023 compliance spreadsheet that provides automatic checking of compliance and flagging of potential issues; 4) Developed and implemented a PRC-023 procedure; and 5) Provided training to system protection engineers on the new spreadsheet and the new procedure. | 2012-05-08 | 2012-12-18 | Neither Admits nor Denies | SERC reviewed Duke's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Duke follows Duke Energy Corporation's (Duke Energy) NERC Reliability Standards Compliance Policy, which has been documented since 2008. Details of the ICP are widely disseminated. In addition, Duke Energy issues a quarterly newsletter addressing internal and external Reliability Standards information. The Reliability Standards executive sponsor committee is a senior management team that provides oversight for the ICP. Duke Energy's vice president compliance and service delivery is responsible for, and has independent access to, the CEO and the executive sponsor committee. The ICP is regularly reviewed and is subject to internal audit. Disciplinary action for Reliability Standards issues is consistent with Duke Energy's corporate practice and protocol for any issue requiring discipline of an employee. Since Duke self-reported after it received notice of the Audit, it did not receive self-reporting credit.