## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
Midwest Reliability Organization (MRO) | Midwest Independent Transmission System Operator, Inc. (MISO) | NCR00826 | MRO201100434 | Settlement Agreement | On October 11, 2011, MISO submitted a Self-Report to MRO stating that, as a Balancing Authority (BA), it was in violation of BAL-005-0.1b R12 because it included retired Tie Line flows with Adjacent BA Areas in the Area Control Error (ACE) calculation. In June 2010, a member entity submitted a substation reconfiguration project to MISO which included changes to two Tie Line flows with the Adjacent BA. The reconfiguration resulted in retiring two Tie Line flows and the addition of two new Tie Line flows with the Adjacent BA. MISO was receiving values from the data point associated with the two new lines with the Adjacent BA and the value from the retired Tie Line flows from March 21, 2011 through March 28, 2011. MISO’s supervisory control and data acquisition (SCADA) - state estimator (SE) tool showed a maximum difference of 83 MW, and an average MW difference of 43 MW. MISO discovered the difference on March 28, 2011. The MISO hourly check-out process failed to identify the issue because its process did not include the comparison of the hourly integrated MW Tie Line values against the Tie Line MW hour metered values. | BAL-005-0.1b | R12 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MISO's SCADA - SE comparison indicated an average MW difference of 43 MW, and the duration was seven days. Additionally, MISO did not identify any other issues upon completing a comprehensive review that ensured all Tie Line MW metering was properly telemetered in the MISO footprint. | 3/21/2011 (when MISO began including retired Tie Line flows with Adjacent BA Areas in the ACE calculation) | 3/28/2011 (when MISO removed the retired Tie Line flows from the ACE calculation) | 0 | Self-Report | To mitigate this violation, MISO: 1) performed a comprehensive review of Tie Line flow inputs into the MISO ACE calculation, and developed an external training session focused on MISO's current process for Inter-Control Center Communications Protocol object identifier mapping; 2) re-configured the SCADA comparison tool to enhance the alarming capabilities; 3) modified the Daily Reliability Coordination Report to enhance visibility of any updated in-service dates for Tie Lines for real-time operations personnel; 4) modified shift turnover processes to include a requirement that operators specifically review the Daily Reliability Coordination Report for any status changes to the Tie Line listing at the beginning of each shift turnover; 5) developed and completed training of operations personnel regarding the requirements of BAL-005-0.lb R12 and the tool and process enhancements implemented to ensure compliance; 6) augmented its real-time displays to add a comparison report that will provide additional quality assurance checks of data sources; and 7) modified its facilities commissioning process to ensure that topology modifications are accurately captured in the outage database, and better coordinated between operations personnel and modeling personnel. | 2012-08-20 | 2012-08-22 | Admits | MRO reviewed MISO's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. MRO considered the following mitigating factors when determining the penalty amount: 1) MISO will enhance its Tie Line error display to include a column displaying the last three hours of any delta, so that an operator can more easily reconcile instances in which there is a delay or overstatement in the MW hour value received from the local BA. Additionally, MISO will also incorporate a checkbox function that a MISO operator must acknowledge whenever: (1) a delta greater than 20 MW in the current hour is calculated and displayed; and (2) whenever any missed or double counted local BA MW hour values are calculated and displayed. These enhancements will cost approximately $5,280 to implement and will be complete by May 1, 2013. 2) MISO will also develop a new display specific to transmission system facilities being brought into service that impact the MISO footprint. The display will also have a checkbox function that will require the MISO Operators to acknowledge that: (1) they are aware that the new or revised tie line is in service, and (2) they have verified the tie line flow magnitude and direction. The display will cost approximately $10,560 and will be complete by May 1, 2013. A Settlement Agreement covering two violations of BAL-005-0.1b R9 for MISO was filed with FERC under NP12-10-000 on December 30, 2011. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. MRO determined that these prior violations should not serve as a basis for aggravating the penalty because they did not involve same or similar conduct to the instant case.
Midwest Reliability Organization (MRO) | Omaha Public Power District (OPPD) | NCR00860 | MRO201000171 | Notice of Confirmed Violation | On March 16, 2010, OPPD submitted a Self-Report to MRO stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2 because it failed to provide evidence that Protection System devices were maintained and tested within the defined intervals and it failed to provide the date each Protection System device was last tested and maintained. OPPD discovered noncompliance while preparing for a Compliance Audit scheduled for April 2010. OPPD performed a comprehensive review of its Protection System maintenance and testing device records. Upon completing the review, OPPD reported that it has 1,722 Protection System relays, 1,722 DC control circuits, 161 associated communication system devices, 2,521 voltage and current sensing devices, and 101 station batteries subject to PRC-005-1 R2. Of those devices, OPPD failed to provide evidence that it maintained and tested the following devices: 49 Protection System relays, 137 DC control circuits, and 101 station batteries, or approximately 4% of its Protection System devices. More specifically, of the 49 Protection System relays identified, 39 relays are associated with 161 kV transmission circuits and nine are associated with 345 kV transmission circuits. For two of the relays, OPPD failed to provide the date that the device was last tested. Thirty-seven of the 39 relays on 161 kV circuits missed their four year interval by 128 days. Eight of the nine protective relays associated with the 345 kV transmission circuits were maintained and tested by December 2007, and missed the scheduled maintenance and testing interval by one month. OPPD also failed to provide evidence of the maintenance interval for its DC control circuitry. Panel lights were included in OPPD's monthly routine substation inspections and OPPD did not identify any issues with its DC control circuitry during those inspections. OPPD also failed to provide specific gravity maintenance and testing records for 101 station batteries. However, OPPD performed cell voltage tests on a semi-annual basis, and internal cell, connection resistance, and impedance tests on an annual basis. Additionally, OPPD continuously monitored the battery bank voltage on its supervisory control and data acquisition (SCADA) system. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although OPPD failed to provide evidence of Protection System maintenance and testing within defined intervals for 37 relays associated with 161 kV, the manufacturer's recommended maintenance and testing interval is six years for unmonitored protective relays. Therefore, the relays were maintained and tested within manufacturer's recommended intervals. Also, eight of the nine protective relays associated with the 345 kV transmission circuits were maintained and tested by December 2007, and missed the scheduled maintenance and testing interval by one month. Additionally, although OPPD failed to provide evidence of the maintenance interval for its DC Control Circuitry, panel lights are included in OPPD's monthly routine substation inspections and OPPD did not identify any issues with its DC control circuitry during those inspections. Furthermore, although OPPD failed to provide specific gravity maintenance and testing records for 101 station batteries, OPPD performed cell voltage tests on an semi-annual basis, and internal cell, connection resistance, and impedance tests on an annual basis. OPPD also continuously monitored the battery bank voltage on its SCADA system. | 6/18/2007 (when the Standard became mandatory and enforceable) | 6/15/2012 (when OPPD completed the maintenance and testing) | $5,000 (MRO201000171 and MRO2012009549) | Self-Report | To mitigate this violation, OPPD: 1) performed additional maintenance and testing of the battery systems; 2) maintained, tested, or replaced all transmission related relays that were identified in the Self-Report; 3) identified all generation battery systems and ensured properly scheduled testing occurred; 4) performed a comprehensive inventory of the Protection System maintenance and testing database; 5) after reviewing the comprehensive inventory, OPPD completed testing for any equipment found outside the defined maintenance and testing intervals; 6) increased the frequency of report reviews for a compliance database; 7) enhanced reports from the compliance database to include forecasting; 8) purchased a Doble three phase test set; and 9) sent an additional employee to a vendor provided training session on the compliance database. | 2012-08-21 | 2012-08-21 | Admits | MRO reviewed OPPD's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. OPPD hired an additional full-time engineer within the substation and system protection department to solely focus on PRC-related maintenance issues. The start date for this position was June 6, 2011. Additionally, OPPD revised its ICP to combine the generation and transmission maintenance functions. MRO considered these factors in its penalty determination.
Midwest Reliability Organization (MRO) | Omaha Public Power District (OPPD) | NCR00860 | MRO2012009549 | Notice of Confirmed Violation | On January 13, 2012, OPPD submitted a Self-Report to MRO stating that, as a Distribution Provider, Generator Owner, and Transmission Owner, it was in violation of PRC-005-1 R2 because it failed to provide evidence Protection System devices were maintained and tested within the defined intervals. While verifying completion of the Mitigation Plan associated with Violation ID MRO201000171, MRO staff identified that OPPD did not complete specific gravity testing for 13 of 101 (13%) generation station batteries. OPPD provided its supporting evidence of completion after the Mitigation Plan proposed completion date of May 31, 2011. While reviewing this supporting evidence, MRO staff identified incomplete specific gravity testing records. Since the Mitigation Plan completion date had passed, OPPD submitted a Self-Report for another PRC-005-1 R2 violation. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although OPPD failed to provide specific gravity maintenance and testing records for 13 station batteries, OPPD had other battery maintenance and testing in place such as periodic inspections, battery connection checks, battery voltage tests, and cell impedance tests. Furthermore, OPPD monitored the generation battery bank voltage continuously. | 6/18/2007 (when the Standard became mandatory and enforceable) | 8/20/2012 (Mitigation Plan completion) | $5,000 (MRO201000171 and MRO2012009549) | Self-Report | To mitigate this violation, OPPD: 1) identified and performed specific gravity testing on all substation battery systems with a due date prior to November 11, 2011 (the date when changes were made to the Protection System Maintenance & Testing Program (PSMP) with regards to the removal of specific gravity testing requirements); 2) revised the PSMP to add internal controls on approval processes for changes to PSMP testing requirements; 3) performed a comprehensive review of testing procedures within the PSMP and generation battery system maintenance procedures to review and validate that all testing and maintenance procedures are executed according to the PSMP and generation battery systems maintenance procedure documents; 4) after completing the comprehensive review of testing procedures, OPPD corrected any discrepancies between the testing procedures and maintenance documents; and 5) completed any missed maintenance and testing. | 2012-08-20 | 2012-08-23 | Admits | MRO reviewed OPPD's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. OPPD revised its ICP to combine the generation and transmission maintenance functions. MRO considered this factor in its penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta York Renewable Energy, LLC. (Covanta York) | NCR10388 | RFC2012010615 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta York, as a Generator Owner (GO), was in violation of FAC-008-1 R1.2 for failing to document the method by which the Facility Ratings are determined. Specifically, Covanta York failed to include the method by which it determined the Ratings for transmission conductors, transformers, relay protection devices, and terminal equipment, in violation of FAC-008-1 R1.2.1. Additionally, Covanta York failed to include the method by which it established Emergency Ratings in the Facility Ratings Methodology, in violation of FAC-008-1 R1.2.2. | FAC-008-1 | R1.2; R1.2.1; R1.2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated because Covanta York's facility is designed so that the generators are the most limiting factors. Following an assessment of all facility-owned equipment, Covanta York confirmed that no other equipment limits this facility from the established generator nameplate ratings. Finally, the revised Facility Ratings Methodology did not result in a de-rating of Covanta York's facility. | 12/28/2011 (when Covanta York registered as a GO) | 12/31/2012 (Mitigation Plan completion) | $0 (for RFC2012010615, RFC2012010616, and RFC2012010617) | Compliance Audit | To mitigate this violation, Covanta York: 1) implemented and communicated a revised Facility Ratings Methodology; and 2) re-assessed its Facility Ratings using the revised Facility Ratings Methodology. | 2012-12-31 | 2013-04-15 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated, within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta York Renewable Energy, LLC. (Covanta York) | NCR10388 | RFC2012010616 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta York, as a Generator Owner (GO) was in violation of FAC-009-1 R1 for failing to establish Facility Ratings consistent with Covanta York’s Facility Rating Methodology. Covanta York established the Facility Ratings for the Facility based on steam flow, but Covanta York did not consider steam flow as one of the elements in its analysis. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated because Covanta York's facility is designed so that the generators are the most limiting factors. Following an assessment of all facility-owned equipment, Covanta York confirmed that no other equipment limits this facility from the established generator nameplate rating. Finally, the revised Facility Ratings methodology did not result in a de-rating of Covanta York's facility. | 12/28/2011 (when Covanta York registered as a GO) | 4/11/2013 (Mitigation Plan completion) | $0 (for RFC2012010615, RFC2012010616, and RFC2012010617) | Compliance Audit | To mitigate this violation, Covanta York: 1) reassessed all of its facility-owned equipment; and 2) implemented a new Facility Ratings Methodology. | 2013-04-11 | 2013-04-15 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated, within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta York Renewable Energy, LLC. (Covanta York) | NCR10388 | RFC2012010617 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta York, as a Generator Owner (GO), was in violation of PRC-005-1a R1. Specifically, ReliabilityFirst determined that Covanta York did not include maintenance and testing intervals and their basis for current and potential sensing devices and DC control circuitry within their Protection System maintenance and testing program. Additionally, Covanta York failed to include a summary of maintenance and testing procedures for current and potential sensing devices and DC control circuitry within their Protection System maintenance and testing programs. Covanta York’s violation affected all of its 53 current and potential sensing devices and 10 DC control circuitry, which constituted 69% of Covanta York’s 91 Protection System devices. | PRC-005-1a | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Covanta York failed to include testing intervals, their basis, and summaries of testing procedures within their maintenance and testing programs, it had tested all affected protective devices during the relay calibration testing cycle of three-years. These tests consisted of inputting current and voltage to each device, ensuring that associated devices, such as current and potential sensing devices and DC control circuitry were maintained in working order. During this functional testing, Covanta York found no evidence of misoperations or faulty conditions. Furthermore, Covanta York's monitoring method provides operators with a real-time alert system, which allows for immediate action in the event that an indication points to a problem with a Protection System. | 12/28/2011 (when Covanta York registered as a GO) | 2/24/2013 (Mitigation Plan completion) | $0 (for RFC2012010615, RFC2012010616, and RFC2012010617) | Compliance Audit | To mitigate this violation, Covanta York: 1) revised its Protection System maintenance and testing program; and 2) implemented the program. | 2013-02-24 | 2013-03-28 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated within each of the Compliance Audit reports that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. A Settlement Agreement covering violation of PRC-005-1 R2 in ReliabilityFirst for Covanta Plymouth was filed with FERC under NP12-27-000 on May 30, 2012. Another Settlement Agreement covering violations of PRC-005-1 R1 and R2.1 in another region for one of the Covanta Entities' affiliate was filed with FERC under NP11-123-000 on February 23, 2011. On June 29, 2012 and March 25, 2011, respectively, FERC issued orders stating it would not engage in further review of these Notices of Penalty. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta Plymouth Renewable Energy, LLC. (Covanta Plymouth) | NCR10389 | RFC2012010618 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta Plymouth, as a Generator Owner (GO), was in violation of FAC-008-1 R1.2 for failing to document the method by which the Facility Rating is determined. Specifically, Covanta Plymouth failed to include the method by which it determined the Ratings of transmission conductors and terminal equipment, in violation of FAC-008-1 R1.2.1. Additionally, Covanta Plymouth failed to include the method by which it had established Emergency Ratings in its Facility Ratings Methodology, in violation of FAC-008-1 R1.2.2. | FAC-008-1 | R1.2; R1.2.1; R1.2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated because Covanta Plymouth's facility is designed so that the generators are the most limiting factors. Following an assessment of all facility-owned equipment, Covanta Plymouth confirmed that no other equipment limits this facility from the established generator nameplate ratings. Finally, the revised Facility Ratings Methodology did not result in a de-rating of Covanta Plymouth's facility. | 10/9/2009 (when Covanta Plymouth registered as a GO) | 12/31/2012 (Mitigation Plan completion) | $0 (for RFC20120618, RFC20120619, RFC20120629, and RFC20120631) | Compliance Audit | To mitigate this violation, Covanta Plymouth: 1) implemented a revised Facility Ratings Methodology; and 2) re-assessed their Facility Ratings using the revised Facility Ratings Methodology. | 2012-12-31 | 2013-03-20 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated, within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta Plymouth Renewable Energy, LLC. (Covanta Plymouth) | NCR10389 | RFC2012010619 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta Plymouth, as a Generator Owner (GO), was in violation of FAC-009-1 R1 for failing to establish Facility Ratings for its relay protective devices and terminal equipment, specifically, two disconnect switches and two breakers, which are identified in Covanta Plymouth’s Facility Rating Methodology. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated because Covanta Plymouth's facility is designed so that the generators are the most limiting factors. Following an assessment of all facility-owned equipment, Covanta Plymouth confirmed that no other equipment limits this facility from the established generator nameplate rating. Finally, the revised Facility Ratings methodology did not result in a de-rating of Covanta Plymouth's facility. | 10/9/2009 (when Covanta Plymouth registered as a GO) | 4/11/2013 (Mitigation Plan completion) | $0 (for RFC20120618, RFC20120619, RFC20120629, and RFC20120631) | Compliance Audit | To mitigate this violation, Covanta Plymouth: 1) reassessed all of their facility-owned equipment; and 2) implemented a new Facility Ratings Methodology. | 2013-04-11 | 2013-04-15 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated, within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta Plymouth Renewable Energy, LLC. (Covanta Plymouth) | NCR10389 | RFC2012010629 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta Plymouth, as a Generator Owner (GO), was in violation of PRC-005-1 R1. Specifically, ReliabilityFirst determined that the Covanta Plymouth did not include maintenance and testing intervals and their basis for current and potential sensing devices and DC control circuitry within their Protection System maintenance and testing program in violation of PRC-005-1 R1.1. Additionally, Covanta Plymouth failed to include a summary of maintenance and testing procedures for current and potential sensing devices and DC control circuitry within their Protection System maintenance and testing programs in violation of PRC-005-1 R1.2. Covanta Plymouth’s violation affected all of its 52 current and potential sensing devices and 5 DC control circuitry, which constituted 48% of Covanta Plymouth’s 118 Protection System devices. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Covanta Plymouth failed to include testing intervals, their basis, and summaries of testing procedures within their maintenance and testing programs, it had functionally tested all implicated protective devices during the relay calibration testing cycle of three-years. These tests consisted of inputting current and voltage to each device, ensuring that associated devices, such as current and potential sensing devices and DC control circuitry were maintained in working order. During this functional testing, Covanta Plymouth found no evidence of misoperations or faulty conditions. Furthermore, Covanta Plymouth's monitoring method provides operators with a real-time alert system, which allows for immediate action in the event that an indication points to a problem with a Protection System. | 10/9/2009 (when Covanta Plymouth registered as a GO) | 2/4/2013 (Mitigation Plan completion) | $0 (for RFC20120618, RFC20120619, RFC20120629, and RFC20120631) | Compliance Audit | To mitigate this violation, Covanta Plymouth: 1) revised its Protection System maintenance and testing methodologies; and 2) implemented the newly revised and approved Protection System maintenance and testing methodologies. | 2013-02-04 | 2013-03-28 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. A Settlement Agreement covering violation of PRC-005-1 R2 in ReliabilityFirst for Covanta Plymouth was filed with FERC under NP12-27-000 on May 30, 2012. Another Settlement Agreement covering violations of PRC-005-1 R1 and R2.1 in another region for one of the Covanta Entities' affiliate was filed with FERC under NP11-123-000 on February 23, 2011. On June 29, 2012 and March 25, 2011, respectively, FERC issued orders stating it would not engage in further review of these Notices of Penalty. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
ReliabilityFirst Corporation (ReliabilityFirst) | Covanta Plymouth Renewable Energy, LLC. (Covanta Plymouth) | NCR10389 | RFC2012010631 | Settlement Agreement | During a Compliance Audit from April 30, 2012 through May 10, 2012, ReliabilityFirst discovered that Covanta Plymouth, as a Generator Owner (GO), was in violation of PRC-005-1 R2. ReliabilityFirst determined that Covanta Plymouth failed to document that all monthly and quarterly battery maintenance and testing was performed in accordance with their defined intervals in violation of PRC-005-1 R2.1. Specifically, the Covanta Maintenance and Testing Methodology lists tasks associated with maintaining all batteries. Among the tasks listed within the Covanta Maintenance and Testing Methodology is the requirement that batteries be tested by sampling the specific gravity for individual cells. This task can be performed on the Vented Lead Acid Batteries, but this task is not possible for sealed batteries. Covanta Plymouth previously did not identify this distinction between battery types and was unable to complete all tasks listed in its Maintenance and Testing Methodology for sealed batteries. This violation affected all of Covanta Plymouth’s 60 batteries, which constituted 51% of Covanta Plymouth’s 118 Protection System devices. | PRC-005-1 | R2; R2.1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Covanta Plymouth failed to complete all tasks listed in its Maintenance and Testing Methodology for sealed batteries, Covanta Plymouth completed all technically feasible tasks during each testing and maintenance interval. | 10/9/2009 (when Covanta Plymouth registered as a GO) | 2/14/2013 (Mitigation Plan completion) | $0 (for RFC20120618, RFC20120619, RFC20120629, and RFC20120631) | Compliance Audit | To mitigate this violation, Covanta Plymouth: 1) revised its PRC-005 procedures to include maintenance and testing tasks based on individual battery types; and 2) implemented the revised Protection System maintenance and testing methodology. | 2013-02-14 | 2013-03-28 | Admits | ReliabilityFirst reviewed Covanta Entities’ (together Covanta York and Covanta Plymouth constitute Covanta Entities) internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The Covanta Entities are subject to a corporate compliance program, which is a widely disseminated program within the Covanta Entities. The ICP is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the ICP is supervised by the senior vice president of domestic operations, who has independent access to all senior management personnel, including the chief executive officer. Employees also have access to senior management personnel for compliance reporting purposes. Furthermore, the Covanta Entities’ manager of NERC compliance provides annual compliance awareness training on all internal compliance initiatives and strategies to employees and conducts annual internal compliance assessments. ReliabilityFirst also considered the Covanta Entities’ cooperation with ReliabilityFirst during the compliance enforcement activities as a mitigating factor during its penalty determination. Specifically, ReliabilityFirst stated within each of the Compliance Audit reports, that the Covanta Entities were very receptive to ReliabilityFirst’s clarifying questions and additional requests for information. Throughout the enforcement process, the Covanta Entities also provided timely and complete information to ReliabilityFirst. A Settlement Agreement covering violation of PRC-005-1 R2 in ReliabilityFirst for Covanta Plymouth was filed with FERC under NP12-27-000 on May 30, 2012. Another Settlement Agreement covering violations of PRC-005-1 R1 and R2.1 in another region for one of the Covanta Entities' affiliate was filed with FERC under NP11-123-000 on February 23, 2011. On June 29, 2012 and March 25, 2011, respectively, FERC issued orders stating it would not engage in further review of these Notices of Penalty. Although ReliabilityFirst considered the Covanta Entities’ compliance history to constitute an aggravating factor, ReliabilityFirst determined that the Covanta Entities’ compliance history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to the Covanta Entities’ compliance history. Therefore, due to the Covanta Entities’ efforts to ensure the reliability of the BPS as demonstrated through their ICP and cooperation with ReliabilityFirst, in addition to the minimal risk posed by each violation, ReliabilityFirst determined that a monetary penalty was not necessary.
SERC Reliability Corporation (SERC) | Alabama Power Company (APC) | NCR01166 | SERC2012010332 | Settlement Agreement | On May 24, 2012, APC submitted a Self-Report to SERC stating that, as a Generator Owner, it was in violation of PRC-005-1 R2 because six battery banks at Plant Farley were not being maintained according to its Plant Farley generation Protection System maintenance and testing program (Plant Farley program), a Plant Farley-specific program that complements APC's generation Protection System maintenance and testing program. In April 2012, APC learned through a review of its procedures that six battery banks at Plant Farley were not maintained according to the Plant Farley program. APC determined that four of the six battery banks, located at the Turbine Building for Farley Units 1 and 2, were not maintained according to the Plant Farley program because the four batteries were not listed in the testing data sheets in the procedure for implementing the Plant Farley program. The remaining two battery banks, located at the Switch House for Farley Units 1 and 2, are included in Plant Farley's NERC generation Protection System maintenance and testing procedures, but maintenance personnel used a different method of verifying battery connection integrity than the method specified in the procedures. The procedure for implementing the Plant Farley program calls for thermal scanning of the battery connections at a frequency of six years. However, APC Plant Farley personnel never implemented thermal scanning as a method of verifying battery connection integrity for any of the six Plant Farley batteries. Instead, plant maintenance personnel used a different method of monitoring electrical connection integrity, specifically measuring and recording the connection resistance readings at an interval of 18 months for the NERC-related batteries and 22 months for the non-NERC batteries, which APC considered a more effective method. APC never updated the Plant Farley program documentation to reflect this new maintenance practice. SERC reviewed a spreadsheet prepared by APC that included each of its generation Protection System devices and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC verified the assigned intervals by reviewing APC’s Protection System maintenance and testing program and the Plant Farley program. Based on this review, SERC determined that APC tested six out of 234 station batteries (2.6%) outside of their defined intervals. In total, APC had six out of 11,735 Protection System devices (0.05%) that were not compliant with PRC-005-1 R2. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. APC's Plant Farley maintained and tested four of the six batteries pursuant to its Plant Farley non-NERC generation Protection System electrical maintenance procedures, which calls for the same maintenance and testing activities as the Plant Farley program, but has a longer defined interval of 42 days plus a grace period of 10 days (compared to a defined interval of 31 days plus a grace period of seven days for the Plant Farley program). The Plant Farley Turbine Building batteries and chargers were monitored and alarmed in the control room to alert APC personnel in the event of problems. Although APC failed to perform thermal scanning every six years on all six generation Protection System battery banks at Plant Farley, as called for in its Plant Farley program, it tested two of the batteries every 18 months and four of the batteries every 22 months by measuring battery connection resistance instead of using thermal scanning. | 6/18/07 (when the Standard became mandatory and enforceable) | 11/15/12 (Mitigation Plan completion) | 14000 | Self-Report | To mitigate this violation, APC: 1) added the battery banks for the Turbine Building at Farley Units 1 and 2 to the Plant Farley program by revising its maintenance and testing program to include data sheets for those battery banks; and 2) revised the Plant Farley program to reflect the current method used to verify battery connection integrity (measurement of electrical resistance or ductor measurement). | 11/15/2012 | 2013-02-14 | Admits | SERC reviewed APC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Details of the compliance program were available internally through the corporate intranet. Compliance-related information was regularly communicated through various means including, email, newsletters, web-based, and classroom training sessions. APC's compliance officer implemented the ICP and reported directly to APC's CEO and had independent access to the APC board of directors' compliance and controls committee. The ICP was fully supported by APC's officers and senior management. The ICP was regularly reviewed by senior management and was subject to internal and external audits on a periodic basis. APC ensured that employees responsible for reliability standards compliance understood their roles through a variety of communications and training. Settlement Agreements covering violations of PRC-005-1 R2 for APC were filed with FERC under NP10-34-000 on December 30, 2009 and NP11-169-000 on April 29, 2011. On March 15, 2010 and May 27, 2011, FERC issued orders stating it would not engage in further review of the Notices of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Gulf Power Company, an affiliate of APC, was filed with FERC under NP10-32-000 on December 30, 2009. On March 15, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Georgia Power Company, an affiliate of APC, was filed with FERC under NP11-20-000 on November 5, 2010. On December 3, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Mississippi Power Company, an affiliate of APC, was filed with FERC under NP10-33-000 on December 30, 2009. On March 15, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Southern Power Company, an affiliate of APC, was filed with FERC under NP10-35-000 on December 30, 2009. On March 15, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that APC's and its affiliates' previous violations of PRC-005-1 R2 constituted prior violations and were an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC2011006761 | Settlement Agreement | On April 29, 2011, LG&E & KU submitted a Self-Report to SERC stating that, as a Balancing Authority (BA), it was in violation of BAL-005-0 R12 because not all Tie Line flows with Adjacent BA Areas were included in its Area Control Error (ACE) calculation. On February 8, 2011, two loads and their associated losses in an adjacent BA were identified as not being included in the ACE calculation, totaling an average load of 5-10 MW. The loads and losses were added to the ACE equation that same day. Before September 21, 2010, when the neighboring BA put in metering for these loads, these loads had been handled via a schedule in the LG&E & KU system, which ensured their inclusion in the ACE calculation. Once the neighboring BA obtained metering capability in September 2010, the loads were treated as a pseudo-tie within the energy management system (EMS) and should have been reflected at that time in the ACE calculation as a deduction. After identifying the issue, LG&E & KU completed a full review of all foreign interchange ties and loads. On March 21, 2011, it was observed that losses of 1-2 MW were not being accounted for in a different neighboring BA's Total Load calculation. The issue was corrected by including the losses in the EMS ACE equation on March 23, 2011. LG&E & KU could not confirm when this issue first occurred, but believe this problem may have existed before June 18, 2007. According to LG&E & KU’s recorded data, during peak hours the total Tie Line flows with these two neighboring BAs were on average 5 MW on a system balancing on average 4,800 MW. | BAL-005-0 | R12 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The combined Tie Line flows that were not included in the ACE calculation were approximately 0.1 % and would have had a small contribution to the Automatic Generation Control if they had been included in ACE calculation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/23/2011 (when the identified loads and losses were included in the ACE calculation) | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) developed a written process and sign-off checklist to ensure that all aspects of the future addition or removal of foreign loads, Tie Lines, and losses are thoroughly and completely addressed with respect to interchange and telemetry and are included in the ACE equation; and 2) provided training to appropriate personnel on the written process and checklist. | 2011-11-29 | 2012-11-19 | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP) ), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC201100752 | Settlement Agreement | On January 26, 2011, LG&E & KU submitted a Self-Report to SERC stating that, as a Balancing Authority (BA), it was in violation of BAL-005-0.1b R6 because on August 19, 2010 it was unable to calculate Area Control Error (ACE) for more than 30 minutes and it did not notify its Reliability Coordinator (RC). On August 18, 2010, at 9:45 p.m., LG&E & KU’s energy management system (EMS) began reporting multiple alarms indicating loss of external power to the Simpsonville transmission control center. The RC posted a notification on the RC information system that LG&E & KU was evacuating its primary control center and reporting to the Dix backup control center. LG&E & KU also notified SERC of the situation via the SERC Situational Awareness Hotline. During the transition from Simpsonville to Dix, LG&E & KU’s EMS was still functional and the regulated generation dispatch personnel, who are NERC RC-certified operators, were able to monitor ACE and frequency, and coordinated the dispatch of generation using the EMS. At Dix, the backup ACE Micro supervisory control and data acquisition (SCADA) system calculated ACE from telemetry independent of the EMS. The operator at the Dix backup control center used this system and relayed information between the Dix backup control center, the RC, Southwest Power Pool as the Independent Transmission Organization, and the LG&E & KU regulated generation dispatch operator for manual coordination of the dispatch of units. At 12:47 a.m. on August 19, 2010, the backup ACE Micro SCADA system was inadvertently turned off at the Dix backup control center by an operator who was trying to get another system rebooted. As a result, LG&E & KU was unable to calculate ACE. By 1:35 a.m. on August 19, 2010, LG&E-KU was calculating ACE automatically. Although the RC was aware of LG&E & KU’s move to the backup control center and was closely monitoring the system, LG&E-KU was unable to provide evidence that it had notified the RC regarding the loss of its ability to calculate ACE. | BAL-005-0.1b | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because LG&E & KU’s failure to notify the RC of its inability to calculate ACE could have left the RC ill-prepared to respond to changes in system conditions and led the RC to make incorrect assumptions regarding LG&E & KU’s response to those changes. However, the RC had received notification of the transfer to the backup control center and was alerted to the fact that LG&E & KU may have trouble performing its functions as the BA. Additionally, LG&E & KU was unable to calculate ACE for only a short period of time (approximately 50 minutes) during off-peak hours. Additionally, LG&E & KU has four redundant EMS servers, two at the primary Simpsonville control center and two at a backup control center, which could have been used to calculate and supply ACE to the personnel performing the BA functions. | 8/19/2010 (LG&E & KU lost ability to calculate ACE and did not notify its RC) | 8/19/2010 (when LG&E & KU regained the ability to calculate ACE) | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) developed BAL-005-0.1b R6 training materials and trained applicable personnel; and 2) assigned the responsibility for monitoring ACE to the BA desk and communicating the loss of an accurate ACE calculation to the recently-created system operations desk, which already serves as the primary point of contact with the RC and LG&E & KU management. | 2011-07-29 | 2012-10-17 | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP) ), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC2011006699 | Settlement Agreement | On April 21, 2011, LG&E & KU submitted a Self-Report to SERC stating that, as a Generator Owner (GO) and Transmission Owner (TO), it was in violation of PRC-005-1 R2 after it discovered Protection System devices that were not being tested pursuant to its maintenance and testing programs. LG&E & KU had a prior violation of PRC-005-1 R2. SERC asked LG&E & KU why the mitigation plan for the prior violation did not address the Protection System devices in the 2011 Self-Report. LG&E & KU stated that it had not identified the indirect impact that Protection System devices for auxiliary equipment could have on generators. After determining that these devices could impact the generators’ lockout relay, LG&E & KU added the generator auxiliary relay instruments to the list of devices that needed to be tested pursuant to its Protection System maintenance and testing program. In addition, LG&E & KU discovered that Protection System devices at the GO/TO interface had not been tested as a result of incorrect assumptions by the GO function that instruments were being maintained and tested by the TO and vice versa. SERC reviewed a spreadsheet prepared by LG&E & KU, which included each of the transmission and generation Protection System devices and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device, and made the following findings: For TO protective relays and GO protective relays, LG&E & KU had 38 of 3,054 devices (1.2%) that were tested outside of the interval defined in the maintenance and testing program, and two of 3,054 devices (less than 1%) that did not have previous test or maintenance records. For TO and GO voltage and current sensing devices, LG&E and KU had 482 of 6,950 devices (6.9%) that did not have previous test/maintenance records. In total, 522 of 11,275 devices (4.6%) were out of compliance. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Eight percent (8%) of LG&E & KU’s protective relays are digital, perform self-testing, and alert LG&E & KU personnel in the event of a failure. Fifty-five percent (55%) of LG&E & KU’s protective relays are single-phase relays monitoring one of three phases. Consequently, if one phase relay failed, the BPS equipment would have still been protected by the other two phase relays if the fault was not limited to a single phase. Sixty-six (66%) percent of LG&E & KU’s protective relays provide overlapping protection for other relays connected to the same equipment and provide continued protection of BPS equipment in the event of a single relay failure. The LG&E & KU current transformers were part of differential protection circuits, which monitor several instruments simultaneously and compare their values to verify that the sum of incoming values equals the sum of outgoing values. If any of the instrument transformers fail, the incoming values and outgoing values would not match, resulting in a protective relay trip and an alert that there was a problem with the circuit. | 6/18/2007 (when the Standard became mandatory and enforceable) | present | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) performed an additional review at the GO/TO interface points to confirm the PRC-005 equipment; 2) selected a data management method to store, track, and report all PRC-005 related equipment; 3) tested all devices that did not have current test records; 4) recorded and reconciled data in data management system; and 5) developed/modified procedures to provide a periodic coordinated review of the information stored using the new data management method. LG&E & KU will complete the following mitigating actions: 1) train applicable personnel on the data management system and new data management method. | 6/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO. A Settlement Agreement covering a violation of PRC-005-1 R2 for LG&E & KU was filed with FERC under NP10-120-000. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that LG&E & KU's previous violation of PRC-005-1 R2 constituted a prior violation and an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC2012009707 | Settlement Agreement | On February 10, 2012, LG&E & KU submitted a Self-Report to SERC stating that, as a Generator Operator, it was in violation of VAR-002-1.1b R3 because on January 24, 2012 it failed to notify the Transmission Operator (TOP) within 30 minutes of a change in status of an automatic voltage regulator (AVR) and that in a number of cases when providing notification to the TOP of a status or capability change on a generator Reactive Power resource, it had failed to provide the expected duration of the change. SERC reviewed the operator log for the January 24, 2012 event, as well as questioned LG&E & KU regarding the details surrounding it. The operator log showed that the Brown Station #2 generator and the associated AVR tripped off-line at 20:57 on January 23, 2012 and that the TOP was notified of this change in status at that time. The Brown Station #2 generator was returned to service and the AVR placed in automatic voltage control mode at 00:40 on January 24, 2012. The TOP was not notified of this change in status of the Brown Station #2 generator AVR until 01:50 on January 24, 2012, 1 hour and 10 minutes after the change occurred. After requesting additional information from LG&E & KU, SERC determined that there was no violation VAR-002-1.1b with regard to expected duration of the change in status or capability. SERC determined that LG&E & KU was in violation of VAR-002-1.1b R3 for failing to notify the TOP within 30 minutes of the change in status of an AVR, as required. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The change in status was from manual to automatic voltage control mode, the required mode of operation. The change in status was reported to the TOP within 1 hour and 10 minutes of the change. | 1/24/2012 (when the status change occurred without notifying the TOP) | 1/24/2012 (when the notification of the change in status was given to the TOP) | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) held training for operators at each generating station regarding the requirements of VAR-002; 2) posted VAR-002 quick reference cards in the control rooms at each generating station; 3) installed AVR status points into the remote terminal units at Brown Station; and 4) modified the software used by the generator operators when providing information to the TOP so that the duration field was a required field instead of an optional field. | 9/14/2012 | 2012-12-11 | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO. A Settlement Agreement covering a violation of VAR-002-1.1a R3 and VAR-002-1 R3 for LG&E & KU was filed with FERC under NP12-33-000. On July 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that LG&E & KU's these previous violations constituted prior violations and an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC2012011080 | Settlement Agreement | On September 18, 2012, LG&E & KU submitted a Self-Report to SERC stating that, as a Generator Operator, it was in violation of VAR-002-1.1b R2 because the integrated hourly average of the transmission bus voltage was outside the tolerance band for one hour on May 20, 2012. According to LG&E & KU, the Transmission Operator's (TOP) established voltage schedule for Green River Generating Station (GR) was 141 kV with a tolerance band of 140 kV–142 kV. The voltage schedule is based on an integrated hourly average of the voltage. On May 20, 2012, from 01:00 a.m. to 02:00 a.m., the integrated hourly average was 143 kV, 1 kV outside of the tolerance band. At 01:00 a.m. on May 20, 2012, a vendor began performing network maintenance that resulted in a communication interruption between the GR’s data control system (DCS) and the energy management system (EMS) at 01:11 a.m., rendering the primary voltage indication nonfunctional. The DCS could no longer receive real-time voltage readings, and as a result stored the last real-time voltage value it had received prior to the interruption for the duration of the communication interruption. Therefore, the bus voltage master (BVM) increased the voltage due to the DCS inability to communicate with the EMS and update the real-time voltage value. At 01:56 a.m., after performing a series of routine duties, an employee noticed that the legacy analog meter measured a voltage above 142 kV. The BVM immediately was switched from automatic to manual. The voltage was decreased and maintained within the TOP-established schedule. At 04:47 a.m. , the network maintenance restored communication between GR’s DCS and the EMS. SERC reviewed additional information which included a summary of voltage excursions including comments regarding notification to the TOP, a generation voltage regulation log showing notifications to the TOP of voltage excursions at GR, EMS and real-time data comparisons, and the EMS hourly averages for the 138 kV voltage at GR. Based on its review of this information, SERC verified that for one hour on May 20, 2012, LG&E & KU exceeded the TOP-established voltage schedule for GR. At the request of SERC, LG&E & KU verified that there were no other instances of failure to meet the TOP-established voltage schedule. | VAR-002-1.1b | R2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The voltage was 1 kV above the tolerance band. The duration of the voltage excursion lasted 65 minutes. LG&E & KU modeled the conditions for the period in question and an N-1 contingency analysis was performed. It was determined that no thermal or voltage violations were incurred. | 5/20/2012 (when the voltage increased above the acceptable bandwidth) | 5/20/2012 (when the voltage returned to the bandwidth set by the schedule) | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) implemented DCS functionality that automatically switches the BVM mode of operation from automatic to manual when the DCS registers a possible remote terminal unit or voltage indication failure alarm; and 2) installed a voltage meter with multiple digital outputs for the single voltage analog signal input from the potential transformer. The meter reads the analog signal, converts it to a digital value, and transmits the value simultaneously to the plant’s DCS and the EMS’s remote terminal unit. | 2013-02-25 | 2013-02-27 | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO. A Settlement Agreement covering a violation of VAR-002-1.1a R2 for LG&E & KU was filed with FERC under NP12-33-000. On July 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of VAR-002-1.1a R2 for LG&E & KU was filed with FERC under NP11-97-000. A Settlement Agreement covering a violation of VAR-002-1 R2 for LG&E & KU was filed with FERC under NP10-120-000. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that LG&E & KU's these previous violations constituted prior violations and an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E & KU) | NCR01223 | SERC2012010373 | Settlement Agreement | On May 31, 2012, LG&E & KU submitted a Self-Report to SERC stating that, as a Transmission Owner, it was in violation of PRC-023-1 R1 because it discovered six instances of wrong settings for relay loadability. In two instances, a setting was not enabled in the field that would increase the loadability of the relay at each end of a 345 kV line to the correct setting. The other four instances were calculations that resulted in a setting less than the specified 150%. Three 345 kV lines were affected. SERC requested and reviewed additional information in order to complete its assessment. According to LG&E & KU, it only used R1.1 and R1.10 to comply with the Standard. The six relays at issue were set based on R1.1 criteria. The cause of four of the relay settings being below 150% was incorrect calculations. The cause of the additional two relay settings being below 150% was incorrect field settings in the field, however the calculation was correct. | PRC-023-1 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failing to provide enough margin between relay set points and the associated Facility Rating could result in Facilities being automatically removed from service without providing operators enough time to mitigate overload conditions. However, for the six relays classified as R1.1, the average relay set points were 298.5% of the maximum historical loads and never less than 143.1%, therefore indicating the unlikeliness the set points would have limited loadability. | 7/1/2010 (when the Standard became mandatory and enforceable) | 12/28/2012 (Mitigation Plan completion) | $40,000 (for SERC2011006761, SERC201100752, SERC2011006699, SERC2012009707, SERC2012011080 and SERC2012010373) | Self-Report | To mitigate this violation, LG&E & KU: 1) developed and documented a process to ensure the loadability of transmission terminals is accounted for in protective relay settings; 2) developed and documented a process to ensure that the transmission relay settings specified by the engineer match the settings installed in the field; and 3) corrected the settings on the six relays and verified that all of the field settings on existing PRC-023 eligible transmission relays match the file settings. | 2012-12-28 | 2013-02-25 | Neither Admits nor Denies | SERC reviewed LG&E & KU's documented internal compliance program (ICP), which provides the framework for its internal compliance structure, and considered it to be a neutral factor in the penalty determination. The ICP is reviewed and modified, if necessary, on an annual basis. The ICP requires that all senior management be responsible for ensuring that their subordinates cooperate, are aware of, and understand the ICP. LG&E & KU senior management is involved in the compliance program. The steering committee, which meets monthly and is comprised of approximately 15 officers and other senior managers, approves and reviews the ICP, assigns roles, and monitors all activities related to compliance. LG&E & KU’s compliance department is responsible for maintaining and implementing the ICP. The director of compliance and ethics, who is also LG&E & KU’s compliance officer, has oversight of the ICP and independent access to the CEO.
Texas Reliability Entity, Inc (Texas RE) | Texas-New Mexico Power Co (TNMP) | NCR04143 | TRE201100387 | Settlement Agreement | On August 31, 2010, TNMP submitted a Self-Certification to Texas RE indicating, that as a Transmission Planner, it was in violation of FAC-014-1 R4 because it did not establish System Operating Limits (SOLs) consistent with the Electric Reliability Council of Texas' (ERCOT) SOL methodology. ERCOT serves as TNMP's Planning Authority. TNMP established SOLs for all of its facilities but failed to conduct a simulated stability analysis pursuant to the ”ERCOT System Planning SOL Methodology for Planning Horizon R3.0.” The omitted analysis includes the review of transient, dynamic, and voltage stability studies for the SOLs. | FAC-014-1 | R4 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). Without a valid stability assessment, what may be perceived as stable operation could be the initiation of an unstable condition. Operating with SOLs that have not been validated places the BPS at risk for cascading outages or uncontrolled separation. However, this risk was partially mitigated by TNMP having established SOLs. In addition, although the stability analysis was not performed, TNMP’s internal controls led TNMP to the discovery of the omitted stability analysis, which was promptly addressed upon discovery. | 1/1/2009 (when the Standard became mandatory and enforceable) | 4/4/2011 (Mitigation Plan completion) | $7,000 (for TRE201100387, TRE201100388, TRE201100389, and TRE201100390) | Self-Certification | To mitigate this violation, TNMP 1) completed the necessary stability analysis and submitted the associated assessment report ERCOT on April 4, 2011; and 2) incorporated stability studies into its annual system assessments and methodology for establishing SOLs to reduce the likelihood of future reoccurrences of this violation. | 2011-04-04 | 2013-02-05 | Neither Admits nor Denies | Texas RE reviewed TNMP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. As an affiliate of PNM Resources (PNMR), TNMP is part of an enterprise-wide internal compliance program administered by PNMR's NERC Compliance Department. PNMR’s overall Corporate Compliance Program is managed independently of the affiliate organizations and respective business units responsible for operational compliance with the NERC Reliability Standards. Responsibility for TNMP’s implementation of PNMR’s NERC Compliance Program (NCP) is distributed within TNMP to include both cross-functional teams and employees within TNMP that coordinate NERC compliance activities and communication with the management for each Registered Entity's business unit. PNMR’s Director, NERC Compliance, serves as TNMP’s Reliability Compliance Manager, and has direct access to both TNMP’s President and the PNMR CEO and Board of Directors. PNMR’s NCP also consists of internal audits, compliance gap assessments, regular reviews of its own compliance policies, and training for other PNMR staff on NERC compliance. In addition to activities identified in the mitigation plans associated with these violations, TNMP also performed a number of activities well beyond strict adherence to requirements associated with the violations. The activities included but were not limited to adding a third Transmission Planner, hiring three engineers representing an additional annual financial commitment in excess of $285,000, budgeting $90,000 for the addition of a dedicated NERC Compliance Project Manager, and administering at least 300 hours of one-on-one training to the transmission planners on an annual basis.
Texas Reliability Entity, Inc (Texas RE) | Texas-New Mexico Power Co (TNMP) | NCR04143 | TRE201100388 | Settlement Agreement | On July 18, 2011, TNMP submitted a Self-Certification to Texas RE stating, that as a Transmission Planner (TP), it was in violation of TPL-002-0 R1. TNMP failed to demonstrate, through a complete assessment, that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels, over the range of forecast system demands, under the contingency conditions as defined in Table 1, Category B, which is included in TPL-002-0. Specifically, TNMP failed to conduct a stability analysis to test system performance under the conditions defined in Category B of Table 1 to demonstrate that system performance met the criteria for Category B contingencies for all contingencies applicable to Category B. | TPL-002-0 | R1; R1.3; R1.3.1; R1.3.7; R1.5 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). Without a valid stability assessment, what may be perceived as stable operation could be the initiation of an unstable condition. Operating with SOLs that have not been validated places the BPS at risk for cascading outages or uncontrolled separation. However, this risk was partially mitigated by TNMP having established SOLs. In addition, although the stability analysis was not performed, TNMP’s internal controls led TNMP to the discovery of the omitted stability analysis, which was promptly addressed upon discovery. | 6/28/2007 (when TNMP registered as a TP) | 4/4/2011 (Mitigation Plan completion) | $7,000 (for TRE201100387, TRE201100388, TRE201100389, and TRE201100390) | Self-Certification | To mitigate this violation, TNMP 1) conducted stability studies for the relevant parts of its transmission planning area to assess performance under NERC Category B, C, and D conditions that were previously missed; 2) completed the necessary studies and documented the findings within its transmission assessment; 3) completed stability studies for all areas that TNMP serves as a TP; and 4) incorporated stability studies into its annual system assessments and methodology for establishing SOLs to reduce the likelihood of future reoccurrences of this violation. | 2011-04-04 | 2013-02-05 | Neither Admits nor Denies | Texas RE reviewed TNMP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. As an affiliate of PNM Resources (PNMR), TNMP is part of an enterprise-wide internal compliance program administered by PNMR's NERC Compliance Department. PNMR’s overall Corporate Compliance Program is managed independently of the affiliate organizations and respective business units responsible for operational compliance with the NERC Reliability Standards. Responsibility for TNMP’s implementation of PNMR’s NERC Compliance Program (NCP) is distributed within TNMP to include both cross-functional teams and employees within TNMP that coordinate NERC compliance activities and communication with the management for each Registered Entity's business unit. PNMR’s Director, NERC Compliance, serves as TNMP’s Reliability Compliance Manager, and has direct access to both TNMP’s President and the PNMR CEO and Board of Directors. PNMR’s NCP also consists of internal audits, compliance gap assessments, regular reviews of its own compliance policies, and training for other PNMR staff on NERC compliance. In addition to activities identified in the mitigation plans associated with these violations, TNMP also performed a number of activities well beyond strict adherence to requirements associated with the violations. The activities included but were not limited to adding a third Transmission Planner, hiring three engineers representing an additional annual financial commitment in excess of $285,000, budgeting $90,000 for the addition of a dedicated NERC Compliance Project Manager, and administering at least 300 hours of one-an-one training to the transmission planners on an annual basis.
Texas Reliability Entity, Inc (Texas RE) | Texas-New Mexico Power Co (TNMP) | NCR04143 | TRE201100389 | Settlement Agreement | On July 18, 2011, TNMP submitted a Self-Certification to Texas RE stating, that as a Transmission Planner (TP), it was in violation of TPL-003-0 R1. TNMP failed to demonstrate, through a complete assessment, that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels, over the range of forecast system demands, under the contingency conditions as defined in Table 1, Category C, which is included in TPL-003-0. Specifically, TNMP failed to conduct a stability analysis to test system performance under the conditions defined in Category C of Table 1 to demonstrate that system performance met the criteria for Category C contingencies for all contingencies applicable to Category C. | TPL-003-0 | R1; R1.3; R1.3.1; R1.3.7; R1.5 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). Without a valid stability assessment, what may be perceived as stable operation could be the initiation of an unstable condition. Operating with SOLs that have not been validated places the BPS at risk for cascading outages or uncontrolled separation. However, this risk was partially mitigated by TNMP having established SOLs. In addition, although the stability analysis was not performed, TNMP’s internal controls led TNMP to the discovery of the omitted stability analysis, which was promptly addressed upon discovery. | 6/28/2007 (when TNMP registered as a TP) | 4/4/2011 (Mitigation Plan completion) | $7,000 (for TRE201100387, TRE201100388, TRE201100389, and TRE201100390) | Self-Certification | To mitigate this violation, TNMP 1) conducted stability studies for the relevant parts of its transmission planning area to assess performance under NERC Category B, C, and D conditions that were previously missed; 2) completed the necessary studies and documented the findings within its transmission assessment; 3) completed stability studies for all areas that TNMP serves as a TP; and 4) incorporated stability studies into its annual system assessments and methodology for establishing SOLs to reduce the likelihood of future reoccurrences of this violation. | 2011-04-04 | 2013-02-05 | Neither Admits nor Denies | Texas RE reviewed TNMP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. As an affiliate of PNM Resources (PNMR), TNMP is part of an enterprise-wide internal compliance program administered by PNMR's NERC Compliance Department. PNMR’s overall Corporate Compliance Program is managed independently of the affiliate organizations and respective business units responsible for operational compliance with the NERC Reliability Standards. Responsibility for TNMP’s implementation of PNMR’s NERC Compliance Program (NCP) is distributed within TNMP to include both cross-functional teams and employees within TNMP that coordinate NERC compliance activities and communication with the management for each Registered Entity's business unit. PNMR’s Director, NERC Compliance, serves as TNMP’s Reliability Compliance Manager, and has direct access to both TNMP’s President and the PNMR CEO and Board of Directors. PNMR’s NCP also consists of internal audits, compliance gap assessments, regular reviews of its own compliance policies, and training for other PNMR staff on NERC compliance. In addition to activities identified in the mitigation plans associated with these violations, TNMP also performed a number of activities well beyond strict adherence to requirements associated with the violations. The activities included but were not limited to adding a third Transmission Planner, hiring three engineers representing an additional annual financial commitment in excess of $285,000, budgeting $90,000 for the addition of a dedicated NERC Compliance Project Manager, and administering at least 300 hours of one-an-one training to the transmission planners on an annual basis.
Texas Reliability Entity, Inc (Texas RE) | Texas-New Mexico Power Co (TNMP) | NCR04143 | TRE201100390 | Settlement Agreement | On July 18, 2011, TNMP submitted a Self-Certification to Texas RE stating, that as a Transmission Planner (TP), it was in violation of TPL-004-0 R1. TNMP failed to demonstrate, through a complete assessment, that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels, over the range of forecast system demands, under the contingency conditions as defined in Table I, Category D, which is included in TPL-004-0. Specifically, TNMP failed to conduct a stability analysis to test system performance under the conditions defined in Category D of Table 1 to demonstrate that system performance met the criteria for Category D contingencies for all contingencies applicable to Category D. | TPL-004-0 | R1; R1.3; R1.3.1; R1.4 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). Without a valid stability assessment, what may be perceived as stable operation could be the initiation of an unstable condition. Operating with SOLs that have not been validated places the BPS at risk for cascading outages or uncontrolled separation. However, this risk was partially mitigated by SOLs. In addition, although the stability analysis was not performed, TNMP’s internal controls led TNMP to the discovery of the omitted stability analysis, which was promptly addressed upon discovery. | 6/28/2007 (when TNMP registered as a TP) | 4/4/2011 (Mitigation Plan completion) | $7,000 (for TRE201100387, TRE201100388, TRE201100389, and TRE201100390) | Self-Certification | To mitigate this violation, TNMP 1) conducted stability studies for the relevant parts of its transmission planning area to assess performance under NERC Category B, C, and D conditions that were previously missed; 2) completed the necessary studies and documented the findings within its transmission assessment; 3) completed stability studies for all areas that TNMP serves as a TP; and 4) incorporated stability studies into its annual system assessments and methodology for establishing SOLs to reduce the likelihood of future reoccurrences of this violation. | 2011-04-04 | 2013-02-05 | Neither Admits nor Denies | Texas RE reviewed TNMP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. As an affiliate of PNM Resources (PNMR), TNMP is part of an enterprise-wide internal compliance program administered by PNMR's NERC Compliance Department. PNMR’s overall Corporate Compliance Program is managed independently of the affiliate organizations and respective business units responsible for operational compliance with the NERC Reliability Standards. Responsibility for TNMP’s implementation of PNMR’s NERC Compliance Program (NCP) is distributed within TNMP to include both cross-functional teams and employees within TNMP that coordinate NERC compliance activities and communication with the management for each Registered Entity's business unit. PNMR’s Director, NERC Compliance, serves as TNMP’s Reliability Compliance Manager, and has direct access to both TNMP’s President and the PNMR CEO and Board of Directors. PNMR’s NCP also consists of internal audits, compliance gap assessments, regular reviews of its own compliance policies, and training for other PNMR staff on NERC compliance. In addition to activities identified in the mitigation plans associated with these violations, TNMP also performed a number of activities well beyond strict adherence to requirements associated with the violations. The activities included but were not limited to adding a third Transmission Planner, hiring three engineers representing an additional annual financial commitment in excess of $285,000, budgeting $90,000 for the addition of a dedicated NERC Compliance Project Manager, and administering at least 300 hours of one-an-one training to the transmission planners on an annual basis.
Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC), d/b/a NV Energy | NCR05390 | WECC201002416 | Settlement Agreement | On October 21, 2010, SPPC submitted a Self-Report to WECC stating that, as a Generator Operator, it was in violation of VAR-002-1.1a R3. WECC subject matter experts (SMEs) reviewed the Self-Report and determined the SPPC North Valmy Station Unit 1 was in service with the Power System Stabilizer (PSS) out of service from July 20, 2010 through July 26, 2010. The SME noted that when the control room operator noticed the PSS was not in service, the operator immediately notified the Transmission Operator (TOP) and returned the PSS to service. By the time SPPC was aware of the change in status of the PSS, the allotted thirty-minute window to notify the TOP had elapsed. The SME determined SPPC's failure to notify the TOP within 30 minutes of a change in status of the PSS resulted in a violation of VAR-002-1.1a R3. The SME forwarded the Self-Report and the SME's findings to Enforcement. Enforcement reviewed the Self-Report and the SME's findings. Enforcement determined SPPC's failure to notify the TOP within 30 minutes of a change in status of the PSS resulted is a violation of VAR-002-1.1a R3. | VAR-002-1.1a | R3 | Medium | Lower | This violation posed minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The PSS remained in service for all other SPPC units when the Valmy Station Unit 1 PSS was offline. The Valmy Unit 1 has a total capacity of approximately 254 MW and SPPC's total generating capacity is approximately 2,000 MW. Therefore, if the Valmy unit started to swing, the PSS on the remaining units (representing 88 percent of the SPPC system) would protect the SPPC system and the BPS. | 7/20/2010 (when the PSS outage began) | 7/26/2010 (when the PSS was restored and TOP was notified of the change of status) | $16,400 (for WECC201102424, WECC201102425, WECC201102426, WECC201102438, WECC201002416) | Self-Report | To mitigate this violation, SPPC: 1) created and implemented an alarm, better to provide PSS status and operation to SPPC Generator Operators; 2) created and placed on the plant information status screen for each generating unit in the control room a PSS "ON" or "OFF" status graphic. When the PSS is detected "OFF," the status will change colors and flash; 3) addressed control room staff performance issues; and 4) provided refresher training regarding the requisite TOP notification and other NERC compliance components of this Standard. | 2010-08-31 | 2011-04-15 | Neither Admits nor Denies | WECC evaluated SPPC's internal compliance program (ICP) and found the following: SPPC has a fully documented ICP that has been reviewed and approved by general counsel who also serves as its chief compliance officer. SPPC's oversight position is identified and staffed, and is supervised at a high level within the company. The ICP oversight position has direct access to the CEO and board of directors and SPPC operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards. The ICP has sufficient staff and an adequate budget, SPPC senior management support and participate in the ICP, and SPPC's ICP has an annual review cycle. Based on these findings, WECC concluded that SPPC has an effective compliance culture.