## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Basin Electric Power Cooperative (BEPC) | NCR00102 | MRO201000236 | Notice of Confirmed Violation | During a Compliance Audit conducted from August 23, 2010 through September 1, 2010, MRO determined that BEPC, as a Distribution Provider and Transmission Owner, failed to have a Protection System maintenance and testing program with intervals and the basis for the intervals, as well as a summary of maintenance and testing procedures. BEPC had separate Protection System maintenance and testing programs for each of its member cooperatives. One of BEPC's member cooperatives, Northern Iowa Power Cooperative (NIPCO) had a Protection System maintenance and testing program that only identified relays. It did not address other Protection System devices such as station batteries, current and voltage sensing devices, DC circuitry, and associated communications systems. Additionally, the basis for the five-year interval used was not identified, and the document did not provide a summary of maintenance and testing procedures. Another BEPC member cooperative, Central Power Electric Cooperative (CPEC), failed to provide evidence of a Protection System maintenance and testing program prior to October 15, 2007. Another BEPC member cooperative, East River Electric Power Cooperative (EREPC), had a Protection System maintenance and testing program in place from June 2007 to October 2007, but it only identified relays and station batteries. EREPC's program failed to address other Protection System components such as current and voltage sensing devices, DC circuitry, and associated communication systems. Additionally the basis for the three-year interval for battery maintenance and testing was not identified. EREPC's Protection System maintenance and testing program also did not provide a summary of maintenance and testing procedures. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although BEPC and three of its members did not have Protection System maintenance and testing intervals and their respective basis for several device types or a summary of procedures, BEPC and the three members provided maintenance and testing records for over 99% of their Protection System devices. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/29/2012 (Mitigation Plan completion) | $0 (for MRO201000236, MRO201000237, and MRO201100435) | Compliance Audit | To mitigate this violation, BEPC: 1) entered into a contract with NIPCO pursuant to which BEPC will maintain and test NIPCO's only BPS facility, the Eagle Substation, including the transmission system Protection Systems, pursuant to BEPC's Protection System maintenance and testing program; 2) revised its transmission and generation Protection System maintenance and testing program to include NIPCO's Eagle 230 kV Substation; 3) CPEC revised and implemented a Protection System maintenance and testing program to address all components identified as Protection System devices and the basis for their testing and maintenance intervals; and 4) EREPC revised and implemented a Protection System maintenance and testing program that addressed all components identified as Protection System devices and the basis for their testing and maintenance intervals. | 5/29/2012 | 5/29/2012 | Admits | MRO reviewed BEPC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. BEPC contracted with a third-party NERC compliance consultant to provide BEPC and its member cooperatives with a software solution to provide continuous monitoring of BEPC's ICP and the activities required by the applicable NERC Reliability Standards. BEPC's compliance project included: 1) training to both BEPC and member cooperatives employees on the consultant's compliance system; 2) consultant staff conducting a compliance assessment of BEPC and identified changes necessary prior to implementing the software; 3) BEPC and the consultant working to implement all identified changes and modifications for its policies, procedures and programs; 4) utilizing consultant's software for continuous compliance; 5) the consultant's software: a) identifying all evidence required for monitoring, prompting subject matter experts for upcoming compliance due dates, measuring compliance on a continuous basis and incorporating new Standards and/or corporate changes; and b) aligning BEPC and its member cooperatives with the objectives produced by MRO's performance and risk oversight committee; and 6) investing more than $750,000 towards improving its ICP on behalf of itself and its member cooperatives.
Midwest Reliability Organization (MRO) | Basin Electric Power Cooperative (BEPC) | NCR00102 | MRO201100435 | Notice of Confirmed Violation | On December 13, 2011, BEPC submitted a Self-Report to MRO stating that, as a Distribution Provider and Transmission Owner, it was in violation of PRC-005-1 R1. Two of BEPC's member cooperatives, Central Power Electric Cooperative (CPEC) and East River Electric Power Cooperative (EREPC), failed to include a summary of maintenance and testing procedures for protective relays in their Protection System maintenance and testing programs as required by the Mitigation Plan for NERC violation identification number MRO201000236, with a completion date of October 15, 2011. BEPC did not request an extension for Mitigation Plan completion prior to October 15, 2011, and instead, self-reported this violation. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although CPEC and EREPC did not have Protection System maintenance and testing intervals and their respective basis for several device types or a summary of procedures, they provided maintenance and testing records for over 99% of their Protection System devices. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/29/2012 (Mitigation Plan completion) | $0 (for MRO201000236, MRO201000237, and MRO201100435) | Self-Report | To mitigate this violation, BEPC, with CPEC and ERPEC, adopted a single unified transmission Protection System maintenance and testing program. | 5/29/2012 | 5/29/2012 | Admits | MRO reviewed BEPC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. BEPC contracted with a third-party NERC compliance consultant to provide BEPC and its member cooperatives with a software solution to provide continuous monitoring of BEPC's ICP and the activities required by the applicable NERC Reliability Standards. BEPC's compliance project included: 1) training to both BEPC and member cooperatives employees on the consultant's compliance system; 2) consultant staff conducting a compliance assessment of BEPC and identified changes necessary prior to implementing the software; 3) BEPC and the consultant working to implement all identified changes and modifications for its policies, procedures and programs; 4) utilizing consultant's software for continuous compliance; 5) the consultant's software: a) identifying all evidence required for monitoring, prompting subject matter experts for upcoming compliance due dates, measuring compliance on a continuous basis and incorporating new Standards and/or corporate changes; and b) aligning BEPC and its member cooperatives with the objectives produced by MRO's performance and risk oversight committee; and 6) investing more than $750,000 towards improving its ICP on behalf of itself and its member cooperatives.
Midwest Reliability Organization (MRO) | Basin Electric Power Cooperative (BEPC) | NCR00102 | MRO201000237 | Notice of Confirmed Violation | During a Compliance Audit conducted from August 23, 2010 through September 1, 2010, MRO determined that BEPC, as a Distribution Provider and Transmission Owner, failed to provide evidence that Protection System devices were maintained and tested within the defined intervals in accordance with its Protection System maintenance and testing program, as required by PRC-005-1 R2.1. Specifically, one of BEPC's members, East River Electric Power Cooperative (EREPC) with Protection System components subject to PRC-005-1 R2 identified 15 Protection System relays that missed the six-year maintenance and testing cycle by fewer than 30 days. BEPC and its member cooperatives with Protection System components subject to PRC-005-1 R2 performed a full inventory of their Protection System devices and reported that collectively, have: 1,337 Protection System relays; 48 associated communication systems; 235 voltage and current system devices; 51 station batteries; and 158 DC control circuits. Of those devices, BEPC failed to provide maintenance and testing records for 15 Protection System relays, which accounts for fewer than 1% of BEPC's total of 1,829 Protection System devices. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 15 affected relays are located at a substation in Bristol, South Dakota and are associated with 115 kV transmission circuits. Additionally, the six-year maintenance and testing interval was missed by fewer than 30 days in each instance. | 6/18/2007 (when the Standard became mandatory and enforceable) | 10/19/2012 (Mitigation Plan completion) | $0 (for MRO201000236, MRO201000237, and MRO201100435) | Compliance Audit | To mitigate this violation, BEPC: 1) revised its data retention procedures to ensure that backup maintenance and testing records are maintained; 2) performed, with its member cooperatives, a comprehensive review of their Protection System maintenance and testing records; and 3) performed testing on devices missing records. | 2012-10-19 | 2012-10-29 | Admits | MRO reviewed BEPC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. BEPC contracted with a third-party NERC compliance consultant to provide BEPC and its member cooperatives with a software solution to provide continuous monitoring of BEPC's ICP and the activities required by the applicable NERC Reliability Standards. BEPC's compliance project included: 1) training to both BEPC and member cooperatives employees on the consultant's compliance system; 2) consultant staff conducting a compliance assessment of BEPC and identified changes necessary prior to implementing the software; 3) BEPC and the consultant working to implement all identified changes and modifications for its policies, procedures and programs; 4) utilizing consultant's software for continuous compliance; 5) the consultant's software: a) identifying all evidence required for monitoring, prompting subject matter experts for upcoming compliance due dates, measuring compliance on a continuous basis and incorporating new Standards and/or corporate changes; and b) aligning BEPC and its member cooperatives with the objectives produced by MRO's performance and risk oversight committee; and 6) investing more than $750,000 towards improving its ICP on behalf of itself and its member cooperatives.
Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA (NG) | NCR11171 | NPCC2012010579 | Notice of Confirmed Violation | On June 18, 2012, NG submitted a Self-Report to NPCC stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2.1. On two 345 kV transmission lines, monthly testing of the directional comparison blocking carrier systems was not performed within the defined interval as specified in its Protection System maintenance and testing program. Subsequently, upon implementing the Mitigation Plan, NG identified a failure to perform a monthly test on another 345 kV transmission line. Testing was missed for 3 out of 116 (2.59%) communication systems. Between the period of June 2007 to March 2009, NG provided documentation evidencing that monthly testing on both of these lines did occur in certain months, but the documentation did not show that the testing occurred on a monthly basis during that time period. Also, there was no documentation found for monthly testing from March 2009 until March 2012. | PRC-005-1 | R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC determined that the violation posed a moderate risk because without performing the monthly testing, it was unknown whether the carrier system would operate properly for external faults and possibly result in misoperations. The risk was mitigated because, from June 2007 to March 2009, NG was performing testing on both lines, just not on a monthly basis. Additionally, high-speed clearing on both the primary and secondary lines of protection was in service at all times providing proper clearing for circuit faults. Finally, annual testing of the directional comparison blocking carrier systems was completed with no problems found, and records indicate that there were no misoperations of these transmission lines involving the carrier systems while the monthly testing was not being performed. | 6/21/2007 (when NG registered as a TO) | 3/9/2012 (when the missed monthly testing was completed) | 0 | Self-Report | To mitigate this issue, NG: 1) reinstated monthly manual testing of channel health per NG's procedure; 2) completed a review of on/off power line carrier systems without automatic check-back equipment in New England and New York to ensure monthly checks of communication channels are being conducted consistent with internal procedure; 3) provided awareness training to substation operations and maintenance services to highlight those maintenance activities that support compliance with PRC-005-1; and 4) developed and implemented training materials for Protection System compliance requirements for all protection operations supervisors and technicians. | 2012-09-07 | 2013-01-16 | Admits | NPCC reviewed NG's internal compliance program and considered it to be a mitigating factor in the penalty determination. A Find, Fix, Track and Report (FFT) information filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1a R2.1 for NG was filed with FERC under RC13-1-000 on October 31, 2012. The 60-day review period passed on December 31, 2012. Settlement Agreements covering violations of PRC-005-1 R2 for National Grid Generation LLC were filed with FERC under NP10-128-000 on July 6, 2010. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. NPCC determined that this prior issue should not serve as a basis for aggravating the penalty because it did not involve same or similar conduct as the instant case and was filed as an FFT with minimal risk. NPCC determined that the prior violation should not serve as a basis for aggravating the penalty because the issue was different from the instant violation and it involved not performing testing on current transformers, voltage transformers, and batteries along with documentation issues. NPCC assessed a $0 penalty because NG agreed to the violation and the annual testing of the directional comparison blocking carrier system was performed. Additionally, the testing of the protective relay systems was completed within the defined interval to ensure that the clearing would be proper for a fault on the line.
ReliabilityFirst Corporation (ReliabilityFirst) | CMS Generation Michigan Power, L.L.C. (CMSMP) | NCR00727 | RFC2012011195 | Settlement Agreement | On October 2, 2012, CMSMP, in its capacity as a Generator Owner self-certified a noncompliance with PRC-005-1.1b R2 to ReliabilityFirst. Due to miscommunication between CMSMP and its testing contractor, as well as insufficient documentation, CMSMP failed to perform maintenance and testing on the 32 voltage sensing devices (PT) at its Livingston generating station within the defined seven-year interval. CMSMP discovered the issue while preparing for the ReliabilityFirst self-certification. ReliabilityFirst determined that CMSMP violated PRC-005-1 R2 by failing to have evidence it maintained and tested certain Protection System devices within defined intervals. | PRC-005-1.1b | R2; R2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because the relays have both audible and visual alarms located in the Livingston generating station control room. The visual alarms are within direct line-of-sight of the operator, and the audible alarms actuate in the control room to alert the operator. The control room at Livingston generating station is manned at all times when the plant is running. CMSMP experienced no misoperations during the time period of the violation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 10/19/2012 (when CMSMP performed maintenance and testing on the PTs) | 0 | Self-Certification | To mitigate this violation, CMSMP: 1) identified and tested the associated PTs; 2) created a preventative work order plan that will automatically create a work order for the scheduled maintenance and testing activities related to PTs; 3) added each PT to the maintenance and testing tracking spreadsheet; 4) added the latest test completion result information into its SharePoint site for document retention; and 5) completed pre-job brief training. | 2012-10-24 | 2013-04-03 | Admits | ReliabilityFirst reviewed CMSMP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. CMSMP participates in the corporate compliance program of CMS Energy Corporation (CMS). The compliance program is well-documented and distributed throughout the company, and employees participate in yearly training on topics related to compliance. The regulatory compliance program utilizes the Treadway Commission’s Committee of Sponsoring Organizations principles of control environment, risk assessment, information and communication, control activities, and monitoring. The Chief Compliance Officer oversees the CMS Enterprises Compliance Review Committee, demonstrating senior management’s active role in compliance. The CMS Enterprises Compliance Review Committee monitors policies, procedures, implementation, and execution of the enterprises’ regulatory compliance, including NERC compliance. CMSMP promptly corrected the violation at issue due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst seeks to encourage this type of behavior by imposing no monetary penalty for the violation. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. This is CMSMP’s first violation of PRC-005-1 R2. Certain of CMSMP’s affiliated entities have previous violations of PRC-005-1 R2. Although ReliabilityFirst considered CMSMP’s affiliated entities violation history as an aggravating factor, ReliabilityFirst determined that CMSMP’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Electric Utilities Corporation (PPL EU) | NCR00884 | RFC2012011124 | Settlement Agreement | On September 12, 2012, PPL EU submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2 because it failed to provide evidence that its Protection System devices were maintained and tested within the defined intervals. PPL EU verbally informed ReliabilityFirst of this violation on June 13, 2012, and on September 12, 2012, PPL EU submitted a written Self-Report. On February 6, 2012, the Northampton Generating Company (NGC), which interconnects with PPL EU, informed PPL EU that its generating facility would be on a planned outage and inquired whether PPL EU would like to test its relays during the outage. At the time of this inquiry, it was PPL EU’s understanding that NGC owned and maintained all relays at the facility. Despite not confirming ownership or maintenance responsibility for each of the relay devices at issue, NGC and PPL EU agreed to have all relays due for maintenance and testing to be maintained and tested pursuant to the PPL EU relay Protection System maintenance and testing program during the facility outage in April 2012. Of the 18 relays at issue, 16 were overdue for maintenance and testing pursuant to that program. One of the relays was last tested in 2010 and subsequently replaced in 2012; one of the relays was last tested in 2009; four of the relays were last tested in 2007; four of the relays were last tested in 2005; four of the relays were last tested in 1997; and two of the relays were last tested in 1995. The results of the tests demonstrated that all Protection System components were functioning as designed. PPL EU and NGC have not determined long-term responsibility for the relays at the NGC facility. Until PPL EU and NGC make a final determination as to ownership and maintenance and testing responsibility, PPL EU and NGC agreed that PPL EU would include each of the 18 relays in its Protection System maintenance and testing program. | PRC-005-1 | R2 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because the maintenance and testing responsibilities were unclear for five years. These devices were not in a maintenance and testing program until 2012. However, the relays at issue constitute 0.26% of PPL EU’s relays, and the April 2012 tests demonstrated that all Protection System components were functioning as designed. The relays at issue have alarms and primary and backup protection. In addition, there were no misoperations related to these relays. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/29/2012 (when PPL EU performed maintenance and testing on the relays) | 0 | Self-Report | To mitigate this violation, PPL EU: 1) tested all relays located at the NGC facility regardless of ownership; 2) completed an assessment of the relays located at the NGC facility; 3) resolved open issues regarding relay ownership with NGC; 4) identified the scope of generators interconnected with PPL EU for relay ownership purposes; 5) completed a review of relay ownership for the generation facilities; and 6) completed required testing on PPL EU relays identified during the reviews. | 2013-04-30 | 2013-05-16 | Admits | ReliabilityFirst reviewed PPL EU's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. PPL’s compliance program governs the compliance activities of PPL’s subsidiaries in the ReliabilityFirst region, including PPL EU. PPL’s chief compliance officer has independent access to the CEO as well as the board of directors, and senior management both supports and participates in compliance activities. PPL operates and manages its NERC compliance program separately from the departments primarily responsible for performance to the Standards. PPL has in place a responsible behavior program that consists of systematic reminders along with coaching and counseling, which is intended to correct unacceptable behaviors. Importantly, PPL cultivates a culture of compliance by motivating its employees to identify possible compliance issues. PPL implements a process to encourage employees to identify possible compliance issues, which in turn enables PPL to both promptly mitigate these compliance issues and self-report possible violations of the Reliability Standards to ReliabilityFirst. ReliabilityFirst considered that PPL EU assumed responsibility for the maintenance and testing of the relays at issue and sought to determine ownership of all relays at its interconnection points. ReliabilityFirst also considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. PPL EU promptly reported the violation due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst seeks to encourage this type of behavior including self-reporting characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action, and assuming responsibility for the reliability of the registered entity’s interconnection points, by imposing a zero dollar penalty for this violation. A Settlement Agreement covering a violation of PRC-005-1 R2 for PPL EU was filed with FERC under NP10-71-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for PPL - Lower Mount Bethel Energy, LLC, PRC-005-1 R2 for PPL Montour, L.L.C., PRC-005-1 R2 for PPL Holtwood, L.L.C., PRC-005-1 R2; R2.1 PPL Brunner Island, L.L.C., and PRC-005-1 R2 PPL Martins Creek, L.L.C. was filed with FERC under NP13-23-000 on January 31, 2013. On March 1, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty, A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL - Lower Mount Bethel Energy, LLC, PRC-005-1 R2.1 for PPL - Lower Mount Bethel Energy, LLC, PRC-005-1 R2.1 for PPL Brunner Island, L.L.C, and PRC-005-1 R2.1 for PPL Montour, L.L.C was filed with FERC under NP11-74-000 on December 22, 2010. On January 21, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for PPL Montana, LLC was filed with FERC under NP10-57-000 on March 1, 2010. On March 31, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst determined that PPL EU' prior violation of PRC-005-1 R2 was an aggravating factor in the penalty determination. However, ReliabilityFirst determined that PPL EU’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation.
SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC2012011166 | Settlement Agreement | On September 28, 2012, PEC submitted a Self-Report to SERC stating that, as a Transmission Operator (TOP), it was in violation of VAR-001-1 R6 because it did not know the status of power system stabilizers (PSS) for four units. The four units were located at two fossil generating plants, Mayo and Smith Energy Complex (SEC). Mayo is a single-unit coal-fired plant. SEC has five combustion turbine (CT) units and two combined cycle power blocks. Each combined cycle is comprised of two CTs and one steam turbine (ST). The three SEC units included in PEC's Self-Report were CT9, CT10, and ST4. In fall of 2010, Power Generation Carolinas personnel conducted a value stream analysis session at PEC on VAR-002. During the analysis, the personnel mentioned that the Mayo Plant had a PSS, which at the time, was unknown by the TOP. With regard to the SEC CT9 and CT10, the communication to the TOP regarding the PSS status did not occur until after the units became commercially operable. On June 28, 2012, the SEC plant personnel notified the TOP function that the PSS was installed and enabled at SEC ST4. Prior to that date, the TOP was unaware of the status of the PSS. The unit had been in operation since June 2002. PEC began an investigation and determined that the PSS should not have been enabled. The TOP was notified at the time the PSS was disabled. There were a total of four out of 90 units (4.44%) on PEC’s system of which the TOP did not know the PSS status. PEC’s total generation is approximately 22,000 MW. The four units have a combined generation of about 1,328 MW, which equates to 6% of generation that was affected. | VAR-001-1 | R6 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the TOP did not know the status of the PSS for Mayo and SEC CT9 and CT10, the PSS were enabled, which was the correct state and therefore, the TOP would not have taken different actions had it known of the existence of the PSS. The risk was also mitigated because automatic voltage regulators (AVR) are not dependent on their associated PSS to function; the voltage was being measured and controlled to a set-point voltage through the AVRs' operation. Finally, at no time during the period of this violation was instability observed on the PEC transmission system as a result of the PSS on any of the units identified in this violation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 6/28/2012 (when the TOP was notified of the PSS status) | 0 | Self-Report | To mitigate this violation, PEC: 1) added PSS status indications to the Energy Management System (EMS), which allows the status of the PSS to be tracked with the AVR status indications; 2) updated the system operator reference manual with the active status of the PSS; 3) added a third selection to the VAR log tool, which reflects cases where the AVR status and PSS status are linked; and, 4) surveyed and compiled an inventory of all generating units that have a PSS, the status of each and the recommended status for each. To mitigate this violation, PEC will: 1) update the system operator reference manual and the PSS status indications in the EMS to be consistent with inventory results, as necessary; 2) develop a procedure for all future new generation integration checklists to include the requirement to continuously inform the TOP of changes in PSS status; 3) develop training materials and train applicable personnel on the new selection to the VAR log tool; and, 4) reissue directives to all non-owned generation units that direct each to operate in the appropriate mode. | 5/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed PEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC observed that at the time of the violation and self-reporting, PEC followed the documented ICP of its parent company, Progress Energy. The ICP, initially approved on December 13, 2007, was developed to formally document and drive existing compliance business practices. SERC also observed that PEC’s compliance program was disseminated to all organizations within PEC that must comply with NERC Standards. Progress Energy’s compliance program was prepared for and approved by Progress Energy’s Electric Reliability Organization (ERO) Steering Committee. The ERO Steering Committee was comprised of officers of PEC and Progress Energy Florida and was chaired by the ERO compliance officer, who is Progress Energy’s executive vice president – general counsel and corporate secretary. The ERO compliance officer was independent of all PEC organizations that must comply with NERC Standards. The ERO compliance officer reported directly to the chairman/president/CEO and had direct access to the Board of Directors. Company officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments. A Settlement Agreement covering violations of VAR-001-1 R6 for Progress Energy Florida (PEF), an affiliate of PEC, was filed with FERC under NP11-256-000 on August 11, 2011. On September 9, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that the prior violations should not serve as a basis for aggravating the penalty because the issues are not indicative of a holding company wide issue. This violation was processed as a spreadsheet notice of penalty with a $0.00 penalty as opposed to an FFT because the mitigating activities had not been completed.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP201100671 | Settlement Agreement | On August 26, 2011, LAFA, as a Distribution Provider, Generator Owner, and Transmission Owner, self-reported a violation of PRC-005-1 R1. LAFA reported that its Protection System maintenance and testing program (Program) did not include four communications devices associated with Protection System for four line segments of its transmission system. The 4 communications devices consisted of 1 microwave communication system, 1 wavetrap, and 2 mirrored bit communications devices. Since LAFA's Program did not address these four devices, LAFA was in violation of PRC-005-1 R1.1 for failing to include maintenance and testing intervals and their basis, and in violation of R1.2 for failing to include a summary of maintenance and testing procedures for the 4 communications devices. The 4 devices made up 25% (4 out of 16) of LAFA’s Protection System associated communication devices and represent less than 1% of LAFA’s total Protection System devices (4 out of 803). | PRC-005-1 | R1; R1.1; R1.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The four devices that were not included in LAFA's Program were continuously monitored by the LAFA system operators. All four of the communication devices were alarmed and monitored 24 hours a day and 365 days a year via the LAFA energy control system (ECS). Additionally, the size of LAFA, which has a peak load of 478 MW and 16 miles of transmission line at or above 100 kV, further reduced the risk to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 8/18/2011 (Mitigation Plan completion) | $34,000 (for SPP201100671, SPP201100672, SPP2011008214, and SPP2011008217) | Self-Report | LAFA performed the following actions to mitigate this violation: 1) modified its Program to ensure that all communications devices associated with Protection Systems are included in the Program; and 2) instituted routine maintenance and testing of all associated communications devices. | 2011-08-18 | 2012-03-26 | Neither Admits nor Denies | SPP RE reviewed LAFA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. LAFA implemented a formal ICP in early 2010, has worked to improve its ICP, and has employed consulting support since 2005 to create and implement its formal ICP. An internal compliance committee (ICC) consisting of LAFA employees as well as consultants was formed and meets quarterly to discuss compliance matters. In 2011, the Electric Reliability Department was formed for the purpose of handling compliance and reliability matters, and staffing has been increased. A SharePoint site was created to improve document and record management. Since 2010, LAFA conducts an annual self-assessment and mock audit to identify compliance issues. Also, senior management supports the compliance program. LAFA's director annually reviews and approves the ICP. A Settlement Agreement covering three violations, including a violation of PRC-005-1 R1 and PRC-005-1 R2 for LAFA (NOC-1631) was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE determined these two prior violations should serve as a basis for aggravating the penalty for the instant PRC-005-1 R1 (SPP201100671) and PRC-005-1 R2 (SPP201100672) violations.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP201100672 | Settlement Agreement | On August 26, 2011, LAFA, as a Distribution Provider, Generator Owner and Transmission Owner, self-reported a violation of PRC-005-1 R2, stating that it failed to test certain instrument transformers and DC control circuitry within the intervals set forth in its Protection System maintenance and testing program (Program). Specifically, there were 69 current transformers (14.8%) and 23 potential transformers (29.1%) at two generating plants (Labbe and Doc Bonin) that were out of the defined testing interval. Additionally, 10 DC control circuits (28.6%) across three facilities were out of defined testing intervals. LAFA had a total of 465 current transformers, 79 potential transformers and 35 DC circuits at these two facilities. These 102 devices at issue made up 12.7% of LAFA’s total inventory of Protection System devices (803 total devices). LAFA was in violation of PRC-005-1 R2.1 for failing to maintain and test all 102 of the devices within defined intervals, and was in violation of R2.2 for failing to document the date that 26 of the devices (18 instrument transformers and 8 DC control circuits) were last tested and maintained. | PRC-005-1 | R2; R2.1; R2.2 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For 76 out of the 102 devices at issue (74 instrument transformers and 2 DC circuits at the Labbe generating plant), the last testing was performed in April 2005. Therefore, the 74 instrument transformers were tested within the maximum allowable interval (seven years) provided in the NERC Protection System Maintenance A Technical Reference document dated September 13, 2007 (NERC Technical Reference) for unmonitored instrument transformers. The 2 DC circuits at the Labbe plant were approximately one year past the maximum allowable interval from the NERC Technical Reference, which is identical to the five-year interval provided by LAFA’s Protection System maintenance and testing program. Of the remaining 26 devices that were not tested in April 2005 and did not have a last testing date, 19 devices (18 instrument transformers and 1 DC circuit) were located at the Doc Bonin generating plant No. 1 facility, which has not been on-line since June 2009. The final seven devices were DC circuits at the Doc Bonin switchyard. LAFA reported that no misoperations occurred during the violation period at the Doc Bonin switchyard. Additionally, the size of LAFA, which has a peak load of 478 MW and 16 miles of transmission line at or above 100 kV, reduced the potential risk to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 6/1/2012 (Mitigation Plan completion) | $34,000 (for SPP201100671, SPP201100672, SPP2011008214, and SPP2011008217) | Self-Report | LAFA performed the following actions to mitigate this violation: 1) Performed testing of all the out-of-interval instrument transformers and DC circuitry; 2) Defined responsibilities within the organization to ensure that testing of DC circuitry and instrument transformers is performed pursuant to the intervals defined in LAFA's Program; and 3) Completed transmission upgrades concurrently with the performance of the Mitigation Plan. With the completion of these transmission upgrades in the Acadiana Load Pocket, LAFA now can schedule outages to perform the necessary testing to maintain compliance with PRC-005. | 2012-06-01 | 2012-06-14 | Neither Admits nor Denies | SPP RE reviewed LAFA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. LAFA implemented a formal ICP in early 2010, has worked to improve its ICP, and has employed consulting support since 2005 to create and implement its formal ICP. An internal compliance committee (ICC) consisting of LAFA employees as well as consultants was formed and meets quarterly to discuss compliance matters. In 2011, the Electric Reliability Department was formed for the purpose of handling compliance and reliability matters, and staffing has been increased. A SharePoint site was created to improve document and record management. Since 2010, LAFA conducts an annual self-assessment and mock audit to identify compliance issues. Also, senior management supports the compliance program. LAFA's director annually reviews and approves the ICP. A Settlement Agreement covering three violations, including a violation of PRC-005-1 R1 and PRC-005-1 R2 for LAFA was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE determined these two prior violations should serve as a basis for aggravating the penalty for the instant PRC-005-1 R1 (SPP201100671) and PRC-005-1 R2 (SPP201100672) violations.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2011008214 | Settlement Agreement | SPP RE conducted a Compliance Audit of LAFA from September 19, 2011 through September 22, 2011. The SPP RE Audit team determined that LAFA, as a Transmission Owner and Distribution Provider, was in violation of PRC-008-0 R2 for its failure to implement and document its underfrequency load shedding (UFLS) equipment maintenance and testing program. LAFA was unable to provide test results for 3 of its 26 UFLS relays (11.5%) and therefore, could not demonstrate testing within the five-year interval outlined in its UFLS testing program. | PRC-008-0 | R2 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, 23 out of the 26 UFLS relays at issue were tested within the interval set forth in LAFA’s UFLS testing procedure (five years with a one year grace period). This interval is significantly shorter than the maximum interval of 10 years set forth in the NERC Protection System Maintenance A Technical Reference for testing of microprocessor relays. All 26 of LAFA’s UFLS relays are multi-function microprocessor relays and are monitored by the LAFA energy control system (ECS). The relays have a self-test feature and would alarm the LAFA ECS should a relay fail a self-test. The ECS is also set to receive an alarm when one of the relays operates due to an underfrequency event. There were no underfrequency events during the period of the violation. Additionally, the size of LAFA, which has a peak load of 478 MW and 16 miles of transmission line at or above 100 kV, reduced the potential risk to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/15/2011 (Mitigation Plan completion) | $34,000 (for SPP201100671, SPP201100672, SPP2011008214, and SPP2011008217) | Compliance Audit | LAFA performed the following actions to mitigate this violation: 1) Performed UFLS testing on the three relays that were found to be out of compliance; 2) Reviewed and modified its internal procedures to include additional checks to ensure errors of this nature will not occur in the future; and 3) Revised its Transmission and Generation Maintenance and Testing Program document to specifically include a section for UFLS testing. Previously, the UFLS testing program was documented only in a separate procedure document. | 2011-12-15 | 2012-02-08 | Neither Admits nor Denies | SPP RE reviewed LAFA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. LAFA implemented a formal ICP in early 2010, has worked to improve its ICP and has employed consulting support since 2005 to create and implement its formal ICP. An internal compliance committee (ICC) consisting of LAFA employees as well as consultants was formed and meets quarterly to discuss compliance matters. In 2011, the Electric Reliability Department was formed for the purpose of handling compliance and reliability matters, and staffing has been increased. A SharePoint site was created to improve document and record management. Since 2010, LAFA conducts an annual self-assessment and mock audit to identify compliance issues. Also, senior management supports the compliance program. LAFA's director annually reviews and approves the ICP.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2011008217 | Settlement Agreement | SPP RE conducted a Compliance Audit of LAFA from September 19, 2011 through September 22, 2011. The SPP RE Audit team determined that LAFA, as a Transmission Operator, was in violation of TOP-004-2 R6.4 because LAFA did not have accurate alarms set for all of its transmission facilities pursuant to its formal transmission operations procedure (Procedure). LAFA’s Procedure did address how LAFA was to respond to Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs) violations. The relevant section of the Procedure stated, in part, that “energy control system (ECS) operators will monitor all [LAFA] transmission facilities for compliance with voltage and rating criteria,” and that “[f]facilities are alarmed for notification of frequency deviations, facility overloads, and voltages out of tolerance.” However, the Procedure did not provide any information regarding the process of setting the alarms and what the set points should be. Not all transmission facilities had alarms set, and those that were set had been done on an ad hoc basis. Therefore, SPP RE determined that LAFA failed to properly implement its Procedure as required by the Standard. | TOP-004-2 | R6; R6.4 | N/A | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because two 230 kV substation buses did not have alarms set. However, thermal limit alarms were set for all of LAFA’s 16 miles of 230 kV transmission lines at 91% of line rating or lower, meaning that the system operator would see the alarm in time to identify and respond to an impending SOL violation. Thermal alarms on the two 138/230 kV autotransformers owned by LAFA were set at 94% of the normal rating. Bus voltages at three 230 kV substations had high-side and low-side voltage alarms set at plus and minus 4% of nominal. A fourth 230 kV substation bus was also alarmed on the high-side but not on the low-side. LAFA’s experienced system operators would have been required to identify impending SOL violations for those 230 kV busses without the help of ECS system alarms. LAFA only operates at 138 kV at a single substation, where voltage alarms were set at plus or minus 5% of nominal. LAFA has a summer peaking load of 478 MW, and owns 16 miles of 230 kV and 28 miles of 69 kV transmission line. A small portion of LAFA's facilities operate at 138 kV, but LAFA owns no 138 kV transmission lines, which further reduced the risk to the BPS. Also, all 5 of LAFA’s NERC-certified operators are very experienced: 2 have 20 or more years of experience as a LAFA system operator, 2 have 10 or more years of experience, and 1 has four years of experience. The operator with 4 years of experience has over 17 years of additional power plant experience with LAFA. Notwithstanding the fact that not all alarms were set in accordance with LAFA’s policy, system voltages, transformer loadings, and transmission line loadings are monitored by the system operators on a 24-hour basis in real-time via the LAFA ECS. No facility ratings or SOLs were violated during the violation period. | 1/22/2009 (when LAFA's previous audit ended, and when Version 2 of the Standard became mandatory and enforceable) | 2/3/2012 (Mitigation Plan completion) | $34,000 (for SPP201100671, SPP201100672, SPP2011008214, and SPP2011008217) | Compliance Audit | LAFA performed the following actions to mitigate this violation: 1) Reviewed all SOLs to ensure that LAFA includes all appropriate thermal and voltage operating limits in its SOL methodologies; 2) Developed an appendix to the LAFA Policy, Guideline and Procedure (PGP) for TOP-004-2, outlining how LAFA's engineering and operations staff develops SOLs and implements ECS alarm levels; 3) Implemented the required changes to the ECS database; and 4) Provided training to system operators on the revised PGP, SOLs and ECS alarms. | 2012-02-03 | 2012-04-20 | Neither Admits nor Denies | SPP RE reviewed LAFA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. LAFA implemented a formal ICP in early 2010, has worked to improve its ICP and has employed consulting support since 2005 to create and implement its formal ICP. An internal compliance committee (ICC) consisting of LAFA employees as well as consultants was formed and meets quarterly to discuss compliance matters. In 2011, the Electric Reliability Department was formed for the purpose of handling compliance and reliability matters, and staffing has been increased. A SharePoint site was created to improve document and record management. Since 2010, LAFA conducts an annual self-assessment and mock audit to identify compliance issues. Also, senior management supports the compliance program. LAFA's director annually reviews and approves the ICP.
Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (Empire) | NCR01155 | SPP2012011134 | Settlement Agreement | On September 27, 2012, Empire submitted a Self-Report to SPP RE stating that, as a Balancing Authority (BA), Generator Operator, and Transmission Operator (TOP), it was in violation of COM-002-2 R1.1 because it did not notify its Reliability Coordinator (RC) and all other potentially affected BAs and TOPs of a condition that could threaten the reliability of its area. The threatening condition occurred when Empire's energy management system (EMS) became unresponsive for 40 minutes on March 8, 2012. Additionally, during its review, SPP RE determined that the EMS became unresponsive for fewer than 30 minutes on March 7, 2012, and again for fewer than 30 minutes on March 9, 2012 and on March 10, 2012. The EMS failures occurred following a programming change to the EMS which resulted in system failures. Empire corrected the underlying EMS programming issue on March 10, 2012. | COM-002-2 | R1; R1.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because although the loss of its EMS impaired the ability of system operators to monitor and control the system in real time, the Empire operators engaged Empire's backup EMS system to effectively mitigate the loss of its primary EMS. Additionally, during the shorter outages, when the backup EMS was not activated, system operators continued to receive tie-line data from Empire's neighbors, thereby providing Empire's system operators with partial situational awareness of power flows entering and leaving the Empire system. During the EMS outages, tie-line flows did not change significantly. Because the EMS outages were of short duration, and Empire's system status did not change significantly, neighboring BAs, TOPs, and the RCs were unaffected by the EMS failures. | 3/7/2012 (the first instance of EMS unresponsiveness during which Empire failed to notify its neighboring TOPs, BAs, or RC) | 3/10/2012 (the last instance of EMS unresponsiveness during which Empire failed to notify its neighboring TOPs, BAs, or RC) | 3500 | Self-Report | To mitigate this violation, Empire conducted a training session with its operations staff and reiterated the importance of immediately notifying the RC, TOPs, and BAs following an EMS failure. | 2012-11-19 | 2013-02-20 | Neither Admits nor Denies | SPP RE reviewed Empire's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Empire maintains a documented ICP. A reliability compliance department (RCD), a manager of reliability compliance, and a reliability compliance team (RCT) are identified in the ICP. The RCD is responsible for developing and maintaining policies and procedures that are compliant with the NERC Reliability Standards. The manager of reliability compliance oversees the RCD, coordinates and facilitates personnel compliance training and meetings, and coordinates internal compliance assessments with the RCT. Members of the RCT include key department managers, directors, and personnel who manage areas that are vital to ensuring company compliance with the Reliability Standards.
Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2012011229 | Settlement Agreement | On October 12, 2012, AZPS submitted a Self-Report to WECC stating, that as Generator Operator (GOP), it was in violation of VAR-002-1.1b because it failed to notify its Transmission Operator (TOP) within 30 minutes of the status change for a Power System Stabilizer (PSS). On September 2, 2012 at 18:18, a generation operations technician was in the process of bringing the steam turbine (ST) for combined cycle unit #4 (CC4) online. Upon closing the breaker for the CC4 ST, alarms were received on the Continuous Environmental Monitoring System (CEMS) for CC4. As the startup continued, the shift supervisor assisted the operations technician in identifying and correcting the cause of the CEMS alarms. At 18:31, CC4’s power level was sufficient for bringing the PSS online. However, AZPS reported that the PSS did not come online as expected. AZPS reported that the operations technician detected the PSS was offline at 19:38 but was unable to confirm the status at that time. AZPS reported that it was late in confirming the status change of the PSS due to the concurrent environmental alarms, its efforts to clear the alarms, and a failure of an alarm to sound indicating that the PSS was offline. AZPS reported that it did not confirm the PSS was not online until after the CEMS alarms were cleared and the shift supervisor asked the operations technician to report the status of the PSS. After a visual scan of the control board by the operations technician, the operations technician confirmed that the PSS was still offline at 20:27. Subsequent to the confirmation and nearly two hours after a status change of the PSS, the operations technician informed its TOP, AZPS Energy Control Center (ECC), of the status change for the PSS. The PSS was brought online at 23:06 that same day. AZPS, after learning that the PSS alarm was not functioning on CC4, conducted a thorough investigation to identify additional times when the PSS may have been off and not alarmed. Through this investigation, AZPS discovered that on June 3, 2012, when the Operations Technician was bringing CC4 online, the PSS should have come on at 13:31 but failed to do so. The Technician recognized the problem, and the PSS was brought on line at 13:59. AZPS further reported that the operations technician did not report the incident to its TOP, ECC, because the technician mistakenly believed that since he had brought the PSS on line within 30 minutes, he did not have to report the incident as required by VAR-002-1.1b R3.1. | VAR-002-1.1b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risks posed by AZPS's noncompliance were limited by compensating measures in place during the violation period. The PSS involved in the incident is associated with a combined cycle generator that is rated at less than 25 MW. The CC4 unit involved in the incident had comparably conservative outputs of 22 MW in June and 19 MW in September. All other generation resources on its system (26 generators in June and 22 in September) were equipped with functioning PSSs and system loads of 4,485 and 3,980 MWs, respectively. Additionally, after discovering the PSS was not online, AZPS’s employees worked quickly to place the PSS online in an expedited fashion, limiting the duration of the violation. | 6/3/2012 (when AZPS should have reported to its TOP that the PSS for CC4 was offline) | 9/2/2012 (when AZPS reported to its TOP that the PSS for CC4 was offline) | 20000 | Self-Report | To mitigate this violation, AZPS: 1) held a video conference with senior plant managers of all fossil generating plants to review what happened, the proposed mitigation plans, and why previous actions were not effective; 2) informed all plant and operations managers of the September 2, 2012 event and required a review of the lessons learned to be conducted with all operators and shift supervisors; 3) had Information Technology (IT) engineering complete a review of all alarms in the new control system and added the PSS Out of Service (OOS) alarm. This alarm has been tested and verified to be operational; 4) completed a root cause evaluation and identified potential shortcoming in the guidelines for the Human Machine Interface (HMI) change out. This evaluation also identified potential shortcomings in the verification process when programming alarms in the replaced HMI; 5) generated a corrective action request to research the current process and determine if any changes or controls are necessary; 6) conducted documented coaching and disciplinary actions as necessary, in accordance with AZPS’s Internal Compliance Program (ICP); 7) informed Palo Verde Nuclear Generating Station of this event and reinforced, with its control room personnel, the importance of understanding their indications and reporting requirements for their generators. | 2012-10-12 | 2012-12-03 | Neither Admits nor Denies | WECC reviewed AZPS's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AZPS's ICP is documented, disseminated throughout its operations staff, and includes ICP oversight staff supervised at a high level in the organization with independent access to the CEO and/or board of directors. AZPS operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards. AZPS has allocated sufficient resources to its ICP while allotting it the support and participation of senior management. AZPS reviews and modifies its ICP regularly. AZPS's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis. AZPS's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. This was AZPS's third violation of VAR-002-1.1 b R3. The first violation occurred on October 9, 2011. In that case, WECC determined that AZPS failed to notify its TOP of a PSS change of status. Consequently, AZPS's TOP was not notified of the Palo Verde Nuclear Generating Station Unit 3 PSS change in status until twenty-four hours later. The second violation occurred on June 30, 2012. In that instance, WECC determined that AZPS failed to notify its TOP of a PSS change of status. AZPS's TOP was unaware of the status change for 102 minutes. In this case, AZPS failed, in two instances, to notify its TOP of a PSS status change as required by VAR-002-1.1 b R3. WECC considered the two previous violations to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | City of Tacoma, Department of Public Utilities, Light Division (TPWR) | NCR05097 | WECC201103024 | Settlement Agreement | On October 3, 2011, TPWR, submitted a Self-Report to WECC stating that, as a Balancing Authority, it was in violation of BAL-005-0.1b R15. because it failed to have reliable backup power supplies and to test these supplies periodically to ensure continuous operation of its Automatic Generation Control (AGC) and vital data recording equipment during loss of the normal power supply. On July 1, 2011, TPWR experienced a loss of station service power to its energy control center (ECC) when the station service breaker servicing the ECC opened and the automatic transfer switch (ATS) did not automatically transfer the electrical load to the emergency generator. TPWR's generator was isolated, and the emergency control center relied on its uninterruptable power supply (UPS) to carry the essential load. However, the UPS was depleted within fourteen minutes, causing a complete power outage to essential load. | BAL-005-0.1b | R15 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because AGC and data recording equipment are vital for the reliable operation of the BPS. TPWR had a full outage that caused it to fail to have continuous power supplies for its AGC and data recording. As a compensating measure, TPWR had in place adequate telecommunications facilities located at its backup control center to ensure that system events and conditions are adequately communicated. Further, TPWR maintained system control during the outage and maintained full system and local awareness. | 1/20/2010 (when TPWR established its backup control center at a remote substation) | 10/06/2011 (Mitigation Plan completion) | $13,200 (for WECC201103024 and WECC201102854) | Self-Report | To mitigate this violation, TPWR: 1) replaced its UPS battery; 2) replaced the ECC's station service breaker and the damaged UPS control circuit board; 3) wrote a procedure for emergency bypass of the ECC ATS; 4) created a preventative maintenance work order for ATS circuit breakers; 5) conducted periodic testing of its UPS; and, 6) wrote a test procedure and testing schedule for the backup control center's emergency power system. | 2011-10-06 | 2012-05-07 | Agrees/ Stipulates | WECC reviewed TPWR's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that TPWR's ICP is documented; the ICP is disseminated throughout its operations staff. TPWR has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; TPWR operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; TPWR has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; TPWR reviews and modifies its ICP regularly; TPWR's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and TPWR's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | City of Tacoma, Department of Public Utilities, Light Division (TPWR) | NCR05097 | WECC201102854 | Settlement Agreement | On June 17, 2011, TPWR, submitted a Self-Report to WECC stating that, as a Balancing Authority (BA), it was in violation of BAL-005-0 R12.1 because it failed to ensure that its telemetry emanated from the common metering equipment agreed upon with the Bonneville Power Administration (BPA). On April 20, 2011 TPWR and BPA performed an Automatic Generation Control (AGC) interchange MW metering common source verification test for a BPA-owned meter at TPWR's Mossyrock Switchyard. During the test, when currents were removed from the meter, the BPA dispatcher observed the corresponding change in BPA's meter signal, but TPWR did not observe a change in TPWR's signal. After investigating, TPWR and BPA discovered that TPWR was receiving its signal from a separate transducer at Mossyrock Switchyard, not the BPA meter. Therefore, TPWR concluded that the two meters were improperly configured. | BAL-005-0 | R12 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BPA did not report any noticeable differences between its integrated megawatts and megawatt hour values during the duration of the violation. Additionally, the entities meter testing procedures would have helped to detect any potential overloads and would have alerted the entities of any large potential fluctuations. | 5/5/2008 (when TPWR failed to ensure that its telemetry emanated from the common metering equipment agreed upon with BPA) | 4/21/2011 (when the meters were reconfigured to comply with the Standard) | $13,200 (for WECC201103024 and WECC201102854) | Self-Report | To mitigate this violation, TPWR: 1) reviewed and updated its procedures for conducting metering tests; 2) reviewed interchange test records and/or other documentation for pseudo-ties with other entities and updated documentation as necessary; 3) provided training to process owners and stakeholders on any revisions to procedures; 4) corrected any new related issues discovered at TPWR tie-lines or pseudo-ties, retested and updated documentation; and 5) communicated the importance of coordinating with neighboring BAs to its employees. | 2011-11-14 | 2012-05-11 | Agrees/ Stipulates | WECC reviewed TPWR's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that TPWR's ICP is documented; the ICP is disseminated throughout its operations staff. TPWR has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; TPWR operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; TPWR has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; TPWR reviews and modifies its ICP regularly; TPWR's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and TPWR's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2012011538 | Settlement Agreement | On December 14, 2012, CHPD submitted a Self-Report to WECC stating that, as a Distribution Provider, Generator Owner, and Transmission Owner, it was in violation of PRC-005-1 R2 because it failed to provide evidence that certain Protection System devices were maintained and tested within the defined intervals. CHPD's Protection System maintenance and testing program required 3-year interval testing for electromechanical relays and 5-year testing intervals for solid-state or microprocessor relays, with a one-year grace period for work scheduling. CHPD's current and voltage sensing devices and DC circuitry were to be tested at the same time as its relays. CHPD failed to test the Protection System devices due to improper classification leading to improper maintenance and testing intervals. The misclassification affected 8 out of 511 relays, 17 out of 586 current and voltage sensing devices, 2 out of 65 communication channels, and 7 out of 241 DC control circuits. A total of 34 out of 1,425 (2.4%) Protection System devices were not maintained or tested within the defined intervals. The remaining 22 devices were batteries that were tested and maintained within the defined interval and not included in the violation. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Testing was performed in the prior interval for all the devices in question. All protective circuits were backed up by a breaker failure protection and backup generator and line protection. Additionally, visual inspections were performed in accordance with the testing procedures. CHPD had an established maintenance and testing program which required testing at frequent intervals and was device specific. Under this approach, CHPD tested devices based on their importance to the reliability of the BPS, ensuring that testing was performed based on device importance and function. Additionally, CHPD maintains all maintenance and testing intervals in an electronic database. Furthermore, upon discovering that devices were not tested, CHPD reviewed all of its Protection System devices to ensure they had been tested and maintained. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/7/2012 (Mitigation Plan completion) | 10000 | Self-Report | To mitigate this violation, CHPD: 1) performed maintenance and testing on all devices that were not tested during the defined intervals; 2) updated its Protection System maintenance and testing program to correct the interval basis for the devices referenced; and 3) developed a new work management report to show the required compliance activities that are due in the next 90 days. | 2012-12-07 | 2013-04-01 | Does Not Contest | WECC reviewed CHPD's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that CHPD has a comprehensive, established, and documented ICP. The ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as the Standards change. It includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis. CHPD has identified and assigned responsibility and accountability to a compliance officer and has one position fully dedicated to FERC/NERC compliance. CHPD's compliance official has dedicated, adequate resources to support its ICP, and the ICP has the support and participation of senior management. CHPD's ICP includes measurable, specific compliance performance targets. CHPD distributes the ICP to all employees and, if applicable, contractors and vendors. CHPD has fully implemented its program which includes procedures for disciplinary action for employees involved in violations of the Reliability Standards. The ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis. It includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC. CHPS regularly reviews its ICP at least annually and it includes a process to prevent recurrence of NERC Reliability Standard violations. CHPD also participates in outreach compliance program activities.
Western Electricity Coordinating Council (WECC) | South Feather Power Project (SFPP) | NCR11054 | WECC2012010838 | Settlement Agreement | On August 2, 2012, SFPP submitted a Self-Report to WECC stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R1 because: (1) it did not have a Protection System maintenance and testing program for each component of its Protection Systems; and (2) it used the standards and guidelines created by another entity. SFPP stated that it contracted to sell all of its power through a Power Purchase Contract (PPC) to a Transmission Owner (TO). In compliance with the PPC, SFPP adopted a policy that incorporated the Protection System maintenance and testing procedures created by the contracting TO. While reviewing SFPP's Self-Certification associated with a violation of PRC-005-1 R2, WECC discovered that SFPP was applying the Protection System maintenance and testing program procedures of its contracting TO to its station battery systems and did not have its own Protection System maintenance and testing program. However, WECC later determined that SFPP had a Protection System maintenance and testing program that included intervals and a summary of procedures, but SFPP did not have a basis for the intervals. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). Although SFPP failed to have its own maintenance and testing program for its Protection Systems, it had a written policy statement concerning Protection System maintenance and testing. The policy required it to abide by the standards for routine testing of protective devices developed by the TO, and SFPP followed the guidelines found in this policy during the violation period. Specifically, SFPP conducted periodic maintenance and testing of its protection system devices in accordance with the guidelines developed by the TO. Further, SFPP maintained and tested its relays and voltage and current sensing devices in accordance with the defined intervals outlined in the contracting TO's procedures. Finally, the issue was limited to quarterly battery testing. | 7/17/2009 (when SFPP registered as a GO) | 8/27/2012 (Mitigation Plan completion) | $7,000 (for WECC2012010838 and WECC2012010725) | Self-Report | To mitigate this violation, SFPP: 1) formalized its Protection System maintenance and testing program, including information about the protective devices covered under the program, their maintenance and testing intervals and their basis, and a summary of the maintenance and testing procedures; and 2) updated the Protection System maintenance and testing program to provide documentation that protection system devices were maintained and tested at the appropriate intervals. | 2012-08-27 | 2012-09-05 | Neither Admits nor Denies | WECC reviewed SFPP's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that SFPP had an established, and documented program. SFPP's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change. The ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis. SFPP has identified and assigned responsibility and accountability to a compliance officer or other high ranking official. SFPP has at least one position partially dedicated to FERC/NERC compliance. SFPP's compliance official has independent access to the CEO or equivalent. SFPP's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. SFPP has dedicated adequate resources to support its ICP. SFPP's ICP has the support and participation of senior management. SFPP's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC. SFPP participates in outreach compliance program activities.
Western Electricity Coordinating Council (WECC) | South Feather Power Project (SFPP) | NCR11054 | WECC2012010725 | Settlement Agreement | On July 19, 2012, SFPP submitted a Self-Certification to WECC stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2 because it failed to record battery cell voltages at its Forbestown Powerhouse during the period of January 1, 2011 through March 31, 2011. The Forbestown Powerhouse was shut down and cleared for replacement of the turbine shut-off valve and its control system from January 16, 2011 to March 16, 2011. This work caused an oversight on the required quarterly battery test. SFPP had been conducting a quarterly inspection of the Forbestown Powerhouse station batteries, which required the individual cell voltages to be recorded, in accordance with the Protection System maintenance and testing program of its contracting Transmission Owner (TO). WECC determined that SFPP had been conducting maintenance and testing pursuant to intervals defined in the Protection System maintenance and testing program of its contracting TO, but failed to provide evidence that 60 out of 180 (33.3%) battery cells were maintained and tested within defined intervals. The quarterly battery cell voltage readings were taken and recorded during the first 30 days of the month immediately following the quarters in which they were missed. | PRC-005-1 | R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SFPP failed to provide evidence that it had conducted quarterly battery cell inspections for one quarter, it conducted daily checks and recorded logs of the battery voltages during that time. Additionally, although no individual cell voltage readings were recorded during the first quarter, the operator still inspected the batteries. | 4/1/2011 (the first day after the end of the quarter) | 4/11/2011 (when the missed batteries were tested) | $7,000 (for WECC2012010838 and WECC2012010725) | Self-Certification | To mitigate this violation, SFPP: 1) tested the missed batteries that were not tested within the defined interval; and 2) established reminders for the Operations Supervisor at the middle of the second month of each quarter to complete the quarterly cell voltage records. | 2012-04-25 | 2012-08-08 | Neither Admits nor Denies | WECC reviewed SFPP's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that SFPP had an established, and documented program. SFPP's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change. The ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis. SFPP has identified and assigned responsibility and accountability to a compliance officer or other high ranking official. SFPP has at least one position partially dedicated to FERC/NERC compliance. SFPP's compliance official has independent access to the CEO or equivalent. SFPP's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. SFPP has dedicated adequate resources to support its ICP. SFPP's ICP has the support and participation of senior management. SFPP's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC. SFPP participates in outreach compliance program activities.