## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
ReliabilityFirst Corporation (ReliabilityFirst) | Dearborn Industrial Generation, L.L.C. (Dearborn) | NCR00751 | RFC2012010627 | Settlement Agreement | On June 19, 2012, Dearborn submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it was in violation of PRC-005-1 R1 because it incorrectly applied the basis to the intervals for its station batteries and direct current control circuitry. For these devices, Dearborn utilized NERC’s publication, Protection System Maintenance: A Technical Reference (NERC Guidelines), to establish the intervals. For unmonitored station batteries, the NERC Guidelines recommend a monthly interval, and Dearborn implemented a five-year interval. For fully monitored voltage and current sensing devices and direct current control circuitry, the NERC Guidelines recommend continuous monitoring and verification. Dearborn, however, implemented a five-year maintenance and testing interval. Dearborn’s maintenance and testing intervals for station batteries, direct current control circuitry, and voltage and current sensing devices were unsupported by a basis because Dearborn incorrectly applied the NERC Guidelines. | PRC-005-1 | R1; R1.1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because the station battery systems have local alarms and voltage and current meters, which Dearborn monitors daily during operator rounds. Dearborn has performed testing annually on the batteries since 2007, and monthly testing on the batteries from March 2011 to the present. In addition, Dearborn has performed maintenance on all voltage and current sensing devices, and testing on all of the monitored voltage and current sensing devices in 2011. Of the two unmonitored voltage and current sensing devices, Dearborn performed testing on one in 2011. Twice a year when there is a planned outage on the facility, Dearborn performs initiated trip tests to verify breaker trip paths. Dearborn also visually inspected the fully monitored direct current control circuits in 2008. In addition, Dearborn checks the partially monitored direct current control circuits twice a day. If a status light is not lit, then the operator writes a work order to initiate investigation and remediation of the issue. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $0 (for RFC2012010627 and RFC2012010628) | Self-Report | To mitigate this violation, Dearborn will revise its Protection System maintenance and testing program to include all required intervals and bases for those intervals. | TBD | TBD | Admits | ReliabilityFirst reviewed Dearborn’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered certain aspects of Dearborn’s ICP as mitigating factors. Dearborn participates in the corporate ICP of CMS Energy Corporation, its parent company. The ICP is well-documented and distributed throughout the company, and employees participate in yearly training on topics related to compliance. The regulatory ICP utilizes the Treadway Commission’s Committee of Sponsoring Organizations principles of control environment, risk assessment, information and communication, control activities, and monitoring. The chief compliance officer oversees the CMS enterprises compliance review committee, demonstrating senior management’s active role in compliance. The CMS Enterprises compliance review committee monitors policies, procedures, implementation, and execution of the enterprises’ regulatory compliance, including NERC compliance. ReliabilityFirst considered that it discovered the violations through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the bulk power system depends on robust and timely self-reporting by registered entities. Dearborn promptly reported the violation at issue due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst seeks to encourage this type of behavior including self-reporting characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action by imposing a zero dollar penalty for this violation. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. This is Dearborn’s first violation of PRC-005-1 R1. A Settlement Agreement covering violations of PRC-005-1 R1 for Craven County Wood Energy, LP, a Dearborn affiliate, was filed with FERC under NP08-27-000 on June 5, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R1 and PRC-005-1 R2 for T.E.S. Filer City Station Limited Partnership, a Dearborn affiliate, was filed with FERC under NP11-214-000 on June 29, 2011. On July 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although ReliabilityFirst considered Dearborn’s violation history as an aggravating factor, ReliabilityFirst determined that Dearborn’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the penalty aggravation.
ReliabilityFirst Corporation (ReliabilityFirst) | Dearborn Industrial Generation, L.L.C. (Dearborn) | NCR00751 | RFC2012010628 | Settlement Agreement | On June 19, 2012, Dearborn submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it was in violation of PRC-005-1 R1 because it failed to provide documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in R2. Dearborn discovered that it was unable to locate documentation for testing of 3 of its 30 (10%) protective relays within the five-year interval. In addition, Dearborn discovered that it failed to perform maintenance and testing on 4 of its 42 (9.5%) direct current control circuits within the five-year interval. | PRC-005-1 | R2; R2.1 | High | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because while Dearborn’s maintenance and testing interval for relays is five years, Dearborn performed testing of all of its protective relays except the three at issue in the violation in 2007, 2008, and 2009 and performed maintenance on these relays in 2007 and 2008. Twice a year when there is a planned outage on the facility, Dearborn performs initiated trip tests to verify breaker trip paths, and Dearborn visually inspected the fully monitored direct current control circuits in 2008. In addition, Dearborn checks the partially monitored direct current control circuits twice a day during regular rounds. If a status light is not lit, then the operator writes a work order to initiate investigation and remediation of the issue. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/15/2013 (Mitigation Plan Completion) | $0 (for RFC2012010627 and RFC2012010628) | Self-Report | To mitigate this violation, Dearborn performed maintenance and testing on the Protection System devices at issue. | 2013-05-15 | TBD | Admits | ReliabilityFirst reviewed Dearborn’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered certain aspects of Dearborn’s ICP as mitigating factors. Dearborn participates in the corporate ICP of CMS Energy Corporation, its parent company. The ICP is well-documented and distributed throughout the company, and employees participate in yearly training on topics related to compliance. The regulatory ICP utilizes the Treadway Commission’s Committee of Sponsoring Organizations principles of control environment, risk assessment, information and communication, control activities, and monitoring. The chief compliance officer oversees the CMS enterprises compliance review committee, demonstrating senior management’s active role in compliance. The CMS Enterprises compliance review committee monitors policies, procedures, implementation, and execution of the enterprises’ regulatory compliance, including NERC compliance. ReliabilityFirst considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the bulk power system depends on robust and timely self-reporting by registered entities. Dearborn promptly reported the violation at issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst seeks to encourage this type of behavior including self-reporting characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action by imposing a zero dollar penalty for this violation. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. This is Dearborn’s first violation of PRC-005-1 R2. A Settlement Agreement covering violations of PRC-005-1 for Craven County Wood Energy, LP, a Dearborn affiliate, was filed with FERC under NP08-27-000 on June 5, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R1 and PRC-005-1 R2 for T.E.S. Filer City Station Limited Partnership, a Dearborn affiliate, was filed with FERC under NP11-214-000 on June 29, 2011. On July 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although ReliabilityFirst considered Dearborn’s violation history as an aggravating factor, ReliabilityFirst determined that Dearborn’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the penalty aggravation.
ReliabilityFirst Corporation (ReliabilityFirst) | Jersey Central Power & Light Company (Jersey Central) | NCR00806 | RFC2011001109 | Settlement Agreement | On August 31, 2011, Jersey Central submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2.1. Jersey Central stated that it had not performed quarterly battery maintenance and testing for one battery installation at its Yards Creek Generating station from April 2011 through June 2011. Further, as a Transmission Owner (TO) and Distribution Provider (DP), Jersey Central reported that it could not locate documentation demonstrating it performed scheduled maintenance and testing within its defined interval for two relay schemes, consisting of five Protection System devices, at its West Wharton substation. Additionally, during a Compliance Audit conducted from October 4, 2011, through October 7, 2011, ReliabilityFirst determined that Jersey Central, GO, TO, and DP, was in violation of PRC-005-1 R2. Jersey Central could not provide evidence demonstrating that it conducted maintenance and testing on its current transformers (CTs) and voltage transformers (PTs) or DC control circuitry. Specifically, Jersey Central stated that it tested its CTs and PTs at the time it calibrated its relays, however Jersey Central did not document its test results. ReliabilityFirst also could not verify that Jersey Central tested its DC control circuitry as it only provided dates of functional tests, not the test results. Jersey Central has 4,760 Protection System devices on its system consisting of 2,550 relays, 400 associated communication systems, 830 CTs and PTs, 150 station batteries, and 830 DC control circuits. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Jersey Central represents that it conducted testing of its CTs and PTs during relay calibration but neglected to document the test results. Further, Jersey Central represents it conducted functional tests on its DC control circuitry and provided ReliabilityFirst with a list of the dates on which it represents it performed the functional tests. Additionally, while Jersey Central missed quarterly testing of batteries at its Yards Creek Generating station, it did perform monthly battery testing pursuant to its Protection System maintenance and testing program. Finally, upon testing of the batteries two months after its quarterly interval, Jersey Central determined the batteries had no performance issues during the duration of the violation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 8/5/2011 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Report | To mitigate this violation, Jersey Central performed and documented the test results of maintenance and testing of the Protection Systems devices that had not been documented or tested within their defined interval. | 2011-08-05 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed Jersey Central's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Jersey Central's internal compliance program (ICP) is overseen by its parent company, FirstEnergy, and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several of the violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Ohio Edison Company (Ohio Edison) | NCR00856 | RFC2011001126 | Settlement Agreement | On September 30, 2011, Ohio Edison submitted a Self-Certification to ReliabilityFirst stating that, as a Distribution Provider, it was in violation of PRC-005-1 R2. Ohio Edison self-certified that it identified four relay schemes associated with the Gates Ohio Edison Distribution substation for which it could not locate documentation demonstrating that it completed maintenance and testing within the five-year and six-month interval listed in its Protection System maintenance and testing program. Ohio Edison has 8,900 Protection System devices consisting of 5,100 relays, 250 associated communication systems, 1,700 current transformers (CTs) and potential transformers (PTs), 150 station batteries, and 1,700 DC control circuits. Specifically, Ohio Edison could not locate documentation demonstrating it completed maintenance and testing on four of the 5,100 (0.08%) relay schemes at issue between 2005 and September 30, 2010. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the short duration of this violation and the small number of affected devices. Ohio Edison performed maintenance and testing on the four relay schemes at issue 20 days outside of its required interval. Upon performing maintenance and testing, Ohio Edison determined the relay schemes at issue would have performed appropriately during the duration of the violation. | 9/10/2010 (when Ohio Edison should have performed maintenance and testing) | 9/30/2010 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, Ohio Edison performed and documented the test results of maintenance and testing of the Protection Systems devices that had not been documented or tested within their defined interval. | 2010-09-30 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed Ohio Edison's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Ohio Edison's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ ICP. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Toledo Edison Company, The (Toledo Edison) | NCR00930 | RFC2011001127 | Settlement Agreement | On September 30, 2011, Toledo Edison submitted a Self-Certification to ReliabilityFirst stating that as a Distribution Provider, it was in violation of PRC-005-1 R2. In its Self-Certification, Toledo Edison stated that it could not locate documentation demonstrating completion of four breaker functional tests within the interval listed in its Protection System maintenance and testing program between June 2004 and June 2009. However, registered entities are not required to produce records of maintenance and testing activities conducted prior to June 18, 2007. Therefore, ReliabilityFirst determined no violation exists for the four breaker functional tests Toledo Edison included in its Self-Certification. Toledo Edison identified one instance where it performed a DC control circuit functional test on November 11, 2003, and subsequently performed the functional test on August 2, 2010, thereby exceeding the six-year and six-month interval. Toledo Edison has 3,290 Protection System devices consisting of 1,770 relays, 250 associated communication systems, 590 current transformers (CTs) and potential transformers (PTs), 90 station batteries, and 590 DC control circuits. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated by the small number of affected devices and that upon testing, Toledo Edison found the DC control circuit at issue to be intact, functional, and in proper working order. Therefore, the DC control circuit would have functioned properly during the duration of the violation | 5/11/2010 (when Toledo Edison should have performed the DC control circuit functional test at issue) | 8/2/2010 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, Toledo Edison performed and documented the test results of maintenance and testing of the Protection Systems devices that had not been documented or tested within their defined interval. | 2010-08-02 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed Toledo Edison's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Toledo Edison's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation Corp. (FE Genco) | NCR00782 | RFC2011001128 | Settlement Agreement | On September 30, 2011, FE Genco submitted a Self-Certification to ReliabilityFirst stating that, as a Generator Owner, it was in violation of PRC-005-1 R2.1. FE Genco reported that on four instances at its Bay Shore generating station, it performed maintenance and testing on two Protection System battery units outside the defined intervals of its Protection System maintenance and testing program. FE Genco has 785 Protection System devices consisting of 670 relays, 0 associated communication systems, 35 current transformers (CTs) and potential transformers (PTs), 45 station batteries, and 35 DC control circuits. Specifically, FE Genco did not perform impedance testing within its two-year interval on two battery units and did not perform bi-monthly testing, which consisted of checking battery water levels and taking samples, on two battery units. Additionally, on March 21, 2012, FE Genco discovered that in one instance, it did not perform impedance testing on seven battery units at its Mansfield generating station. FE Genco should have completed impedance testing on the two units by February 28, 2010 and May 31, 2010, respectively, and should have completed bi-monthly testing by March 31, 2011 and May 31, 2011, respectively. FE Genco completed all maintenance and testing on the two batteries at its Bay Shore generating station on September 29, 2011. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the fact that, as it concerns the units at issue in the missed bi-monthly battery tests, FE Genco performed all required monthly battery maintenance and testing as required by its Protective System maintenance and testing program. FE Genco had no performance issues with the battery units at issue during the duration of the violation. Additionally, upon completion of maintenance and testing of the units at issue, FE Genco determined each unit was in proper working order throughout the duration of the violation. | 2/28/2010 (the date by which FE Genco should have completed impedance testing on one of its units) | 4/27/2012 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, FE Genco performed and documented the test results of maintenance and testing of the Protection Systems devices that had not been documented or tested within their defined interval. | 2012-04-27 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed FE Genco's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FE Genco's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | American Transmission Systems, Incorporated (ATSI) | NCR00686 | RFC2011001129 | Settlement Agreement | On September 30, 2011, ATSI submitted a Self-Certification to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2.1. ATSI self-certified that it could not demonstrate that it performed maintenance and testing on 12 relay schemes, consisting of 96 Protection System devices, and could not locate documentation demonstrating it performed 66 breaker functional tests within the five-year and six-month interval listed in its Protection System maintenance and testing program. ATSI has 17,780 Protection System devices consisting of 9,870 relays, 1,010 associated communication systems, 3,290 current transformers (CTs) and potential transformers (PTs), 320 station batteries, and 3,290 DC control circuits. In 44 instances involving 6 relay schemes and 38 breaker functional tests, ATSI could not locate documentation demonstrating it completed maintenance and testing within its defined interval from September 2004 to September 2009. Additionally, in six instances involving the six remaining relay schemes, ATSI could not locate documentation demonstrating it completed maintenance and testing from March 2004 to 2010. ATSI performed testing on the six relay schemes at issue between April 2010 and September 2010. In the remaining 28 instances involving breaker functional tests, ATSI did not properly schedule maintenance and testing, which resulted in ATSI scheduling or performing maintenance and testing outside the defined interval. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because in addition to the lack of documentation, ATSI also did not schedule maintenance and testing of Protection System devices within its the defined interval. The incidents involving missing maintenance and testing records are a documentation issue. ATSI performed the maintenance and testing, but believes the maintenance and testing records at issue were lost during its transition from a paper based legacy work management process to its current digital process. Additionally, ATSI completed all breaker functional tests between August 27, 2010 and December 31, 2012, which revealed all equipment was in proper working order throughout the duration of the violation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/31/2012 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, ATSI performed and documented the test results of maintenance and testing of the Protection Systems devices that had not been documented or tested within their defined interval. | 2012-12-31 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed ATSI's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ATSI's internal compliance program ICP is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Monongahela Power Company (Monongahela) | NCR10200 | RFC2011001130 | Settlement Agreement | On September 30, 2011, submitted a Self-Certification to ReliabilityFirst stating that, as a Generator Owner, it was in violation of PRC-005-1 R1. Monongahela stated that it did not include current transformers (CTs) and potential transformers (PTs) in its Protection System maintenance and testing program. | PRC-005-1 | R1 | High | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because Monongahela did not fulfill its responsibility to update its Protection System maintenance and testing program in a timely manner to include CTs and PTs. The risk posed by the foregoing facts and circumstances was mitigated by the fact that at the time of installation, Monongahela verified the output and accuracy of its CTs and PTs. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/9/2011 (when Monongahela included maintenance and testing intervals and their basis as well as a summary of maintenance and testing procedures for CTs and PTs in its Protection system maintenance and testing program) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, Monongahela included CTs and PTs and the basis for its three-year Protection System relay and DC control circuits maintenance and testing intervals in its Protection System maintenance and testing program. To mitigate this violation, Monongahela will complete maintenance and testing on all CTs and PTs and perform maintenance and testing in conjunction with planned scheduled generating unit outages. | 12/31/2014 (approved completion date) | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed Monongahela's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Monongahela's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several the violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) | NCR02600 | RFC2011001131 | Settlement Agreement | During a Compliance Audit conducted from September 12, 2011 to October 3, 2011, ReliabilityFirst determined that AE Supply, as a Generator Owner, was in violation of PRC-005-1 R1. AE Supply did not address all required Protection System devices and did not include an acceptable basis for Protection System relays and DC control circuitry in its Protection System maintenance and testing program. Specifically, AE Supply did not include current transformers (CTs) and potential transformers (PTs) within its Protection System maintenance and testing program. Additionally, in its Protection System maintenance and testing program AE Supply stated that the maintenance and testing interval for Protection System relays and DC control circuitry is three years, however, AE Supply did not document a basis for the three-year interval. | PRC-005-1 | R1 | High | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because AE Supply did not fulfill its responsibility to update its Protection System maintenance and testing program in a timely manner to include CTs and PTs. The risk was mitigated by the following factors. First, at the time of installation AE Supply verified the output and accuracy of its CTs and PTs. Second, AE Supply’s three-year interval for maintenance and testing of its relays and DC control circuitry is in line with the other Protection System maintenance and testing programs in the industry and AE Supply’s failure to include a basis for its three-year interval within its Protection System maintenance and testing program was a documentation error. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/9/2011 (when AE Supply included CTs and PTs and the basis for its three-year Protection System relay and DC control circuit maintenance and testing intervals in its Protection system maintenance and testing program) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Compliance Audit | To mitigate this violation, AE Supply included CTs and PTs and the basis for its three-year Protection System relay and DC control circuits maintenance and testing intervals in its Protection system maintenance and testing program. To mitigate this violation, AE Supply will complete maintenance and testing on all CTs and PTs and perform maintenance and testing in conjunction with planned scheduled generating unit outages. | 12/31/2014 (approved completion date) | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed AE Supply's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. AE Supply's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for AE Supply was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) | NCR02600 | RFC2011001132 | Settlement Agreement | During a Compliance Audit conducted from September 12, 2011, to October 3, 2011, ReliabilityFirst determined that AE Supply, as a Generator Owner, was in violation of PRC-005-1 R2. AE Supply could not provide sufficient evidence to demonstrate it implemented its Protection System maintenance and testing program AE Supply's Protection System maintenance and testing program stated that maintenance and testing may be performed based upon manufacturer’s recommended frequency, but did not state maintenance and testing procedures should be based upon manufacturer’s recommendations for maintenance and testing. Specifically, ReliabilityFirst determined AE Supply was following manufacturer’s maintenance and testing procedures, not the maintenance and testing procedures detailed in its Protection System maintenance and testing program. Additionally, AE Supply also could not provide evidence demonstrating it performed maintenance and testing for 18 Protection System relays within its three-year interval. AE Supply has 510 Protection System devices consisting of 420 relays, 0 associated communication systems, 30 current transformers (CTs) and potential transformers (PTs), 30 station batteries, and 30 DC control circuits. Finally, AE Supply could not provide the last date on which it performed maintenance and testing on its CTs and PTs and AE Supply only performed maintenance and testing on its CTs and PTs upon installation. | PRC-005-1 | R2; R2.1;R2.2 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because AE Supply's implementation of manufacturer's maintenance and testing program instead of its documented Protection System maintenance and testing program indicated lack of awareness regarding its own maintenance and testing program and its relation to the NERC Reliability Standards. The risk was mitigated because the manufacturer’s maintenance and testing procedures were similar to those maintenance and testing activities described within AE Supply’s Protection System maintenance and testing program with the exception that AE Supply’s Protection System maintenance and testing program had not been updated to include maintenance and testing for one type of battery. Finally, for the CTs and PTs, while AE Supply provided no evidence of periodic maintenance and testing, it represented that it did test the devices upon installation. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Compliance Audit | To mitigate this violation, AE Supply will complete the maintenance and testing on the Protection System devices, at issue in the violation in conjunction with planned scheduled generating unit outages. | 12/31/2014 (approved completion date) | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed AE Supply's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. AE Supply's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for AE Supply was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | Metropolitan Edison Company (MetEd) | NCR00821 | RFC2011001220 | Settlement Agreement | During a Compliance Audit conducted from October 4, 2011 to October 7, 2011, ReliabilityFirst determined that MetEd, as a Distribution Provider and Transmission Owner, was in violation of PRC-005-1 R2. MetEd could not provide sufficient evidence to demonstrate it completed maintenance and testing of its current transformers (CTs) and potential transformers (PTs) and DC control circuits. MetEd has 3,570 Protection system devices consisting of 1,910 relays, 250 associated communication systems, 635 CTs and PTs, 140 station batteries, and 635 DC control circuits. MetEd represented that it measured and tested its CTs and PTs up to 2010, but could not provide test records demonstrating it completed the maintenance and testing. Additionally, MetEd represented that it performed maintenance and testing of its DC control circuits during breaker testing, but could not provide records that it completed this testing. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because maintenance and testing is ongoing and the functional status of Protection System devices that MetEd has not yet tested is unknown. MetEd represents that it performed maintenance and testing at issue, but did not have the records to demonstrate testing as its Protection System maintenance and testing program, in effect until 2010, did not require MetEd maintain those maintenance and testing records. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Compliance Audit | To mitigate this violation, MetEd will complete and document the required maintenance and testing for the applicable Protection System devices. | 6/30/2013 (approved completion date) | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed MetEd's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MetEd's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
ReliabilityFirst Corporation (ReliabilityFirst) | American Transmission Systems, Incorporated (ATSI) | NCR00686 | RFC2012011388 | Settlement Agreement | On October 31, 2011, ATSI submitted a Self-Certification to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-011-0 R2. ATSI could not provide documentation of its Undervoltage Load Shedding (UVLS) equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program. ATSI initially uploaded its Self-Certification related to the violation of PRC-011-0 R2 to ReliabilityFirst’s portal webpage on October 31, 2011. However, ATSI never formally submitted the Self-Certification through the portal webpage to ReliabilityFirst. Therefore, ReliabilityFirst never received ATSI’s Self-Certification. ReliabilityFirst discovered this issue in October 2012 and assigned tracking number RFC2012011388 to the self-certified violation of PRC-011-0 R2. ATSI reported that it could not locate the test record for one of its 65 (1.5%) UVLS relays. ATSI also self-certified noncompliance based on its inability to locate testing records for four relay schemes from 2003 to 2005. However, ATSI reported it had evidence supporting performance of maintenance and testing on these four relays as of June 18, 2007, the date of mandatory compliance. ReliabilityFirst determined ATSI’s failure to locate testing records for four relay schemes from 2003 to 2005 was not a violation of PRC-011-0 R2 as the standard and requirement was not subject to mandatory enforcement during that time period. | PRC-011-0 | R2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined the violation to be a documentation error because although ATSI did not have the actual test record associated with the UVLS relay at issue, it had evidence that demonstrated it created a work order associated with the UVLS relay as well as worked and closed the order on April 15, 2011. Additionally, when ATSI re-tested the UVLS scheme on November 15, 2011, ATSI found the UVLS relay was fully functional and would have responded appropriately during the duration of the violation. Further, the relay scheme uses microprocessor relays with built-in redundancy monitored by supervisory control and data acquisition. | 4/15/2011 (when ATSI should have completed and recorded maintenance and testing on the relay scheme at issue) | 11/15/2011 (Mitigation Plan completion) | $0 (for RFC2011001109, RFC2011001126, RFC2011001127, RFC2011001128, RFC2011001129, RFC2011001130, RFC2011001131, RFC2011001132, RFC2011001220, and RFC2012011388) | Self-Certification | To mitigate this violation, ATSI completed the maintenance and testing and created the associated test record for the UVLS relay at issue. | 2011-11-15 | TBD | Neither Admits nor Denies | ReliabilityFirst reviewed ATSI's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ATSI's internal compliance program (ICP) is overseen by its parent company FirstEnergy and follows FirstEnergy's Reliability and Compliance Policy. ReliabilityFirst favorably considered certain aspects of the FirstEnergy entities’ compliance programs. For instance, the FirstEnergy entities abide by FirstEnergy’s Reliability and Compliance Policy, which addresses all Reliability Standards. FirstEnergy updates its policies and procedures as necessary and distributes its policies and procedures to FirstEnergy and affiliate employees. The ICP also includes the engagement and support of senior management. A Settlement Agreement covering violations of PRC-005-1 for Jersey Central Power & Light Company (Jersey Central) was filed with FERC under NP11-52-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Monongahela Power Company (Monongahela) was filed with FERC under NP10-177-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review. A Settlement Agreement covering violations of PRC-005-1 for Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) was filed with FERC under NP11-186-000 on May 26, 2011. On June 24, 2011, FERC issued an order stating it would not engage in further review. ReliabilityFirst determined that several violations in this Notice of Penalty evidenced repeat infractions and considered the FirstEnergy entities’ compliance history as an aggravating factor. Although ReliabilityFirst considered the FirstEnergy entities’ compliance history an aggravating factor, ReliabilityFirst determined the FirstEnergy entities’ compliance history does not justify a monetary penalty. Specifically, ReliabilityFirst considered that Jersey Central’s prior violation was an isolated incident involving less than 1% of its Protection System relays. Additionally, ReliabilityFirst considered that Monongahela’s and AE Supply’s prior violations of PRC-005-1 R2 occurred prior to FirstEnergy’s February 25, 2011 acquisition of Monongahela and AE Supply.
SERC Reliability Corporation (SERC) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | SERC2012011111 | Settlement Agreement | On September 24, 2012, ODEC submitted a Self-Report to SERC stating that, as a Generator Operator, it was in violation of VAR-002-1 R1 because it operated the automatic voltage regulators (AVRs) for several generators in a mode other than automatic voltage control mode, without notifying the Transmission Operator (TOP). On September 24, 2012, ODEC self-reported an additional instance of a VAR-002-1.1a R1 violation because it did not have evidence that it notified the TOP that the AVRs for several units were not in automatic voltage control mode during start-up. SERC determined that this instance was related to the initial September 24, 2012 Self-Report and decided to treat the subsequent Self-Report as an expansion of scope. SERC determined that this violation extended back to Version 1 of the Standard. SERC determined that ODEC had three separate instances of noncompliance with VAR-002-1 R1. First, SERC learned that the AVRs for ODEC’s three combustion turbine units at Marsh Run and five combustion turbine units at Louisa (collectively referred to as “MR/L units”) were mislabeled, causing the operators to operate the AVR in a mode other than automatic voltage control mode. ODEC operators had three options to choose for the AVR mode of operation: “OFF”, “PF” (power factor control mode), or “VAR” (VAR control mode). ODEC operators had been instructed never to operate in the “OFF” position and thus could choose either “PF” or “VAR.” ODEC later learned “OFF” meant that the AVR of the generator was operating in automatic voltage control mode as opposed to being off. Upon discovery of the labeling issue in July 2009, ODEC changed the “OFF” label on the AVRs to “VOLT” and operated the MR/L units with the AVRs in automatic voltage control mode. Second, after correcting the labeling error but prior to the adoption of revised procedures in July 2009, ODEC operated the MR/L units such that during start-up, each unit’s AVR was in VAR control mode for approximately 12 to 14 minutes and then placed in automatic voltage control mode after achieving the desired voltage. ODEC did not notify the TOP prior to operating the MR/L units in a mode other than automatic voltage control mode. ODEC cannot determine how many times the start-up of each of the eight MR/L units was performed in the manner prescribed by the procedures prior to July 2009. During this time, ODEC started up the MR/L units an average of 47 times per year for each 84 MW unit and 70 times per year for each 168 MW unit. Finally, although the ODEC operating procedures were revised in July 2009, ODEC plant operators did not consistently conduct the MR/L unit start-ups according to the revised procedure. Some operators would start the MR/L units with the AVR in automatic voltage control mode, while others would start with the AVR in VAR control mode and then switch the AVR to automatic voltage control mode after the unit reached full load. ODEC lacked the data to compare how many start-ups its operators conducted with the MR/L units’ AVRs in automatic voltage control mode against the start-ups begun with the AVR in VAR control mode. | VAR-002-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ODEC complied with all TOP-issued directives during the duration of the violation. In addition, when ODEC operated the MR/L units, the AVRs were in service and controlling for VAR or power factor, which should have allowed the units to respond to support the BPS if required. Furthermore, the MR/L units are peaking generating units that are operated an average of 65 times during a typical year. | 8/2/2007 (when the Standard became mandatory and enforceable) | 9/13/2012 (Mitigation Plan completion) | $12,000 (for SERC2012011111, SERC2012011112, and SERC2012011113) | Self-Report | To mitigate this violation, ODEC: 1) altered the human-machine interface screens such that the generator mode “OFF” was changed to “VOLT;” 2) drafted procedures which directed unit operators at MR/L to operate the generators in automatic voltage control mode; 3) instructed all plant operators at the Marsh Run and Louisa plants to operate the MR/L units with the AVR in automatic voltage control mode, including during start-up, unless directed otherwise by the TOP; 4) trained all system operators as to the proper AVR operation mode for the MR/L units and the communications protocol in the event of a change of status or capability of the generator Reactive Power resources; and 5) drafted, approved, and implemented new procedures for the operations of the Marsh Run and Louisa plants. | 2012-09-13 | 2013-03-14 | Neither Admits nor Denies | SERC reviewed ODEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ODEC's ICP has been in place since December 21, 2011. ODEC has posted its ICP on a company-wide, publicly available website, making it available to all ODEC employees. ODEC has a NERC compliance officer who has overall approval authority for, and internal oversight of, the ICP. The NERC compliance officer also has direct access to ODEC's chief executive officer and the ODEC board of directors. ODEC has a NERC compliance specialist responsible for overseeing the implementation of and day-to-day compliance with the NERC Reliability Standards. ODEC's NERC compliance specialist conducts an annual internal audit of the ICP, and ODEC performs interim reviews of its procedures in light of new Standards, new versions of Standards, or other NERC guidance documents. ODEC conducts annual training on complying with the NERC Reliability Standards and publishes a newsletter each quarter which addresses timely topics for compliance.
SERC Reliability Corporation (SERC) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | SERC2012011112 | Settlement Agreement | On September 24, 2012, ODEC submitted a Self-Report to SERC stating that, as a Generator Operator, it was in violation of VAR-002-1 R3 because it failed to notify the Transmission Operator (TOP) within 30 minutes of a change in the status of automatic voltage regulators (AVRs). On September 24, 2012, ODEC self-reported an additional instance of a VAR-002-1.1a R3 violation because it did not have evidence that it notified the TOP that the AVRs for several units were not in automatic voltage control mode during start-up. SERC determined that this instance was related to the initial September 24, 2012 Self-Report and decided to treat the subsequent Self-Report as an expansion of scope. SERC determined that this violation extended back to Version 1 of the Standard. SERC determined that ODEC had three separate instances of noncompliance with VAR-002-1 R3. First, SERC learned that the AVRs for ODEC’s three combustion turbine units at Marsh Run and five combustion turbine units at Louisa (collectively referred to as “MR/L units”) were mislabeled, causing the operators to operate the AVR in a mode other than automatic voltage control mode. ODEC operators had three options to choose for the AVR mode of operation: “OFF”, “PF” (power factor control mode), or “VAR” (VAR control mode). ODEC operators had been instructed never to operate in the “OFF” position and thus could choose either “PF” or “VAR.” ODEC later learned “OFF” meant that the AVR of the generator was operating in automatic voltage control mode as opposed to being off. Upon discovery of the labeling issue in July 2009, ODEC changed the “OFF” label on the AVRs to “VOLT” and operated the MR/L units with the AVRs in automatic voltage control mode. ODEC did not notify the TOP of the change in AVR status for the MR/L units within 30 minutes of the change. Second, after correcting the labeling error but prior to the adoption of revised procedures in July 2009, ODEC operated the MR/L units such that during start-up, each unit’s AVR was in VAR control mode for approximately 12 to 14 minutes and then placed in automatic voltage control mode after achieving the desired voltage. ODEC did not notify the TOP of the change in AVR status for the MR/L units within 30 minutes of the change. ODEC cannot determine how many times the start-up of each of the eight MR/L units was performed in the manner prescribed by the procedures prior to July 2009. During this time, ODEC started up the MR/L units an average of 47 times per year for each 84 MW unit and 70 times per year for each 168 MW unit. Finally, although the ODEC operating procedures were revised in July 2009, ODEC plant operators did not consistently conduct the MR/L unit start-ups according to the revised procedure. Some operators would start the MR/L units with the AVR in automatic voltage control mode, while others would start with the AVR in VAR control mode and then switch the AVR to automatic voltage control mode after the unit reached full load. ODEC lacked the data to compare how many start-ups its operators conducted with the MR/L units’ AVRs in automatic voltage control mode against the start-ups begun with the AVR in VAR control mode. ODEC did not notify the TOP of the change in AVR status for the MR/L units within 30 minutes of the change. | VAR-002-1 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ODEC complied with all TOP-issued directives during the duration of the violation. In addition, when ODEC operated the MR/L units, the AVRs were in service and controlling for VAR or power factor, which should have allowed the units to respond to support the BPS if required. Furthermore, the MR/L units are peaking generating units that are operated an average of 65 times during a typical year. | 8/2/2007 (when the Standard became mandatory and enforceable) | 9/13/2012 (Mitigation Plan completion) | $12,000 (for SERC2012011111, SERC2012011112, and SERC2012011113) | Self-Report | To mitigate this violation, ODEC: 1) altered the human-machine interface screens such that the generator mode “OFF” was changed to “VOLT;” 2) drafted procedures which directed unit operators at MR/L to operate the generators in automatic voltage control mode; 3) instructed all plant operators at the Marsh Run and Louisa plants to operate the MR/L units with the AVR in automatic voltage control mode, including during start-up, unless directed otherwise by the TOP; 4) trained all system operators as to the proper AVR operation mode for the MR/L units and the communications protocol in the event of a change of status or capability of the generator Reactive Power resources; and 5) drafted, approved, and implemented new procedures for the operations of the Marsh Run and Louisa plants. | 2012-09-13 | 2013-03-14 | Neither Admits nor Denies | SERC reviewed ODEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ODEC's ICP has been in place since December 21, 2011. ODEC has posted its ICP on a company-wide, publicly available website, making it available to all ODEC employees. ODEC has a NERC compliance officer who has overall approval authority for, and internal oversight of, the ICP. The NERC compliance officer also has direct access to ODEC's chief executive officer and the ODEC board of directors. ODEC has a NERC compliance specialist responsible for overseeing the implementation of and day-to-day compliance with the NERC Reliability Standards. ODEC's NERC compliance specialist conducts an annual internal audit of the ICP and ODEC performs interim reviews of its procedures in light of new Standards, new versions of Standards, or other NERC guidance documents. ODEC conducts annual training on complying with the NERC Reliability Standards and publishes a newsletter each quarter which addresses timely topics for compliance.
SERC Reliability Corporation (SERC) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | SERC2012011113 | Settlement Agreement | On September 24, 2012, ODEC submitted a Self-Report to SERC stating that, as a Generator Operator, it was in violation of VAR-002-1 R2 because it could not provide evidence that it operated several combustion turbines at its Louisa and Marsh Run plants within the voltage schedule directed by the Transmission Operator (TOP). The TOP required ODEC to maintain its voltage schedule within the associated bandwidth of +/- 3 kV based on a 30-minute average. ODEC’s system voltage levels are not recorded at the power plants. The operator can only see instantaneous values. ODEC’s TOP records the voltage levels at the Louisa and Marsh Run plants. According to an ODEC-prepared summary of the analysis of the TOP’s records, ODEC did not operate within the directed voltage schedule on two occasions. The first instance occurred on July 17, 2010 and affected two combustion turbine units at the Marsh Run plant, which were operating at 230 kV when the voltage schedule was 234 kV +/- 3 kV. The second instance occurred on September 25, 2010 and affected one combustion turbine unit at the Louisa plant, which was operating at 231 kV when the voltage schedule was 235 kV +/- 3 kV. In both instances, ODEC was 1 kV (0.4%) below the lower voltage limit of TOP’s directed voltage schedule. | VAR-002-1 | R2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ODEC complied with all TOP-issued directives during the violation. In addition, ODEC was 1 kV outside of the voltage schedule on two occasions for approximately 30 minutes for each excursion. Furthermore, the Marsh Run and Louisa units are peaking generating units that are operated an average of 65 times during a typical year. | 7/17/2010 (when ODEC first operated outside of its voltage schedule) | 3/12/2013 (Mitigation Plan completion) | $12,000 (for SERC2012011111, SERC2012011112, and SERC2012011113) | Self-Report | To mitigate this violation, ODEC: 1) reviewed the operating procedures at the Marsh Run and Louisa plants and made revisions to ensure that the operators are clear as to when the TOP (or its designee) is to be notified whenever any of ODEC’s eight combustion turbines at the Marsh Run or Louisa operates outside of acceptable TOP-provided schedules; 2) developed and implemented an improved methodology for archiving operating data for its operational compliance and all TOP notifications as required by VAR-002-1.1b R2; and 3) generated data archives from voltage data provided by the TOP through supervisory control and data acquisition (SCADA) in one-minute averages, showing it is following the TOP's operating protocols. | 2013-03-12 | 2013-05-27 | Neither Admits nor Denies | SERC reviewed ODEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ODEC's ICP has been in place since December 21, 2011. ODEC has posted its ICP on a company-wide, publicly available website, making it available to all ODEC employees. ODEC has a NERC compliance officer who has overall approval authority for, and internal oversight of, the ICP. The NERC compliance officer also has direct access to ODEC's chief executive officer and the ODEC board of directors. ODEC has a NERC compliance specialist responsible for overseeing the implementation of and day-to-day compliance with the NERC Reliability Standards. ODEC's NERC compliance specialist conducts an annual internal audit of the ICP and ODEC performs interim reviews of its procedures in light of new Standards, new versions of Standards, or other NERC guidance documents. ODEC conducts annual training on complying with the NERC Reliability Standards and publishes a newsletter each quarter which addresses timely topics for compliance.
Texas Reliability Entity, Inc. (Texas RE) | Coleto Creek Power, LP (CCP) | NCR04042 | TRE201100396 | Settlement Agreement | CCP, as a registered Generator Owner, submitted a Self-Report on August 2, 2011, stating that it was in violation of PRC-005-1 R2 because it failed to provide evidence that Protection System devices were maintained and tested within the defined intervals. Specifically, CCP self-reported that 35 current transformers (CTs), 3 direct current (DC) circuits, and 1 neutral ground transformer (PT) were not tested within the designated 10-year interval. CCP conducted an internal assessment of its Protection System devices in July 2011 and discovered through a random sampling that 31 CTs were not tested. Subsequently, an August 2012 internal assessment, in which all test certificates were reviewed, revealed that the PT would need to be tested because no documentation was available to evidence that it had been tested within the defined 10-year interval. Additionally, a February 2013 internal assessment discovered four neutral ground CTs on a 4 kV line that were also tested outside of the designated 10-year window. CCP and its corporate NERC compliance team discovered the missed testing during a routine internal assessment. Texas RE determined, after a review of the evidence, that 35 CTs, 1 PT, and 3 DC Control Circuits, which make up 46.43% of CCP's 84 total Protection System devices, were not tested within the designated 10-year interval. | PRC-005-1 | R2 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 39 Protection System devices in scope represented 46.43% of CCP's 84 generation elements. The risk was partially mitigated because the current transformers that were not tested were associated with the Generation Step-Up (GSU) and auxiliary transformer differential protection scheme. If one of the subject CTs were to fail, the differential protection would still trip the transformer off. Further, the entity indicated that the DC circuitry to the generator breaker is regularly monitored during shut down to help ensure its reliability. The existing generator protection offered some level of redundancy. Specifically the negative sequence and phase distance elements of the generator protection system offer this redundancy. Faults downstream of the generator will activate this protection and will trip the generator (after some time delay) and open the generator breakers in the switchyard to electrically isolate the sections of the system in question. Finally, there were no reported misoperations during the violation period. | 9/1/2010 (when the devices should have been tested) | 4/30/2013 (Mitigation Plan completion) | 9000 | Self-Report | To mitigate this violation, CCP: 1) tested the current transformers on October 26, 2011; 2) tested the three DC Control Circuits on November 10, 2011; 3) tested the neutral ground transformer on January 16, 2013; 3) tested the four neutral ground current transformers on April 30, 2013; 4) added a project maintenance activity to the CCP computerized maintenance management system to test and verify the continuity of the DC control circuitry; 5) expanded the inventory list of instrument transformers to include the auxiliary transformer instrument transformers and devices on the 4 kV line; 6) had subject matter experts perform a fleet-wide assessment of the Protection System maintenance and testing inventory sheet to ensure that required devices were included; and 7) reviewed the station protection drawings and inventory sheets to ensure both matched. | 2013-04-30 | 5/8/2013 | Neither Admits nor Denies | Texas RE reviewed CCP’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. CCP's ICP is outlined in the GDF Suez Energy North America NERC ICP site procedure manual. This procedure dictates the roles and responsibilities of all personnel involved in NERC compliance, from senior management to plant staff. The ICP also includes regular internal assessments to ensure continuing compliance and detection of any non-compliance activities. The compliance program ensures active internal monitoring of the NERC Reliability Standards and encourages self-reporting of possible violations. CCP and the corporate NERC compliance team discovered that CCP missed testing during a routine internal assessment that is part of the compliance program. The CCP compliance program includes the discovery, mitigation, and steps taken to prevent reoccurrence when possible non-compliances are identified. The corporate program is managed by the NERC Compliance Group; each site has a NERC compliance representative who is responsible for day to day compliance activities of the plant. The plant manager or production manager serve as the primary compliance contact for the site and oversees the compliance activities. International Power-GDF SUEZ has a NERC Steering Committee which is chaired by the director of the NERC compliance program and is attended by the president and chief executive officer of the generation group, vice president of regulatory compliance, vice president of solid fuels, vice president of combustion turbines, vice president of renewables, general counsel for the generation group, and the senior counsel/compliance officer.