## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2012011148 | Settlement Agreement | During a Compliance Audit conducted on September 27, 2012, FRCC determined that SEC, as a Transmission Operator, was in violation of MOD-028-1 R6. SEC documents were not sufficient evidence to demonstrate that SEC used the lesser of the sum of the incremental Transfer Capability and the impacts of Firm Transmission Services as the Total Transfer Capabilities (TTCs), as specified in SEC’s Available Transfer Capability Implementation Document (ATCID), that were included in the study model, or the sum of Facility Ratings of all ties comprising the Available Transfer Capabilities (ATC Path). Specifically, SEC’s Path Summary listed 7 of 22 paths that did not have a segment for the sum of the Facility Ratings of all ties comprising the ATC Path. For these seven paths the TTC only used the incremental Transfer Capability and the impacts of Firm Transmission Services. | MOD-028-1 | R6; R6.3 | pending | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SEC did not limit the TTC to the sum of the Facility Ratings of the ties comprising the paths, resulting in larger TTC than is allowed by the Standard. However, the real-time contingency analysis program would have detected any risk to the BPS and alerted system operators to allow them to prepare an effective operational mitigation plan in the event an issue occurred. | 4/1/2011 (when the Standard became mandatory and enforceable) | 10/11/2012 (when SEC revised the segments/paths setup to include the Facility Ratings of all ties comprising the ATC path component) | $3,000 (for FRCC2012011148 and FRCC2012011149) | Compliance Audit | To mitigate this violation, SEC: 1) revised the segment/paths setup in webTrans for the seven paths to include the Facility Ratings of all ties comprising the ATC Path component; 2) ensured that the TTC value of these ATC Paths is the lesser of the sum of the incremental Transfer Capability and the Facility Ratings of all ties comprising the ATC Path; 3) implemented the revision to the ATC segments/paths setup to the ATC path setup; and 4) included an agenda item to re-verify the data modeled in the TTC Engine and re-validate the calculated ATC values as part of its Quarterly System Operations/Transmission Planning meetings. | 2013-07-09 | TBD | Neither Admits nor Denies | FRCC reviewed SEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC verified that SEC has a documented ICP that includes corrective action processes, internal controls, senior management involvement, and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure SEC maintains a strong ICP.
Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2012011149 | Settlement Agreement | During a Compliance Audit conducted on September 27, 2012, FRCC determined that SEC, as a Transmission Service Provider, was in violation of MOD-028-1 R8. SEC documents were not sufficient evidence to demonstrate that when calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an Available Transfer Capabilities (ATC) Path, SEC used the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF A SEC document demonstrated an example where 653 MW of firm commitments were included in the Total Transfer Capabilities (TTC) calculation for impacts of Firm Transmission Service; however, only 150 MW were subtracted as ETC from TTC in the ATC calculation. Another document reflected three similar examples where firm commitments used in the calculation of TTC were not subtracted from TTC during the ATC calculation. The commitments that were not included in the ETC calculation are 350 MW SSN-FPL, 530 MW SSO-FPL, 750 MW SSN-FPC, and 675 MW SSO-FPC. Specifically, SEC failed to include all firm NITS, GF, PTP, ROR, and OS commitments in the calculation of ETC for 3 of 22 ATC paths. | MOD-028-1 | R8 | pending | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because by incorrectly calculating the ETC values, the entity TTC calculations were erroneously high by as much as 750 MW which could result in overstating ATC values causing potential System Operating Limits violations. However, the real-time contingency analysis program would have detected any risk to the BPS and alerted system operators to allow them to prepare an effective operational mitigation plan in the event an issue occurred. | 4/1/2011 (when the Standard became mandatory and enforceable) | present | $3,000 (for FRCC2012011148 and FRCC2012011149) | Compliance Audit | To mitigate this violation, SEC: 1) modified the TTC Engine and ATC formula setup to deduct from calculation of ATC, the ETCF values as modeled in the Transmission Service Request List of Interchange module. Note, these ETCF values are reflected in the calculation of ATC as Committed Used firm values (CUF); and 2) initiated a review of the modifications described above in the Seminole Quarterly System Operations/Transmission Planning meetings to re-verify the data modeled in the TTC Engine and re-validate the calculated ATC values. To mitigate this violation, SEC will: 1) evaluate and implement changes to the TTC Engine and Seminole transmission scheduling process to deduct the full network allocation/grandfathered contracts in the calculation of ATC values on Seminole’s transmission paths; 2) reflect the grandfathered contracts as unique transmission reservations in Seminole’s OASIS. These reservations will programmatically carry over to the calculation of ATC as ETCF values, and will eliminate the need to manually modify webTrans in the manner described above; and 3) also review its ATC Implementation Document and make any necessary changes. | 12/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed SEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC verified that SEC has a documented ICP that includes corrective action processes, internal controls, senior management involvement, and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure SEC maintains a strong ICP.
Northeast Power Coordinating Council, Inc. (NPCC) | New York Power Authority (NYPA) | NCR07161 | NPCC201100236 | Settlement Agreement | On February 11, 2011, NYPA submitted a Self-Report to NPCC stating that, as a Generator Owner (GO) and Transmission Owner (TO), it was in violation of PRC-005-1 R2. As part of NYPA's internal compliance program (ICP), NYPA conducted an internal assessment to determine the sufficiency of its compliance materials. The assessment revealed that although NYPA had actively managed maintenance and testing programs for its Protections Systems in place at all of its transmission and generation facilities, there were gaps and inconsistencies in the implementation of the programs. The assessment identified the following implementation gaps and inconsistencies: a) gaps in documentation to demonstrate that all Protection System devices were maintained within the defined intervals; b) inconsistent implementation of the battery maintenance and testing program; and c) gaps in documentation for the insulation resistance testing of the associated secondary circuitry wiring for current transformers (CTs) and potential transformers (PTs). The deficiencies comprised 95 devices out of a total inventory of 3,641 (2.6%). | PRC-005-1 | R2; R2.1; R2.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. First, the NYPA relay testing program follows the NPCC Directory 3, Maintenance Criteria for Bulk Power System Protection, and more than 95% of NYPA's relay testing was performed within the required intervals. In the case of those relays not shown to have been tested within the required interval, certain characteristics of those relays mitigated the risk of the missed testing. Specifically, those relays contain components which have self-monitoring capabilities which alarm locally and provide a general alarm to a control center upon misoperation. The control center is manned twenty four hours a day, seven days a week and will dispatch personnel to perform an investigation and make necessary repairs. In addition, while NYPA completed testing of its CTs and PTs at the downstate small clean power plants (SCPP) five months late, NYPA's testing program specifies a testing interval of eight years, and all testing results were satisfactory. Furthermore, the SCPP's individual unit maximum output capability is 80 MW. NYPA implemented most of the interval components of the maintenance and testing program with satisfactory results. Lastly, all BPS station battery banks are continuously monitored via alarm points, which enables NYPA operations and maintenance personnel to respond to take corrective actions as necessary. | 6/21/2007 (when NYPA registered as a GO and TO) | 12/15/2011 (Mitigation Plan completion) | 25000 | Self-Report | To mitigate the violation, NYPA: 1) performed a review of NYPA's maintenance and testing program for Protection Systems and associated equipment and updated policies and procedures to ensure standardized application of the program at all NYPA transmission and generating facilities; 2) communicated the updated policies and procedures to employees responsible for the maintenance and testing of Protection Systems and associated equipment and conducted training on the updated policies; 3) reviewed NYPA's maintenance and testing program for battery systems and made changes where necessary to ensure that proper maintenance and testing procedures are implemented; 4) communicated the revised battery systems maintenance and testing program to employees responsible for the maintenance and testing of battery systems and conducted training on the revised program; and, 5) incorporated the maintenance and testing programs for the protection and battery systems into NYPA's automated work control system. | 2011-12-15 | 2012-04-05 | Does not Contest | NPCC reviewed NYPA's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. NYPA's ICP establishes a uniform policy for energy-related regulatory compliance across the organization. The policy requires direct access by the compliance officer to the chief executive officer, and it requires that compliance reports are provided to the governance committee at all regularly scheduled meetings. The ICP is managed independently and has the support and participation of senior management. Resources to support NYPA's ICP are reviewed to ensure appropriate staffing. In addition, NYPA's ICP also includes awareness training to the entire organization along with specialized training for staff directly responsible for compliance with the reliability standards. NPCC also considered NYPA's cooperation during the processing of the violation as a mitigating factor in the penalty determination. NYPA quickly addressed the non-compliance and provided a Self-Report describing in detail the facts pertaining to the violation. NYPA provided appropriate authorized management to ensure full cooperation throughout the settlement process, and it engaged company resources early in the process to ensure timely resolution to the issues pertaining to the violation.
Northeast Power Coordinating Council, Inc. (NPCC) | NSTAR Electric Company (NSTAR) | NCR07180 | NPCC2012010580 | Notice of Confirmed Violation | On June 22, 2012, NSTAR submitted a Self-Report to NPCC stating that, as a Transmission Owner (TO), it was in violation of PRC-005-1 R2.1. During a routine review of maintenance activities for control and Protection Systems, NSTAR determined that the monthly signal adequacy test for the power line carrier (PLC) communication system associated with the West Medway (NSTAR) and Millbury (National Grid) line 357 was not performed as required by NSTAR’s Protection System maintenance and testing program procedure, W10999 Bulk Power System Protection Assembly Communication Testing Maintenance Plan (dated October 4, 2010 Revision 1) (Procedure W10999). NSTAR mis-categorized the PLC as having an automatic check-back function. Automatic check-back is a method NSTAR utilizes for “continuous monitoring" which would exclude the communication channel from the monthly testing program. Testing was missed for 1 out of 24 (4.1%) communication systems. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC determined that the violation posed a moderate risk because, in the absence of monthly testing, NSTAR could not know whether the PLC communication system would operate properly in the event of an external fault, potentially resulting in a misoperation. However, high speed clearing on both the primary and secondary lines of protection was in service at all times, providing proper clearing for circuit faults. On February 3, 2011, the system operated correctly (clearing time of 4 cycles) for a fault that occurred on the transmission line. In addition, annual testing of the directional comparison blocking carrier systems, which provide the primary line protection for the PLC communication system associated with line 357, was completed per NSTAR policy with no problems found. | 6/21/2007 (when NSTAR registered as a TO) | 3/7/2012 (when the missed monthly testing was completed) | 0 | Self-Report | To mitigate this issue, NSTAR: 1) completed testing of the line 357 communication channels; 2) performed a review of station drawings for PLC communications channels to verify testing requirements specified in NSTAR Procedure W10999; 3) verified the station drawings against as-found field conditions and identified no discrepancies; 4) reviewed all PLC communications channels to ensure possible violation did not extend beyond the line 357 communications channels; and 5) updated NSTAR Procedure W10999 to reflect the monthly PLC communications channel testing for line 357 as well as any other discrepancies identified in previous milestone activities associated with the Mitigation Plan. | 2012-10-12 | 2013-05-22 | Admits | NPCC reviewed NSTAR's internal compliance program and considered it to be a mitigating factor in the penalty determination. NSTAR has an internal compliance program in place that is supported and engaged by senior management. The senior vice president – operations has a weekly meeting with the chief executive officer, and the vice president – information systems has meetings at least monthly with the chief executive officer. These meetings ensure independent access to senior management for issues involving compliance with NERC standards. NSTAR has a training program in place for compliance staff as well as all employees responsible for compliance with NERC standards. In addition, NSTAR has a program in place for employees to report possible compliance issues confidentially without fear of retaliation. NPCC also considered NSTAR's cooperation as a mitigating factor in assessing the penalty as well as the fact that it self-reported the violation to NPCC. NPCC assessed a $0 penalty because NSTAR agreed to the violation and the annual testing of the directional comparison blocking carrier system was performed. Additionally, the testing of the protective relay systems was completed within the defined interval to ensure that the clearing would be proper for a fault on the line. Concurrently being filed is a Spreadsheet Notice of Penalty with $0 penalty for an affiliate of NSTAR, Western Massachusetts Electric Company, for a violation of PRC-005-1 R2.
Northeast Power Coordinating Council, Inc. (NPCC) | Western Massachusetts Electric Company (WMECO) | NCR07232 | NPCC2012010578 | Notice of Confirmed Violation | On June 18, 2012, WMECO submitted a Self-Report to NPCC stating that, as a Transmission Owner (TO), it was in violation of PRC-005-1 R2.1. During a recent review of test documentation, WMECO determined that it did not complete monthly power line carrier (PLC) testing on a 345kv transmission line from June 2007 to May 2012. Monthly tests are required by the Northeast Utility Transmission Maintenance Program Manual (TMPM) for telecommunication system channels that are not continuously monitored. WMECO determined that it failed to coordinate fully testing of the line with the neighboring TO on several occasions, resulting in incomplete tests (i.e., lack of verification of receipt of the carrier signal at the remote end of the line) and missing documentation. The monthly PLC testing resumed on May 3, 2012. Testing was missed for 1 out of 22 (4.5%) communication systems. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC determined that the violation posed a moderate risk because without performing the monthly testing, WMECO could not know whether the carrier system would operate properly in the event of an external fault, potentially resulting in a misoperation. The risk to the reliability of the BPS was mitigated by the following factors. For the duration of the violation, WMECO was performing testing on the line, although not on a monthly basis. In addition, high-speed clearing on both the primary and secondary lines of protection was in service at all times, providing proper clearing for circuit faults. Furthermore, annual testing of the directional comparison blocking carrier systems (which provide the primary protection for the line) was completed with no problems found. Additionally, records indicate that there were no misoperations of the transmission lines involving the carrier systems while the monthly testing was not being performed. | 6/21/2007 (when WMECO registered as a TO) | 5/3/2012 (when monthly testing resumed) | 0 | Self-Report | To mitigate this issue, WMECO: 1) performed a review of all PLC communication channels to ensure no other communication channels lacked the monthly testing; 2) revised the TMPM to: a) provide detailed steps and requirements to perform the monthly carrier tests; b) specify the need for personnel to be present at the remote end; and c) provide guidance to personnel on the appropriate action to be taken when there is a test failure or failure to perform tests as planned. (Training on the revised TMPM will be conducted for appropriate maintenance personnel); 3) defined, published, and conducted training on a work order closeout process to ensure job steps have been performed and that there is proper documentation of work performed in WMECO's maintenance database; 4) implemented the following changes to WMECO's maintenance database: a) created a compliance tab for all Protection System components annotating attributes which determine maintenance activity and interval; b) populated the equipment class and the compliance tab fields for all teleprotection systems; and c) ensured that triggers for monthly/annual testing are correct; 5) conducted a review to ensure similar conditions do not exist elsewhere (WMECO owns 204 Protection System devices on the bulk power system); 6) updated the procedure tab in WMECO's maintenance database to include the correct reference to TMPM monthly carrier check procedure; and 7) counseled the WMECO staff involved. | 2012-12-05 | 2013-05-08 | Admits | NPCC reviewed WMECO's internal compliance program and considered it to be a mitigating factor in the penalty determination. Northeast Utilities and its subsidiary companies (including WMECO) have a robust compliance program and are committed to fully complying with all laws and regulations. Senior management in all NU operating companies is actively engaged in compliance activities and participates on the NERC Reliability Compliance Officer Committee (NRCOC). The NRCOC is chaired by the vice president - transmission strategy & operations, who has overall responsibility within the NU organization for compliance with NERC standards and is a member of the NU Compliance and Ethics Committee. NPCC considered WMECO's cooperation as a mitigating factor in assessing the penalty. NPCC also considered that WMECO self-reported the violation. NPCC assessed a $0 penalty because WMECO agreed to the violation and the annual testing of the directional comparison blocking carrier system was performed. Additionally, the testing of the protective relay systems was completed within the defined interval to ensure that the clearing would be proper for a fault on the line. Concurrently being filed is a Spreadsheet Notice of Penalty with $0 penalty for an affiliate of WMECO, NSTAR Electric Company, for a violation of PRC-005-1 R2.
ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Columbus Southern Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, and Wheeling Power Company (AEP) | NCR00682 | RFC2012011193 | Settlement Agreement | On October 1, 2012, AEP submitted a Self-Certification to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-008-0 R2. AEP discovered that its Under Frequency Load Shedding (UFLS) database lacked information that it had performed maintenance and testing on 28 of its 693 batteries within the required intervals. | PRC-008-0 | R2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because it had the potential to affect the reliable operation of the BPS by allowing important UFLS Protection System devices to remain unmaintained and untested. However, ReliabilityFirst verified that AEP’s automatic UFLS programs consisted of acceptable reliability performance requirements. In addition, in ReliabilityFirst, AEP is capable of shedding approximately 3,100 MW in excess of its required amount of load. These excess amounts offset the amount of load associated with the UFLS devices at issue in the violation. Therefore, if the UFLS devices failed due to deficient maintenance and testing, AEP would still have met its automatic UFLS program requirements. AEP utilizes this excess as a means to ensure that it meets the requirements of its UFLS program in the event a device fails or is removed temporarily for maintenance and testing. | 6/18/2007 (when the Standard became mandatory and enforceable) | 3/4/2013 (Mitigation Plan completion) | $0 (for RFC2012011193 and SPP2012010130) | Self-Certification | To mitigate this violation, AEP: 1) reviewed the asset tracking database for inconsistencies relating to recloser batteries; 2) populated and scheduled newly-identified batteries for maintenance and testing; and 3) completed maintenance and testing activities. | 2013-03-04 | 2013-05-13 | Admits | ReliabilityFirst reviewed AEP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. AEP’s compliance officer has independent access to the chief executive officer, executive committee, and board of directors. In addition, AEP’s reliability compliance committee is responsible for ensuring implementation and oversight of the ICP. The NERC compliance steering committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. AEP’s ICP provides an annual schedule of standards to review and internal assessments of compliance by each affected business unit and by independent staff such as internal audits and regulatory services. AEP also utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. Furthermore, AEP’s tools and training enable employees to comply with the Reliability Standards. ReliabilityFirst also considered that AEP discovered one of the two violations through a Self-Report and applied mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self reporting by Registered Entities. AEP continuously searches for opportunities to discover potential gaps in its Protection System maintenance and testing. AEP discovered the violations by executing custom repeatable queries of its asset tracking database and applying the queries to its Protection System maintenance and testing dashboard, which is refreshed daily. AEP utilized these controls to identify the gaps in its Protection System maintenance and testing at issue in the violation. AEP promptly reported the violation at issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self reporting and internal controls, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for the violation. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering four violations of PRC-008-0 R2 for AEP was filed with FERC under NP12-30-000 on May 30, 2012. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although ReliabilityFirst and SPP RE considered AEP’s violation history as an aggravating factor, ReliabilityFirst and SPP RE determined that AEP’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst and SPP RE assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation.
Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Service Corp. As Agent For Public Svc. Co. Of Oklahoma & SW Ele Pwr Co.(AEP) | NCR01056 | SPP2012010130 | Settlement Agreement | On May 1, 2012, AEP submitted a Self-Report to SPP RE stating that, as a Transmission Owner and Distribution Provider, it was in violation of PRC-008-0 R2. AEP discovered that its Under Frequency Load Shedding (UFLS) database lacked information that it had performed maintenance and testing on two if its 191 batteries, two of its 218 voltage and current sensing devices, and 10 of its 466 direct current control circuits. | PRC-008-0 | R2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because it had the potential to affect the reliable operation of the BPS by allowing important UFLS Protection System devices to remain unmaintained and untested. However, AEP, in SPP-RE, is capable of shedding approximately 350 MW in excess of its required amount of load. These excess amounts offset the amount of load associated with the UFLS devices at issue in the violations. Therefore, if the UFLS devices failed due to deficient maintenance and testing, AEP would still have met its automatic UFLS program requirements. AEP utilizes this excess as a means to ensure that it meets the requirements of its UFLS program in the event a device fails or is removed temporarily for maintenance and testing. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/9/2013 (Mitigation Plan completion) | $0 (for RFC2012011193 and SPP2012010130) | Self-Report | To mitigate this violation, AEP: 1) revised its transmission maintenance and testing program to revise wording surrounding instrument transformers; 2) developed a discussion guide pertaining to the changes it made to the program; 3) ensured all applicable personnel reviewed the discussion guide; and 4) completed applicable maintenance and testing activities on the Protection System devices at issue. | 2013-04-09 | TBD | Admits | SPP RE reviewed AEP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. AEP’s compliance officer has independent access to the chief executive officer, executive committee, and board of directors. In addition, AEP’s reliability compliance committee is responsible for ensuring implementation and oversight of AEP’s ICP. The NERC compliance steering committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. AEP’s ICP provides an annual schedule of standards to review and internal assessments of compliance by each affected business unit and by independent staff such as internal audits and regulatory services. AEP also utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. Furthermore, AEP’s tools and training enable employees to comply with the Reliability Standards. SPP RE also considered that AEP discovered one of the two violations through a Self-Report and applied mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self reporting by Registered Entities. AEP continuously searches for opportunities to discover potential gaps in its Protection System maintenance and testing. AEP discovered the violations by executing custom repeatable queries of its asset tracking database and applying the queries to its Protection System maintenance and testing dashboard, which is refreshed daily. AEP utilized these controls to identify the gaps in its Protection System maintenance and testing at issue in the violation. AEP promptly reported the violation at issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, SPP RE seeks to encourage this type of self reporting and internal controls, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for the violation. When assessing the penalty for the violation at issue, SPP RE considered whether the facts of this violation evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. A Settlement Agreement covering four violations of PRC-008-0 R2 for AEP was filed with FERC under NP12-30-000 on May 30, 2012. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although ReliabilityFirst and SPP RE considered AEP’s violation history as an aggravating factor, ReliabilityFirst and SPP RE determined that AEP’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst and SPP RE assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation.
SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2013011950 | Settlement Agreement | On February 14, 2013, DEP submitted a Self-Report to SERC stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1 R1. DEP operated one automatic voltage regulator (AVR) in VAR mode without notifying the Transmission Operator (TOP). The issue occurred at the Smith Energy Complex. The Smith Energy Complex has a capacity of 1904 MW. The unit involved, ST4, is a 228 MW steam-driven unit of a 588 MW combined cycle power plant. ST4 entered commercial operation in 2002 and operated with a 66.81% capacity factor in 2012. On September 26, 2012, exciter testing was being performed at Smith Energy Complex. While performing the testing, DEP determined that the AVR for ST4 was operating in VAR control mode instead of voltage control mode as directed by the TOP. According to DEP, there was a misinterpretation of the terminology that the steam turbine control system vendor used for the AVR modes. SERC confirmed that the written procedures mistakenly identified “AQR mode” instead of “AVR mode” for automatic voltage control. DEP verified that the two other units on its system, which used the same control system for AVR control, had been operating in automatic voltage control mode, as required. | VAR-002-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected unit provides 12% of the generation from the Smith Energy Complex, and all of the other generators were operating in automatic voltage control mode and were reacting automatically to system conditions. In addition, the voltage schedule assigned to Smith Energy Complex had been maintained throughout the violation period. | 8/2/2007 (when the Standard became mandatory and enforceable) | 9/26/2012 (when the AVR was put in automatic voltage control mode) | 0 | Self-Report | To mitigate this violation, DEP: 1) placed the AVR into the correct mode; 2) updated the operating procedure to reflect the correct mode; 3) removed the AQR mode as an operator selection for the AVR control system at the Smith Energy Complex; and 4) verified that all of the AVRs in generating units owned by DEP were operating in the TOP-directed mode. In addition, DEP will remove the AQR mode as an operator selection for any other AVR control systems having that option. | 8/30/2013 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed DEP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. At the time of the violation and self-reporting, DEP followed the documented ICP of its parent company, Progress Energy. The ICP was initially approved on December 13, 2007, and it was developed to document and drive existing compliance business practices. DEP’s compliance program was disseminated to all organizations within DEP that must comply with NERC Standards. The ICP was prepared for and approved by Progress Energy’s Electric Reliability Organization (ERO) Steering Committee. The ERO Steering Committee was comprised of officers of DEP and Progress Energy Florida and was chaired by the ERO compliance officer, who was Progress Energy’s executive vice president – general counsel and corporate secretary. The ERO compliance officer was independent of all DEP organizations that must comply with NERC Standards. The ERO compliance officer reported directly to the chairman/president/chief executive officer and had direct access to the Board of Directors. Company officers participated in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments. A Settlement Agreement covering a violation of VAR-002-1 R3 for Progress Energy Carolinas (former name of DEP) was filed with FERC under NP13-27-000 on February 28, 2013. On March 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that the prior violation should not serve as a basis for aggravating the penalty because the facts and circumstances did not involve conduct that is the same or similar to the instant case. Moreover, there was nothing in the record to suggest that broader corporate issues were implicated.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2012011582 | Settlement Agreement | On December 13, 2012, TVA submitted a Self-Report to SERC stating that, as a Transmission Owner, it was in violation of PRC-023-2 R1. TVA did not use any of the Standard's criteria for a specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System for all fault conditions. TVA had previously identified that spare breakers 5054 and 5074 were not set to meet PRC-023-1 criteria. However, TVA failed to reset the spare breakers before they were placed into service. On November 2, 2012, the Johnsonville Breaker 5084 for the Johnsonville- Davidson 500 kV line terminal had an unplanned outage and spare breaker 5074 was put into service but it was not set to meet PRC-023-1 criteria. After further assessment, TVA discovered that breaker 5054 had been placed into service on December 8, 2011 but it was also not set to meet the Standard's criteria. Each relay can spare out two 500 kV lines, for a total of four spare 500 kV lines. Three 500 kV lines could have been impacted: Johnsonville- Davidson, Johnsonville-Cumberland, and Johnsonville-Jackson. The fourth line, the Johnsonville-Gleason line, could not have been impacted because it has not been spared out since PRC-023-1 went into effect. | PRC-023-1 | R1 | High | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The highest peak load recorded on the Johnsonville-Davidson 500 kV line during the time period at issue never exceeded 17% of the trip setting, indicating the likelihood the setpoints would not have limited loadability. The highest peak load recorded on the Johnsonville-Cumberland 500 kV line during the time period at issue never exceeded 26% of the trip setting, indicating the likelihood the setpoints would not have limited loadability. The highest peak load recorded on the Johnsonville-Jackson 500 kV line during the time period at issue never exceeded 50% of the trip setting, indicating the likelihood that the setpoints would not have limited loadability. | 12/8/2011 (when TVA first put breaker 5054 into service) | 11/20/2012 (when the spare breakers were set to meet PRC-023-1 criteria) | 13000 | Self-Report | To mitigate this violation, TVA: 1) removed relay tripping as an interim measure; 2) issued relay setting sheets with the appropriate PRC-023 R1 relay loadability margin and implemented the revised relay settings; 3) issued and processed relay rating sheets with the applicable PRC-023 R1 subrequirement and communicated the changes to the Transmission Operator (TOP); 4) provided SERC with an updated PRC-023 applicable facilities list; and 5) added SharePoint between the applicable departments to increase the TOP's awareness of the PRC-023 review status of all of the applicable lines including spare breaker protection. To mitigate this violation, TVA will: 1) update the applicable processes and procedures to outline the use of SharePoint with regard to PRC-023 applicable line status and describe how to mitigate future lines that may not have spare breaker reviews complete for PRC-023; and 2) provide training on the new procedures and the new tools to all applicable departments. | 2013-11-01 | TBD | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TVA's documented ICP was initially approved in July 2008 and was developed to establish formally the structure of TVA’s compliance program. TVA’s compliance program is disseminated to all business units responsible for compliance with NERC Standards. TVA’s chief operating officer (COO) approves and is responsible for the compliance program. TVA’s vice-president of transmission planning and compliance oversees the management and operation of the compliance program. The COO reports to the chief executive officer and has direct access to TVA’s Board of Directors. TVA's Reliability Standards compliance oversight group, which provides guidance and oversight of TVA’s Reliability Standards compliance program, meets monthly and is comprised of vice-presidents and senior management. A Settlement Agreement covering a violation of PRC-023-1 R1 for TVA was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that TVA's previous violation of PRC-023-1 R1 constituted a prior violation and was an aggravating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Kansas City Power & Light Company (KCP&L) | NCR01107 | SPP2013012093 | Settlement Agreement | On March 8, 2013, KCP&L submitted a Self-Report to SPP RE stating that, as a Balancing Authority, it was in violation of BAL-005-0 R16. SPP RE determined that at two of its 90 (2.22%) data sampling locations, KCP&L failed to sample data at least at the same periodicity with which its Area Control Error (ACE) is calculated. KCP&L’s ACE calculation requires that sampling locations be sampled at a four-second periodicity. However, data sampling was occurring at a ten-second periodicity at two secondary sampling locations. | BAL-005-0 | R16 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In addition to involving 2.22% of KCP&L’s sampling locations, KCP&L provided evidence that despite the periodicity deviations, KCP&L’s calculation of control performance standard 1 (CPS1) changed marginally following the correction of the sampling rates (from approximately 115% to 114%). This change established that CPS1 was still above 100% (the minimum acceptable long-term score for CPS1, of which ACE is a direct input). Additionally, once the deviations were identified on January 4, 2013, KCP&L immediately took action to mitigate the deviations, and KCP&L had corrected all deviations by January 4, 2013. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/4/2013 (Mitigation Plan completion) | 0 | Self-Report | To mitigate this violation, KCP&L corrected the identified sampling periodicity deviations and will continue to conduct an annual review of sampling periodicity going forward. | 2013-01-04 | 2013-05-31 | Neither Admits nor Denies | SPP RE reviewed KCP&L's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. KCP&L and its affiliate KCPL - Greater Missouri Operations (KCPL-GMO) share the same compliance program, including compliance policies and procedures. Additionally, KCPL-GMO’s compliance responsibilities are performed by KCP&L staff. The ICP of KCP&L and KCPL-GMO includes eight full-time employees dedicated to compliance. Six employees are dedicated to FERC and NERC compliance and two employees are dedicated to CIP compliance. Additionally, KCP&L/KCPL-GMO enlists the participation of over 200 employees who support compliance as a function of their assigned job responsibilities. Internally, compliance activities are governed by the chief compliance officer and the corporate compliance committee. The committee reports to the KCP&L/KCPL-GMO leadership team. The chief compliance officer reports to the president and chief executive officer as well as maintains independent access to Great Plains Energy’s (KCP&L/KCPL-GMO's parent company) board of directors. The ICP at KCP&L/KCPL-GMO is widely disseminated within the two operating companies. In support of its ICP, KCP&L/KCPL-GMO: 1) have an intranet site that all employees can access that provides information about the Standards associated with the ICP; 2) conduct frequent working group meetings with operations personnel and CIP personnel to discuss NERC compliance; 3) hold periodic executive workshops with compliance participants; 4) communicate to employees via e-mail and newsletters regarding emerging compliance related issues; and 5) provide relevant training to necessary personnel regarding CIP standards. Additionally, KCP&L/KCPL-GMO perform self-audits to identify potential compliance problems. A Settlement Agreement covering a prior violation of BAL-005-0 R16 (SPP2012010529) for KCP&L was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Due to the shared compliance programs of KCP&L and KCPL-GMO, SPP RE considers prior KCPL-GMO violations to be relevant to the penalty determination for KCP&L’s violations. A Settlement Agreement covering a prior violation of BAL-005-0 R16 (SPP2012010530) for KCPL-GMO was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE evaluated the prior violations of BAL-005-0 R16 (SPP2012010529 and SPP2012010530) to determine if aggravation of the instant penalty was appropriate due to the repetitive infraction of BAL-005-0 R16 in the instant violation (SPP2013012093). SPP RE determined that the prior violations should not serve as a basis for aggravating the penalty because the instant violation SPP2013012093 was identified and self-reported via an annual internal control mechanism established by KCP&L during the mitigation of SPP2012010529 and SPP2012010530. The Self-Report of SPP2012010529 and SPP2012010530 identified scanning rates affecting remote terminal units, whereas the established internal control identified additional backup inter-control center communications protocol scanning rates. The effectiveness of the internal control and subsequent behavior of KCP&L to timely self-report and mitigate the possible non-compliance is “indicative of a culture of compliance[,]” and therefore, because SPP RE seeks to encourage such behavior, SPP RE did not assess a penalty for the instant violation, despite the similarities between the past and present violations.
Southwest Power Pool Regional Entity (SPP RE) | KCPL - Greater Missouri Operations (KCPL-GMO) | NCR01058 | SPP2013012092 | Settlement Agreement | On March 8, 2013, KCPL-GMO submitted a Self-Report stating that, as a Balancing Authority, it was in violation of BAL-005-0 R16. SPP RE determined that at two of its 66 (3.03%) data sampling locations, KCPL-GMO failed to sample data at least at the same periodicity with which its Area Control Error (ACE) is calculated. KCPL-GMO's ACE calculation requires that sampling locations be sampled at four-second periodicity. However, data sampling was occurring at a ten-second periodicity at one secondary sampling location, and sampling was not occurring at one primary location. | BAL-005-0 | R16 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In addition to involving 3.03% of KCPL-GMO’s sampling locations, KCPL-GMO provided evidence that despite the periodicity deviations, KCPL-GMO’s calculation of control performance standard 1 (CPS1) changed marginally following the correction of the sampling rates (from approximately 119% to 105%). This change established that CPS1 was still above 100% (the minimum acceptable long-term score for CPS1, of which ACE is a direct input). Additionally, once the deviations were identified on January 4, 2013, KCPL-GMO immediately took action to mitigate the deviations, and KCPL-GMO had corrected all deviations by January 4, 2013. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/4/2013 (Mitigation Plan completion) | 0 | Self-Report | To mitigate this violation, KCPL-GMO corrected the identified sampling periodicity deviations and will continue to conduct an annual review of sampling periodicity going forward. | 2013-01-04 | 2013-05-31 | Neither Admits nor Denies | SPP RE reviewed KCPL-GMO's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. KCPL-GMO and its affiliate Kansas City Power & Light Company (KCP&L) share the same compliance program, including compliance policies and procedures. Additionally, KCPL-GMO’s compliance responsibilities are performed by KCP&L staff. The ICP of KCP&L and KCPL-GMO includes eight full time employees dedicated to compliance. Six employees are dedicated to FERC and NERC Compliance and two employees are dedicated to CIP compliance. Additionally, KCP&L/KCPL-GMO enlists the participation of over 200 employees who support compliance as a function of their assigned job responsibilities. Internally, compliance activities are governed by the chief compliance officer and the corporate compliance committee. The committee reports to the KCP&L/KCPL-GMO Leadership team. The chief compliance officer reports to the president and chief executive officer as well as maintains independent access to Great Plains Energy’s (KCP&L/KCPL-GMO's parent company) board of directors. The ICP at KCP&L/KCPL-GMO is widely disseminated within the two operating companies. In support of its ICP, KCP&L/KCPL-GMO: 1) have an intranet site that all employees can access that provides information about the Standards associated with the ICP; 2) conduct frequent working group meetings with operations personnel and CIP personnel to discuss NERC compliance; 3) hold periodic executive workshops with compliance participants; 4) communicate to employees via e-mail and newsletters regarding emerging compliance related issues; and 5) provide relevant training to necessary personnel regarding CIP standards. Additionally, KCP&L/KCPL-GMO perform self-audits to identify potential compliance problems. A Settlement Agreement covering a prior violation of BAL-005-0 R16 (SPP2012010529) for KCP&L was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Due to the shared compliance programs of KCP&L and KCPL-GMO, SPP RE considers prior KCPL-GMO violations to be relevant to the penalty determination for KCP&L’s violations. A Settlement Agreement covering a prior violation of BAL-005-0 R16 (SPP2012010530) for KCPL-GMO was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE evaluated the prior violations of BAL-005-0 R16 (SPP2012010529 and SPP2012010530) to determine if aggravation of the instant penalty was appropriate due to the repetitive infraction of BAL-005-0 R16 in the instant violation (SPP2013012092). SPP RE determined that the prior violations should not serve as a basis for aggravating the penalty because for the instant violation SPP2013012092 was identified and self-reported via an annual internal control mechanism established by KCPL-GMO during the mitigation of SPP2012010529 and SPP2012010530. The Self-Report of SPP2012010529 and SPP2012010530 identified scanning rates affecting remote terminal units, whereas the established internal control identified additional back-up inter-control center communications protocol scanning rates. The effectiveness of the internal control and subsequent behavior of KCPL-GMO to timely self-report and mitigate the possible non-compliance is “indicative of a culture of compliance[,]” and therefore, because SPP RE seeks to encourage such behavior, SPP RE did not assess a penalty for the instant violation, despite the similarities between the past and present violations.
Southwest Power Pool Regional Entity (SPP RE) | Western Farmers Electric Cooperative (WFEC) | NCR01160 | SPP2012011039 | Settlement Agreement | On September 11, 2012, WFEC submitted a Self-Report to SPP RE stating that, as a Transmission Owner and Distribution Provider, it was in violation of PRC-008-0 R2. WFEC could not provide documents showing that 36 Under Frequency Load Shedding (UFLS) devices had been tested before being included in WFEC’s UFLS equipment maintenance and testing program. During a subsequent review, WFEC identified 16 additional UFLS devices for which testing documentation could not be provided. Following the activation of the UFLS function on the Schweitzer multi-function recloser controls in 2011, WFEC could not demonstrate that it tested the proper operation of the recloser UFLS function as required by its UFLS equipment maintenance and testing program. The identified reclosers represent 17.3% (52 of 301) of WFEC’s UFLS trip devices. | PRC-008-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WFEC’s UFLS equipment maintenance and testing program is a distribution-level program, which limits any failure to test or maintain a UFLS device to a minimal amount of load in a localized area. During the violation, no single recloser control was capable of shedding more than 4.86 MW of load under peak load conditions. Additionally, the affected recloser controls represented only 16.03% (77.16 MW of a total 481.22 MWs) of WFEC’s total load shed capability under peak load conditions, and the remaining 83.97% of WFEC’s recloser controls were tested in accordance with the UFLS equipment maintenance and testing program. Further, WFEC maintained manual load shed capability if any of the recloser controls failed to shed load. | 10/14/2011 (the date of the first occurrence of missed UFLS testing) | 2/27/2013 (Mitigation Plan completion) | 3000 | Self-Report | To mitigate this violation, WFEC: 1) tested all UFLS devices requiring testing; and 2) documented test results. | 2013-02-27 | 2013-03-25 | Neither Admits nor Denies | SPP RE reviewed WFEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WFEC is committed to a culture of regulatory compliance and reliability excellence. On June 19, 2009, WFEC adopted a documented ICP. Under its ICP, the WFEC board of trustees has delegated the responsibility and authority for NERC compliance to an internal compliance officer, who serves as the manager of WFEC compliance programs and the WFEC compliance team. The compliance officer reports to the vice president of legal and corporate services and has independent authority to report directly to the chief executive officer and the board of trustees. The compliance team is comprised of full-time employees devoted to compliance who are supported by managers and subject matter experts. The compliance team has independent reporting channels to the compliance officer and the vice president of legal and corporate services. All WFEC personnel are encouraged to notify any member responsible for NERC compliance should they discover a potential violation. A Settlement Agreement covering a violation of PRC-005-1 R2 for WFEC was filed with FERC under NP12-44-000 on August 31, 2012. On September 28, 2012, FERC issued orders stating it would not engage in further review of the Notices of Penalty. SPP RE determined that WFEC's previous violation of PRC-005-1 R2 constituted a prior violation of a closely related reliability standard and the prior violation and compliance history was considered to be an aggravating factor in the penalty determination for instant violation. SPP RE determined that the PRC-005-1 R2 violation represented an example of conduct similar to that underlying the instant violation, i.e., a failure to provide documentation of equipment testing occurring within a defined interval.
Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2011008636 | Settlement Agreement | On October 28, 2011, SCL submitted a Self-Report to WECC stating it had a violation of FAC-003-1 R2. WECC determined that SCL, as a Transmission Owner, failed to include six tie-line rights-of-way (ROW) in its transmission vegetation management plan (TVMP) and failed to implement an annual plan for vegetation management work for those six transmission lines each year from 2007 through 2010. In June 2011, the SCL customer service and energy delivery (CSED) operating division was performing a vegetation management work assignment verification process. The CSED work unit was assigned to perform vegetation management for the Boundary Plant to Boundary Switchyard (BP-BN) tie-line ROW. The CSED work unit initiated a patrol when it realized vegetation management had not occurred since 2006. At the same time, BPA was performing clearing work around its facilities located in the area, prompting the SCL Boundary Project operating division to contact the CSED vegetation management group about the BP-BN ROW. After fact finding, SCL determined that it did not include the BP-BN ROW in its TVMP annual plans because the BP-BN tie-lines were historically considered part of a hydroelectric generating project rather than discrete transmission lines. WECC subject matter experts determined that the six BP-BN tie-lines are discrete transmission lines subject to FAC-003-1 R2. | FAC-003-1 | R2 | High | High | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system. The six transmission tie lines at issue represent three miles of a total of 484 miles (0.6%) of 230 kV transmission, and one-half mile of a total of 143 miles (0.3%) of 230 kV transmission ROW that SCL owns and maintains. Each of the six lines is one-half mile in length and consists of a vertical span up a rock cliff before crossing rock, seasonal permafrost, and then a treed area. The vegetation in the area remained within SCL’s minimal vegetation clearance distances at all times. | 6/18/2007 (when the Standard became mandatory and enforceable) | 10/26/2011 (Mitigation Plan completion) | 22000 | Self-Report | To mitigate this violation, SCL: 1) patrolled and inspected the BP-BN line ROW on June 23, 2011; 2) performed vegetation management work from July 11, 2011 through July 17, 2011, and from October 17, 2011 through October 23, 2011. The June 2011 patrol established that vegetation was outside the clearance distance established by the TVMP; 5) performed work (which included tree trimming and brush clearing) in consideration of the five-year vegetation management hiatus, notwithstanding that the patrol established the vegetation was outside the clearance distance; 6) added the Boundary line ROW patrol and maintenance to its 2011 work plan; 7) entered the Boundary line ROW in its annual inspection list and work tracking system; and 8) planned to include the ROW in future work plans as conditions require. | 2011-10-26 | 2012-04-03 | Agrees/Stipulates | WECC reviewed SCL's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that SCL had a comprehensive, established, and documented internal compliance program (ICP). Further, WECC found that: 1) SCL's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; 2) the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; 3) SCL has identified and assigned responsibility and accountability to a chief compliance officer; 4) SCL has six positions fully dedicated to FERC/NERC compliance; 5) SCL's chief compliance officer has independent access to the general manager and chief executive officer; 6) SCL's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; 7) SCL has dedicated adequate resources to support its ICP; 8) SCL's ICP has the support and participation of senior management; 9) SCL's ICP includes measurable, specific compliance performance targets; 10) SCL's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; 11) SCL has distributed the ICP to all employees and, if applicable, contractors and vendors; 12) SCL has fully implemented its ICP; 13) SCL's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; 14) SCL's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; 15) SCL's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an triennial basis, annual assessments for Standards on the Actively Monitored Standards List, and annual spot-checks for Standards internally identified as high risk for SCL; 16) SCL's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; 17) SCL regularly reviews its ICP at least annually; 18) SCL's ICP includes a process to prevent recurrence of NERC Reliability Standard Violations; and 19) SCL participates in outreach compliance program activities. SCL has a prior violation of FAC-003-1 R2 which WECC considered an aggravating factor in the penalty determination. The VSL matrix for FAC-003-1 R2 does not include an option that covers the circumstances of this violation. WECC subject matter experts determined that a "High" VSL is appropriate based on the facts of the violation.
Western Electricity Coordinating Council (WECC) | Sunray Energy, Inc. (SRE) | NCR05415 | WECC2013011726 | Settlement Agreement | During a Compliance Audit conducted on November 8, 2012, WECC determined that SRE, as a Generator Owner, had a violation of PRC-005-1 R2. While reviewing the information relating to the R2 violation, WECC inquired whether SRE's Program included testing intervals or a summary of procedures that will be used to test instrument transformers. Subsequently, on January 23, 2013, SRE submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-005-1 R1. SRE failed to have a defined interval and basis for its voltage and current sensing devices (instrument transformers), and failed to have a summary of maintenance and testing procedures for its instrument transformers in its Protection System maintenance and testing program (Program). | PRC-005-1 | R1; R1.1; R1.2 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRE has an extensive documented Program for all other Protection System devices, and all other maintenance and testing records are current. In addition, SRE has thorough monitoring on its instrument transformers. Specifically, multifunction protective relays utilized to provide generator and generator step-up transformer protection provide self-checking of the associated instrument transformers. Therefore, SRE would observe faulty data indicating possible problems with the devices, which would cause SRE to perform an investigation to address the issues with the devices. | 7/3/2009 (when SRE's Program failed to include instrument transformers) | 11/29/2012 (when SRE updated its Program to include defined intervals and basis for testing and maintaining instrument transformers) | $0 (for WECC2013011726 and WECC2012011481) | Self-Report | To mitigate this violation, SRE: 1) updated its Program to reflect the new testing schedule for instrument transformers; 2) updated its Program to define a testing interval for the instrument transformers; 3) uses software for maintenance management and makes use of its preventative maintenance modules; and 4) created preventative maintenance schedules for all required instrument transformers of its generation Protection System. | 2013-01-13 | 2013-02-19 | Neither Admits nor Denies | WECC reviewed SRE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: SRE has a comprehensive, established, and documented program; SRE's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; SRE has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; SRE has at least one position partially dedicated to FERC/NERC compliance; SRE's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; SRE has dedicated adequate resources to support its ICP; SRE's ICP has the support and participation of senior management; SRE's ICP includes measurable, specific compliance performance targets; SRE's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; SRE has distributed the ICP to all employees and, if applicable, contractors and vendors; SRE has fully implemented its program; SRE's ICP includes documentation regarding compensation, awards, employee recognition, or other incentives to encourage employee compliance with NERC Reliability Standards; SRE's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; SRE's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; SRE's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; SRE regularly reviews its ICP at least annually; SRE's ICP includes a process to prevent recurrence of NERC Reliability Standard violations; and SRE participates in compliance outreach program activities. A Settlement Agreement covering a violation of PRC-005-1 R1 for SRE was filed with FERC under NP10-81-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that this prior violation should not serve as a basis for aggravating the penalty because WECC's approval of the Certification of Mitigation Plan Completion associated with the first violation of PRC-005-1 R1 perpetuated SRE's error, resulting in an ongoing violation.
Western Electricity Coordinating Council (WECC) | Sunray Energy, Inc. (SRE) | NCR05415 | WECC2012011481 | Settlement Agreement | During a Compliance Audit conducted on November 8, 2012, WECC determined that SRE, as a Generator Owner, was in violation of PRC-005-1 R2. SRE failed to provide evidence of maintenance and testing of its instrument transformers. Per SRE's Protection System maintenance and testing program (Program), SRE's instrument transformers are tested by the manufacturer prior to installation and verified during commissioning. SRE's Program further states that regular testing is not necessary and therefore not recommended unless there is evidence of a problem. The instrument transformers were tested during commissioning of the station, which occurred about March 1986. The commissioning test records were not available and were not provided to the Audit team. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRE has an extensive documented Program for all other Protection System devices, and all other maintenance and testing records are current. In addition, SRE has thorough monitoring on its instrument transformers. Specifically, multifunction protective relays utilized to provide generator and generator step-up transformer protection provide self-checking of the associated instrument transformers. Therefore, SRE would observe faulty data indicating possible problems with the devices, which would cause SRE to perform an investigation to address the issues with the devices. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/13/2013 (Mitigation Plan completion) | $0 (for WECC2013011726 and WECC2012011481) | Compliance Audit | To mitigate this violation, SRE: 1) scheduled instrument transformer testing during the protective relays and DC control circuitry maintenance and testing; and 2) performed maintenance on instrument transformers and maintained the instrument transformer testing schedule. | 2013-01-13 | 2013-02-19 | Neither Admits nor Denies | WECC reviewed SRE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: SRE has a comprehensive, established, and documented program; SRE's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; SRE has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; SRE has at least one position partially dedicated to FERC/NERC compliance; SRE's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; SRE has dedicated adequate resources to support its ICP; SRE's ICP has the support and participation of senior management; SRE's ICP includes measurable, specific compliance performance targets; SRE's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; SRE has distributed the ICP to all employees and, if applicable, contractors and vendors; SRE has fully implemented its program; SRE's ICP includes documentation regarding compensation, awards, employee recognition, or other incentives to encourage employee compliance with NERC Reliability Standards; SRE's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; SRE's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; SRE's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; SRE regularly reviews its ICP at least annually; SRE's ICP includes a process to prevent recurrence of NERC Reliability Standard Violations; and SRE participates in compliance outreach program activities.