## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Northeast Power Coordinating Council, Inc. (NPCC) | Consolidated Edison Co of NY, Inc (Con Edison) | NCR07046 | NPCC2012010875 | Notice of Confirmed Violation | On June 13, 2012, NPCC notified Con Edison that NPCC would be performing a Spot Check of Con Edison's compliance with PRC-005-1. On July 13, 2012, Con Edison reported the violation to NPCC. While gathering evidence for the Spot Check, Con Edison determined that from 2009 through 2011, for several months each year, monthly testing of telecommunication system channels for nine transmission lines was not documented. Monthly testing has been properly documented since July 2011. Prior to July 2011, Con Edison did not perform some of the required monthly tests or was unable to demonstrate testing was completed because the monthly testing was being tracked and documented using an Excel file that was being overwritten rather than saved separately. Testing documentation was missed for 18 out of 113 (15.9%) communication systems. NPCC determined that Con Edison, as a Transmission Owner (TO), had a violation of PRC-005-1 R2.1 for failing to provide evidence that its Protection System devices were maintained and tested within defined intervals. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, the failure to perform monthly testing created the risk of not knowing whether the carrier system would operate properly for external faults, potentially resulting in a misoperation. The risk to the BPS was mitigated by the following factors. From June 2009 to July 2011, Con Edison was performing some testing on the lines, just not on a monthly basis. Furthermore, high speed clearing on both the primary and secondary lines of protection was in service at all times, providing proper clearing for circuit faults. The primary line protection for this line is provided by a directional comparison carrier blocking scheme utilizing an on/off power line carrier system. This system provides high speed tripping or line faults between the substation terminals. The protection at each terminal is set to determine whether a detected fault is internal or external to the transmission line. If the fault is determined to be external by either terminal, a carrier signal is sent and high speed tripping is blocked. This specific system lacks an automatic check-back feature and therefore requires monthly manual testing. The secondary line protection is provided by a permissive overreaching transfer trip scheme. This system also provides high speed tripping for lines faults between the two terminals. This system utilized frequency shift keying of audio tone via leased line. The guard signal is continuously monitored, and any loss of guard alarm is transmitted to the system control center via a Supervisory Control and Data Acquisition system. There is also a direct transfer trip scheme via dual-channel frequency shift power line carrier providing overall backup for breaker failure. At no point would the line have been unprotected even if the power line carrier equipment had experienced a failure. | 6/21/2007 (when Con Edison registered as a TO) | 7/1/2011 (Mitigation Plan completion) | 0 | Spot Check | To mitigate this issue, Con Edison: 1) implemented a more rigorous process to ensure the monthly carrier checks were performed and documented; 2) held meeting to discuss mitigation plan for PRC-005; 3) finalized naming convention for the 26 transmission line carrier entries into the Maximo database (Con Edison's work management system with automatic task tracking, scheduling, and reporting capabilities); 4) completed the 26 transmission line carrier entries into the Maximo database; 5) developed Maximo tutorial for the performance of carrier testing. | 2012-07-01 | 2013-06-24 | Admits | NPCC considered that this is the first incident of violation by Con Edison of any NERC Reliability Standard. NPCC reviewed Con Edison's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Con Edison has a ICP in place that is supported and engaged by senior management. Con Edison has a training program in place for compliance staff as well as all employees responsible for compliance with NERC Standards. In addition, Con Edison has a program in place for employees to report possible compliance issues confidentially without fear of retaliation through an "Ethics Hotline." NPCC also considered Con Edison's cooperation as a mitigating factor in assessing the penalty. NPCC assessed a $0 penalty because Con Edison admitted to the violation. In addition, the protective relay systems associated with the transmission facilities were being tested in accordance with their protective relay maintenance programs to ensure that clearing would be proper for a fault on the line. Furthermore, NPCC considered the fact that since July 2011, Con Edison has been performing the monthly testing as required.
ReliabilityFirst Corporation (RF) | NAES Corporation - Chesapeake (Chesapeake) | NCR10234 | RFC2012011215 | Settlement Agreement | On October 3, 2012, Chesapeake submitted a Self-Certification stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1 R2. Chesapeake failed to maintain its generator voltage as directed by its Transmission Operator (TOP) (Chesapeake’s voltage schedule is 139.5 kV +/- 3.5kV). Chesapeake determined that it does not have the capability to monitor voltage directly at the high side 138 kV level or collect historical data to demonstrate compliance with VAR-002-1 R2, and therefore it may have operated outside its voltage schedule. From October 15, 2012 through October 26, 2012, RF conducted a Compliance Audit of Chesapeake (the “Compliance Audit”) during which RF confirmed the facts detailed in Chesapeake’s Self-Certification of VAR-002-1 R2. Also during the Compliance Audit, Chesapeake provided RF with evidence it received from its Transmission Owner (TO) of high side voltage which demonstrated that Chesapeake operated outside its voltage schedule from 15:21 p.m. to 17:48 p.m. on July 8, 2011. | VAR-002-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because Chesapeake is located in a high voltage area due to a deficiency of generators' leading reactive capability. Because of the relatively small size of Chesapeake’s generating units, it has very little ability to influence voltage levels. There are numerous occasions when Chesapeake’s generating units are offline and voltage at the point of interconnection is significantly above Chesapeake’s voltage schedule. Additionally, from the commencement of operations, Chesapeake’s TO and TOP have known: 1) the design configuration and operating parameters and physical limitations of Chesapeake; 2) that Chesapeake has no capability to monitor voltage directly on the high side of its generator step-up transformer; and 3) that Chesapeake has sought a revised voltage schedule or exemption more consistent with operating conditions. Finally, during the duration of the violation, neither Chesapeake’s TO nor its TOP directed Chesapeake to modify its voltage output. In the event the voltage was too far out of range, it is expected that the TOP would have contacted Chesapeake to rectify the voltage issue. However, as Chesapeake is often used for voltage support, the TOP has never contacted Chesapeake to reduce high side voltage. | 3/14/2008 (when Chesapeake registered as a GOP) | present | 0 | Self-Certification | To mitigate this violation, Chesapeake will: 1) configure its Digital Control System to monitor high side system voltage at the point of interconnection; 2) develop a written procedure for its operations personnel to follow in the event Chesapeake operates outside its assigned voltage schedule; 3) provide training to its operators on how and when to notify its TOP in the event that Chesapeake has reached its maximum equipment capabilities and is still above or below the limits specified in its voltage schedule; and 4) complete, implement, and verify the implementation of, the new procedure. | 7/19/2014 (approved completion date) | TBD | Neither Admits nor Denies | RF reviewed Chesapeake's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty assessment. RF favorably considered certain aspects of Chesapeake’s ICP. For instance, Chesapeake distributes its ICP to all individuals that have direct or indirect responsibility for compliance with the Reliability Standards. Additionally, Chesapeake’s ICP is reviewed and updated annually and when revisions to NERC Reliability Standard Requirements occur. Finally, Chesapeake conducts annual training on Reliability Standards and NERC policies. RF utilized its discretion to assess a zero dollar penalty for this violation because it considered the fact that Chesapeake is located in a high voltage area with limited ability to affect voltage levels. RF also considered Chesapeake's effort to attain an exemption or expanded voltage schedule from its TOP and Chesapeake's willingness to implement alternative mitigating actions to address the violation. When assessing the penalty for the alleged violations at issue in this Agreement, RF considered whether the facts of these alleged violations evidenced (a) repeated or continuing conduct similar to that underlying the prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. Neither Chesapeake nor its affiliated Registered Entities have any prior alleged violations of the same or closely-related Reliability Standards. A Settlement Agreement covering violations of VAR-002-1 R1 an R2 for NAES Corporation - Burney, an affiliate of Chesapeake, was filed with FERC on September 30, 2011 in NP11-270-000. On October 28, 2011, FERC issued an order stating that it would not engage in further review of the Notice of Penalty. RF determined that this affiliated Registered Entity's prior violations should not serve as a basis for aggravating the penalty because NAES Corporation - Burney violations and Chesapeake's violation were concurrent and therefore not aggravating.
Southwest Power Pool Regional Entity (SPP RE) | Duke Energy Generation Services, Inc. (DEGS) | NCR11241 | SPP2012011537 | Settlement Agreement | On December 14, 2012, DEGS submitted a Self-Report to SPP RE stating that, as a Generator Operator (GOP), it was in violation of TOP-001-1a R3. DEGS did not comply with a reliability directive issued by its Transmission Operator (TOP) for approximately one hour. On October 1, 2012, at 4:49 p.m., the TOP for DEGS, Kansas City Power & Light Company (KCP&L), called a DEGS dispatch operator and issued a directive from KCP&L’s Reliability Coordinator (RC) requiring DEGS to curtail the output of a 131 MW wind generating facility in Kansas from 51 MW to 33 MW. The DEGS dispatch operator documented the directive, but erroneously curtailed a DEGS facility in Pennsylvania by 18 MW rather than the Kansas facility. At 5:41 p.m., KCP&L contacted DEGS and reissued the same reliability directive, at which time DEGS properly curtailed the Kansas generation facility from 51 MW to 33 MW and subsequently released the curtailment on the Pennsylvania generation facility. | TOP-001-1a | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DEGS did not immediately curtail generation at the Kansas facility pursuant to a reliability directive given by its TOP. Because DEGS curtailed generation at its Pennsylvania facility rather than the Kansas facility, it did not address the real-time issue that was occurring on the transmission system, thereby posing a risk to both the Pennsylvania and Kansas transmission systems. However, the violation did not pose a serious or substantial risk to the BPS because the amount of generation to be curtailed was 18 MW, which was minimal compared to the DEGS RC’s peak system load of 30,962 MW. DEGS did perform the proper curtailment 52 minutes after the initial directive was received. | 10/1/2012 (when DEGS failed to follow the directive from the TOP) | 10/1/2012 (when DEGS followed the directive from the TOP) | $4,500 | Self-Report | To mitigate this violation, DEGS: 1) retrained the dispatch operator involved in operating procedures; 2) implemented an end of shift summary report that is distributed via email to all dispatch operators and includes information on curtailments; 3) distributed lessons learned from the incident and required all dispatch operators to review; 4) required all dispatch operators to review the power scheduling and operating procedures as well as the Siemens supervisory control and data acquisition (SCADA) training; and 5) made process improvements in the SCADA/NERC compliance training procedures to include additional steps for verification of curtailment, and implemented a new process that requires the completion of refresher training when a dispatch operator returns from an extended absence. | 2013-04-01 | 2013-05-02 | Neither Admits nor Denies | SPP RE reviewed DEGS' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. DEGS is subject to Duke Energy Corporation's (DEC) corporate-wide ICP. The DEC ICP consists of well-defined processes and procedures for compliance with the NERC Reliability Standards. Roles and responsibilities are well-defined, and information regarding the ICP is widely disseminated across the organization and to DEC affiliates via a quarterly newsletter addressing internal matters as well as general Reliability Standards information. DEC frequently reviews and updates its ICP, which is subject to internal audit. DEC formed its Steering Committee for its ICP in 2009, which meets monthly for the purpose of enhancing the culture of compliance across the DEC companies and to provide guidance and oversight to the ICP. In May 2013, DEC revamped its ICP following its merger with Progress Energy, Inc. to integrate the existing compliance programs of the two companies. A Settlement Agreement covering violations of TOP-001-1 R3 for DEGS was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE determined that this prior violation should not serve as a basis for aggravating the penalty because the prior violation, which occurred nearly three and half years prior to the instant violation, involved a reliability directive that DEGS initially complied with but became non-compliant with after an hour. The instant violation involved an attempt by DEGS to comply with a directive, but DEGS failed to initially comply due to a mistake by personnel.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Public Service Co. (Xcel Energy) (SPS) | NCR01145 | SPP201100630 | Settlement Agreement | On July 12, 2011, SPS submitted a Self-Report to SPP RE stating that, as a Distribution Provider, Generator Owner, and Transmission Owner, it was in violation of PRC-023-1 R1. SPS set one relay on a 230 kV line terminal to operate at or below 150% of the highest seasonal Facility Rating of the circuit for the available defined loading duration nearest four hours. Specifically, the relay setting exceeded the PRC-023-1 R1.1 load limit when using the capacity of two connected auto-transformers. SPS found an additional three relays during the course of mitigation that had incorrect settings. The four relays that had incorrect settings were protecting three SPS transmission lines. | PRC-023-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Out of 444 relays on the SPS system, only four relays had incorrect settings. Because the relay settings of the four relays were more conservatively set below 150%, they were in violation of PRC-023-1 R1, but equipment was adequately protected from damage due to faults. | 7/1/2010 (when the Standard became mandatory and enforceable) | 5/16/2012 (Mitigation Plan completion) | $25,000 (for SPP201100630 and SPP2012011057) | Self-Report | To mitigate this violation, SPS: 1) corrected the settings for all relays that were not in compliance; 2) implemented a new peer review process for the determination and issuance of relay settings; and 3) trained all relevant personnel on the new process. | 2012-05-16 | 2012-12-19 | Neither Admits nor Denies | SPP RE reviewed SPS's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of PRC-023-1 R1 in the WECC region for an affiliate of SPS, Public Service Company of Colorado, was filed with FERC under NP12-26-000 on April 30, 2012. On May 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE determined that this prior violation should not serve as a basis for aggravating the penalty because the instant violation is not recurring conduct. The present violation was discovered shortly after the violation in the WECC region was discovered, and both violations began on the mandatory and enforceable date of the Standard.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Public Service Co. (Xcel Energy) (SPS) | NCR01145 | SPP2012011057 | Settlement Agreement | On September 14, 2012, SPS submitted a Self-Report to SPP RE stating that, as a Generator Operator, it was in violation of VAR-002-1.1b R3. SPS did not notify its Transmission Operator (TOP) as soon as practical or within 30 minutes of a change in the status of the automatic voltage regulator (AVR) for one of its generators on two occasions between July 7, 2012 and July 11, 2012. On July 8, 2012 at 2:15 a.m., SPS system operators received alarms indicating there was high voltage at the cooling tower transformer and 4160 volt source transformer at the Cunningham generating plant. At 5:49 a.m., SPS found, in the course of investigating the alarms, that the AVR for one of the Cunningham generators (Cunningham Unit 2) was in manual mode. SPS immediately informed its TOP of the AVR's status. At 6:03 a.m., SPS switched the AVR back to automatic mode and notified its TOP. SPS determined that the AVR had automatically switched to manual mode as a result of the AVR being turned on prior to closing the field breaker to connect the generator to the grid following a maintenance outage on July 7, 2012. Additionally, the distributed control system (DCS) “VR Not Auto” (Voltage Regulator not automatic) alarm did not function to alert SPS system operators that the AVR had switched to manual mode. SPS later discovered that the alarm was not configured properly. In response to the July 8, 2012 incident, SPS reactivated the AVR “common alarm” that had been previously deactivated during the commissioning of the AVR in March 2012. The common alarm is a generic alarm indicating a problem with the AVR, requiring the operator to investigate further to discover the specific cause of the alarm. On July 11, 2012, at 10:40 a.m., an SPS operator was examining the AVR local panel at the Cunningham plant and noticed that the AVR for the same generating unit had again switched to manual mode. SPS notified its TOP at 10:41 a.m. that the AVR was in manual mode. SPS switched the AVR back to automatic mode and notified the TOP of the change at 10:42 a.m. SPS determined that personnel had switched the AVR back to manual mode using the DCS. SPS believed it had resolved the alarm issue by reactivating the common alarm following the resolution of the first instance on July 8, 2012. However, the common alarm did not function to alert the system operators upon the change from manual to automatic mode. | VAR-002-1.1b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the duration of the violation, the Cunningham generating station bus voltage ranged from 231 kV to 234.3 kV, staying within the System Operating Limits (SOLs) of 230 kV plus or minus five percent (218.5 kV – 241.5 kV). No emergency action was required during either instance. Although the TOP had not been timely informed of the change in status of the AVR, the violation period was less than five days, and over that time period the station bus voltage only varied by 3.4 kV. If the voltage had reached a SOL, alarms would have notified SPS system operators so that corrective action could be taken. Over the duration of the violation, no operator contingency plans were in place that relied on Cunningham Unit 2 or its AVR. Cunningham Unit 2 was operating at between 153 MW to 173 MW at peak hour on these days, compared to the 4,546 MW to 5,323 MW peak hour TOP system loads. In addition, at all times during this period, at least one of SPS’s other three Cunningham station generating units (all of which have AVRs) was in operation with its AVR in automatic mode. Furthermore, SPS verified that all of the other AVRs at its generating plants had functioning DCS alarms in place that would have immediately alerted system operators if an AVR was switched into manual mode. | 7/7/2012 (the date the first instance occurred) | 7/11/2012 (the date the TOP was informed regarding the second instance) | $25,000 (for SPP201100630 and SPP2012011057) | Self-Report | To mitigate this violation, SPS: 1) reactivated the inhibited "common alarm" and corrected the AVR status change alarm logic for Cunningham Unit 2 so that both the control room and the TOP receive the alarm; 2) developed a standardized procedure for activating (or deactivating) alarms for all SPS plants and trained the relevant personnel on the procedure; 3) installed a permissive (a setting in the control system) so that the AVR on Cunningham Unit 2 cannot be turned on unless the field breaker is closed; 4) added a step to the start-up procedure for Cunningham Unit 2 to include verification of machine voltage after turning on the AVR and trained plant operations personnel on the revision; 5) reviewed the events surrounding the violation, as well as the VAR-002 requirements, and provided a summary to all relevant personnel in various departments in order to educate its personnel; 6) checked to verify that all of the AVRs on the SPS system were correctly alarmed to control rooms and to the TOP; 7) provided refresher training to all operations personnel on SPS' human performance tool used to aid in preventing accidents and errors; and 8) ensured that operator action journal software (OAJ) is running in auto-start mode in the DCS and that OAJ is configured to restart on reboot. OAJ logs what operator actions are taken and when they are taken. | 2013-02-04 | 2013-04-10 | Neither Admits nor Denies | SPP RE reviewed SPS's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LDWP) | NCR05223 | WECC2012010121 | Settlement Agreement | On April 27, 2012, LDWP submitted a Self-Report to WECC stating that, as a Transmission Service Provider, it was in violation of MOD-001-1a R8. On February 24, 2012, the outage coordinator scheduled programmed outages on the Path 49 components Navajo-Crystal and Crystal-McCullough 500 kV lines, to begin on April 9, 2012 and April 16, 2012, respectively. When the outage coordinator scheduled the outage, the pre-scheduling department did not use the correct Total Transfer Capability (TTC) in the Available Transfer Capability (ATC) calculation. The correct TTC was calculated and the monthly value ATC calculation was updated by the pre-scheduling department on April 5, 2012, which was more than 28 days after the change and beyond the one week requirement of MOD-001-1a R8.3. WECC found that LDWP should have corrected its monthly ATC value within one week of March 3, 2012, when the ATC was initially calculated. WECC determined that LDWP had a violation of MOD-001-1a R8 for failing to recalculate, at the frequency of once a week, the monthly values in the ATC equation. | MOD-001-1a | R8; R8.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LDWP properly calculated the ATC prior to the scheduled outages thereby preventing any inaccurate loading of transmission lines. In addition, since the outage was scheduled, LDWP's system includes procedures for notifying others that the transmission lines would be out of service. | 3/3/2012 (when the ATC was initially calculated) | 7/9/2012 (Mitigation Plan completion) | $9,000 (for WECC2012010121 and WECC2011009031) | Self-Report | To mitigate this violation, LDWP: 1) provided updated training to applicable pre-scheduling personnel regarding the existing process of updating the TTC values and upcoming improvements to that process; 2) enhanced the outage bid document that is prepared by the outage coordinator and sent to pre-schedulers; and 3) evaluated any new or revised procedures and validated their effectiveness. | 2012-07-09 | 2/4/2013 | Agrees/Stipulates | WECC reviewed LDWP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: LDWP has a comprehensive, established, and documented program; LDWP's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; LDWP has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; LDWP has one position fully dedicated to FERC and NERC compliance; LDWP's compliance official has independent access to the chief executive officer or equivalent; LDWP's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; LDWP has dedicated adequate resources to support its ICP; LDWP's ICP has the support and participation of senior management; LDWP's ICP includes measurable, specific compliance performance targets; LDWP's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; LDWP has distributed the ICP to all employees and, if applicable, contractors and vendors; LDWP has fully implemented its program; LDWP's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; LDWP's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; LDWP's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; LDWP's ICP includes specific procedures to promote prompt detection and self-reporting of violations to WECC; LDWP regularly reviews its ICP at least annually; LDWP's ICP includes a process to prevent recurrence of NERC Reliability Standard violations; and LDWP participates in outreach compliance program activities. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with MOD-001-1a R8 for LDWP was filed with FERC under RC12-6-000 on December 30, 2011. The 60-day review period passed on February 28, 2013. WECC determined that LDWP’s previous issue with MOD-001-1a R8 was an aggravating factor in the penalty determination in that the instant violation was not filed as a FFT.
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LDWP) | NCR05223 | WECC2011009031 | Settlement Agreement | On December 23, 2011, LDWP submitted a Self-Report to WECC stating that, as a Distribution Provider, Generator Owner, and Transmission Owner, it had a violation of PRC-005-1 R2. Specifically, although LDWP’s Haynes Generating Station Unit 3 (Unit 3) was decommissioned, it had a bus stub between the high-side circuit breakers for Unit 3 that was still protected by relays. LDWP’s Protection System relay index did not identify as operational the protective relays for the small stub bus that remained in service. Due to this oversight, LDWP left the relays associated with Unit 3 off of its Protection System maintenance and testing program and never tested the relays. In addition, the breaker failure relay for the associated circuit breaker was not on the list of equipment for the Protection System maintenance and testing program and also was not tested. The last test date for relays, voltage and sensing devices, and DC circuitry for Unit 3 was June 3, 1996; the testing intervals are every four years. LDWP tested the devices on January 4, 2012, after the Self-Report was submitted. LDWP conducted further review and discovered another instance of noncompliance with PRC-005-1 R2. At LDWP’s San Francisquito Power Plant 2 (PP2), Unit #1 had been decommissioned in the late 1990s, but the generating step-up unit transformer for Unit #1 was reconnected to the power system to function as an auxiliary bank. The relays related to the auxiliary bank were left off the Protection System maintenance and testing program and were not tested. For relays, voltage and sensing devices, and DC circuitry connected to PP2, the prior test date was June 6, 1996. The testing interval was every four years, and the most recent test date was November 3, 2011. WECC determined that LDWP had a violation of PRC-005-1 R2 for failing to test certain Protection System devices in accordance with its Protection System maintenance and testing program. LDWP was required to test the relays associated with its decommissioned units because the relays were still considered active in LDWP's Protection System. In addition to Unit 3 and PP2, WECC determined that LDWP failed to include in its maintenance and testing program a battery bank associated with the Haynes Generating Unit #10-14. In total, LDWP failed to test 3 out of 1400 voltage and sensing devices; 3 out of 1400 DC circuits; 3 out of 4147 relays, and 1 out of 116 battery banks. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The stub bus network connected to Unit 3 is small, approximately 30 feet, affecting only 1% of the total bus and the exposure to fault is minimal. Also, the affected relays have been in continuous service. PP2 Unit #1 is located at the end of a 115 kV transmission circuit. Any fault on this circuit would be detected and isolated by a single radial transmission circuit and would not affect the remaining BES facilities. In addition, the affected relays have been in continuous service and only protect an auxiliary bank. In addition, the affected devices made up less than 1% of LDWP's total devices. Furthermore, LDWP had been performing maintenance and testing on a number of other Protection System devices. Regarding the Haynes Generating Unit #10-14, LDWP's maintenance and testing required maintenance and testing four times throughout the year. While LDWP failed to test on two occasions, it did perform maintenance and testing two other times during the year. | 6/18/2007 (when the Standard became mandatory and enforceable) | 7/11/2012 (Mitigation Plan completion) | $9,000 (for WECC2012010121 and WECC2011009031) | Self-Report | To mitigate this violation, LDWP: 1) performed maintenance and testing for identified Protection Systems at the Haynes Generating Units and PP2 and provided documentation of testing to WECC; 2) conducted meetings with facility managers, relay engineering, and system protection to discuss findings of the initial global review and lessons learned; and 3) updated its Protection System maintenance and testing program and performed additional verification and testing for Protection Systems identified during the initial global review (including comprehensive on-site checks) of protective relays. Approximately 3000 relays were checked. | 7/11/2012 | 7/17/2012 | Agrees/Stipulates | WECC reviewed LDWP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: LDWP has a comprehensive, established, and documented program; LDWP's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; LDWP has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; LDWP has one position fully dedicated to FERC and NERC compliance; LDWP's compliance official has independent access to the chief executive officer or equivalent; LDWP's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; LDWP has dedicated adequate resources to support its ICP; LDWP's ICP has the support and participation of senior management; LDWP's ICP includes measurable, specific compliance performance targets; LDWP's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; LDWP has distributed the ICP to all employees and, if applicable, contractors and vendors; LDWP has fully implemented its program; LDWP's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; LDWP's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; LDWP's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; LDWP's ICP includes specific procedures to promote prompt detection and self-reporting of violations to WECC; LDWP regularly reviews its ICP at least annually; LDWP's ICP includes a process to prevent recurrence of NERC Reliability Standard violations; and LDWP participates in outreach compliance program activities. WECC considered LDWP's compliance history and determined that LDWP had three prior violations of PRC-005-1 R2; however, WECC did not consider these prior violations as an aggravating factor in penalty determination because the fact and circumstances were different from the instant violation. The first prior violation resulted from LDWP's failure to maintain and test Protection System relays and associated communication systems that LDWP did not initially determine were subject to PRC-005. The second prior violation resulted from LDWP missing its interval on a device. The third prior violation resulted from LDWP's failure to test certain station batteries within defined intervals. In the instant violation, LDWP failed to test certain Protection System devices because the devices were not found within LDWP's Protection System maintenance and testing program.