## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2012010470 | Settlement Agreement | During a Compliance Audit conducted from June 4, 2012 to June 8, 2012, FRCC determined that VERO, as a Transmission Owner (TO), was in violation of FAC-008-1 R1, R1.2.1, R1.3.2, R1.3.3, R1.3.4, and R1.3.5. VERO's document was not sufficient evidence to demonstrate the method by which the Rating (of major Bulk Electric System (BES) equipment that comprises a Facility) is determined. VERO's document was not sufficient evidence to demonstrate that the scope of equipment addressed included, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. Specifically VERO did not address jumpers and substation buses (terminal equipment). VERO's document was not sufficient evidence to demonstrate that VERO considered design criteria. The design criteria was missing all components except bare overhead conductors. VERO's document considered ambient conditions, operating limitations, and other assumptions. It was missing consideration for design criteria. | FAC-008-1 | R1; R1.2.1; R1.3.2; R1.3.3; R1.3.4; R1.3.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because after considering current limiting devices, the entity found that the rating for its substation 20 was reduced by 14% after properly including the bus and jumpers in the ratings calculations. This violation was deemed to be moderate as the substation was de-rated and is the tie to the adjoining TO/Transmission Operator. The entity is a small municipal with 14 miles of 138 kV transmission (less than 1% of Regional transmission) serving 210 MW peak load and no registered generation (144 MW of non-registered generation connected at 69 kV) and because VERO is contained within a much larger Balancing Authority Florida Municipal Power Pool footprint. VERO has no Interconnection Reliability Operating Limits (IROL) transmission elements within its portion of the BES, and as such errors would more likely impact VERO's own load and non-registered generation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/28/2012 (Mitigation Plan completion) | $7,000 (for FRCC2012010470, FRCC2012010473, FRCC2012010475, and FRCC2013012559) | Compliance Audit | To mitigate this violation, VERO: 1) selected an engineering firm to develop a Facilities Ratings Methodology that meets all FAC-008-3 requirements. The Engineering Firm delivered a Facilities Ratings Methodology and facility ratings to VERO. The delivered methodology and ratings included the new FAC-008-3 document and the supporting evidence for R6; and 2) reviewed and implemented the new document that covers all requirements in FAC-008-3. | 2012-12-31 | 2013-02-27 | Neither Admits nor Denies | FRCC reviewed VERO's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. VERO has a documented ICP that was recently reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2012010473 | Settlement Agreement | During a Compliance Audit conducted from June 4, 2012 to June 8, 2012, FRCC determined that VERO, as a Transmission Operator, was in violation of PER-002-0 R1. Through interviews, it was identified that the VERO system operators are not familiar with the purpose and limitations of Protection System schemes applied in VERO's area. This demonstrates VERO did not implement the VERO training plans that state VERO's training objectives which include applying learned knowledge of all NERC standards (PRC-001-1). Therefore, this demonstrates that VERO was not staffed with adequately trained operating personnel on the topic of Protection System schemes. | PER-002-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined this violation posed a minimal risk because although VERO's operations staff was not adequately trained, and as a result might make operational errors, such errors would more likely impact VEROs own load and non-registered generation. The entity is a small municipal with 14 miles of 138 kV transmission (less than 1% of regional transmission) serving 210 MW peak load and no registered generation (144 MW of non-registered generation connected at 69 kV) and because VERO is contained within a much larger Balancing Authority (Florida Municipal Power Pool) footprint. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/31/12 (Mitigation Plan completion) | $7,000 (for FRCC2012010470, FRCC2012010473, FRCC2012010475, and FRCC2013012559) | Compliance Audit | To mitigate this violation, VERO: 1) performed training documentation improvements to PER-002 R1 EOP training documentation improvements; 2) hired a contractor to conduct training regarding the purpose and limitations of the protective systems applied in the VERO area; and 3) improved training program protective relay scheme training for PRC-001. | 2012-12-14 | 2013-05-06 | Neither Admits nor Denies | FRCC reviewed VERO's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. VERO has a documented ICP that was recently reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PER-002-0 R2 and R4 for VERO was filed with FERC under RC13-9-000 on May 30, 2013 and PER-002-0 R3 was filed in RC11-6-000 on September 30, 2011. FRCC determined that VERO's compliance history should not serve as a basis for aggravating the penalty because the requirements, facts, and circumstances of the violations are different.
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2012010475 | Settlement Agreement | During a Compliance Audit conducted from June 4, 2012 to June 8, 2012, FRCC determined that VERO, as a Transmission Operator, was in violation of PER-002-0. Through a personnel interview and review of job qualification documents, there was insufficient evidence to demonstrate that VERO’s training staff was competent in knowledge of system operations. | PER-002-0 | R3; R3.4 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because although VERO's training staff was identified and had proper instructional capabilities, the training staff's knowledge in system operations was not adequate. The entity is a small municipal with 14 miles of 138 kV transmission (less than 1% of Regional transmission) serving 210 MW peak load and no registered generation (144 MW of non-registered generation connected at 69 kV) and because VERO is contained within a much larger Balancing Authority (Florida Municipal Power Pool) footprint. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/31/12 (Mitigation Plan completion) | $7,000 (for FRCC2012010470, FRCC2012010473, FRCC2012010475, and FRCC2013012559) | Compliance Audit | To mitigate this violation, VERO: 1) added the manager, maintenance and construction to the training staff; 2) enrolled the supervisor, transmission and distribution operations and the manager, maintenance and construction into a "train the trainer" course. | 2012-12-14 | 2013-05-06 | Neither Admits nor Denies | FRCC reviewed VERO's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. VERO has a documented ICP that was recently reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PER-002-0 R2 and R4 for VERO was filed with FERC under RC13-9-000 on May 30, 2013 and PER-002-0 R3 was filed in RC11-6-000 on September 30, 2011. FRCC determined that VERO's violations of PER-002-0 R2 and R4 should not serve as a basis for aggravating the penalty because the requirements, facts, and circumstances are different. FRCC determined that VERO's prior violation of PER-002-0 R3 should serve as a basis for aggravating the penalty.
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2013012559 | Settlement Agreement | On July 1, 2013, VERO submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of EOP-008-1 R6. VERO's existing procedure, “Plans for Loss of Control Center Functionality,” meets all the requirements of EOP-008-1, except R6. VERO does not have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards in particular COM-001-1 R2, COM-002-2 R1, TOP-004-1 R1-R4, and TOP-006-1 R-R6. VERO does not have the ability to provide adequate and reliable data telecommunications internally independently from its backup facility. Specifically, VERO relies on a remote terminal located at the power plant, which is dependent on the primary control center. | EOP-008-1 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a minimal risk because VERO has no Interconnection Reliability Operating Limits (IROL) transmission elements within its portion of the Bulk Electric System (BES), and as such errors would more likely impact VERO's own load and non-registered generation. The Balancing Authority (BA) and neighboring TOPs would still have tie line telemetry to monitor the BES. The entity is a small municipal with 14 miles of 138 kV transmission (less than 1% of Regional transmission) serving 210 MW peak load and no registered generation (144 MW of non-registered generation connected at 69 kV) and because VERO is contained within a much larger BA (Florida Municipal Power Pool) footprint. | 7/1/2013 (when the Standard became mandatory and enforceable) | present | $7,000 (for FRCC2012010470, FRCC2012010473, FRCC2012010475, and FRCC2013012559) | Self-Report | To mitigate this violation, VERO will: 1) complete a request for proposal from fiber optic companies; 2) complete several fiber runs within its territory to create a self-healing fiber loop; and 3) convert an existing block building and install a separate Supervisory Control and Data Acquisition (SCADA) server independent of its primary SCADA server that will allow it to achieve full back-up functionality that does not depend on primary control center functionality. | 4/1/2014 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed VERO's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. VERO has a documented ICP that was recently reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP. FRCC considered the Self-Report Method of Discovery to be a mitigating factor in penalty determination. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with EOP-008-0 R1 was filed in RC11-6-000 on September 30, 2011. FRCC determined that VERO's compliance history should not serve as a basis for aggravating the penalty because the specific facts and circumstances were different and the previous violation ended 3.8 years ago.
ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2012011198 | Settlement Agreement | On October 1, 2012, Lakewood submitted a Self-Report stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R1. On October 11, 2012, Lakewood self-certified that it was non-compliant for the same issue. During an internal self-assessment, Lakewood discovered that it failed to include maintenance and testing intervals for voltage and current sensing devices in its Protection System maintenance and testing program, as required by PRC-005-1b R1.1. Lakewood failed to include adequate summaries of maintenance and testing procedures for voltage and current sensing devices and direct current control circuitry in its Protection System maintenance and testing program, as required by PRC-005-1 R1.2. | PRC-005-1 | R1; R1.1; and R1.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because Lakewood has alarming in place to indicate when a fault occurs. This may be a direct alarm from the Protection System or an alarm from the isolation device indicating that an issue exists. Local flags exist on the electromechanical and lockout relays to identify the activated devices. These alarms are continuously in service, and Lakewood continuously monitors them. In addition, Lakewood represents that it performed maintenance and testing on the batteries at issue, though there are no testing documents for these devices for several testing intervals. | 8/28/2008 (when Lakewood was registered as a GO) | present | $0 (for RFC2012011198, RFC2012011199, and RFC2013011965) | Self-Report | To mitigate this violation, Lakewood will: 1) determine all equipment missing from the maintenance and testing program; and 2) review all owners’ manuals and applicable standards, update all relevant documentation, and communicate those updates to its staff. | 12/13/2013 (approved completion date) | TBD | Admits | ReliabilityFirst reviewed Lakewood's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Lakewood is subject to its parent company's (Essential Power) compliance program, which is a well-documented and widely disseminated program within Lakewood. The ICP is managed and operated independently from those departments responsible for ensuring compliance with NERC's Reliability Standards. Furthermore, the chief compliance officer supervises the ICP and has independent access to the chief executive officer and the Board of Directors. A Settlement Agreement covering violations of VAR-002-1 R1, VAR-002-1.1b R2 and PRC-005-1 R1 and R2 for EP Ocean Peaking Power, LLC was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R1 and R2 for EP Rock Springs, LLC was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst determined that the prior violations by Lakewood's affiliates should not serve as a basis for aggravating the penalty because the violations occurred concurrently and all Essential Power facilities are subject to the same compliance program, and therefore operate to a common set of policies and procedures. Therefore, once an issue arises with one facility, the remaining facilities will most likely have the same issue. As a result, ReliabilityFirst did not consider a single issue at multiple plants to constitute repetitive issues. This includes Lakewood’s PRC-005-1 violation and its VAR-002-1.1a R2 violation. Once Essential Power identified the issue at one facility, it investigated its other facilities and filed Self-Reports for Lakewood as well. As a result, ReliabilityFirst did not consider Lakewood’s violation history in the penalty determination as an aggravating factor as understanding the root cause and the extent of a violation, which is essential to the mitigation of risk, is a desired proactive behavior.
ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2012011199 | Settlement Agreement | On October 1, 2012, Lakewood submitted a Self-Report stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. On October 11, 2012, Lakewood self-certified that it was non-compliant for the same issue. During an internal self-assessment, Lakewood discovered that it cannot locate maintenance and testing records for 60 of its 180 batteries (33%), all of its 173 voltage and current sensing devices, and all of its 9 direct current control circuits. As a result, Lakewood cannot demonstrate that it performed maintenance and testing on these devices and cannot provide the date it last performed maintenance and testing on these devices, as required by PRC-005-1 R2.1. | PRC-005-1 | R2; R2.1; and R2.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the duration of the violation and the number of devices at issue for which Lakewood could not provide maintenance and testing records. ReliabilityFirst determined that the violation posed a moderate risk because Lakewood has alarming in place to indicate when a fault occurs. This may be a direct alarm from the Protection System or an alarm from the isolation device indicating that an issue exists. Local flags exist on the electromechanical and lockout relays to identify the activated devices. These alarms are continuously in service, and Lakewood continuously monitors them. In addition, Lakewood represents that it performed maintenance and testing on the batteries at issue, though there are no testing documents for these devices for several testing intervals. | 8/28/2008 (when Lakewood was registered as a GO) | present | $0 (for RFC2012011198, RFC2012011199, and RFC2013011965) | Self-Report | To mitigate this violation, Lakewood will: 1) determine all equipment missing from the maintenance and testing program; and 2) review all owners’ manuals and applicable standards, update all relevant documentation to ensure that it is line with the requirement and establishes the expectations to maintain compliance with respect to maintenance and testing on a continuous basis, and communicate those updates to its staff. Further, Lakewood will inspect the excluded equipment for the potential of near-term failure and any required immediate corrective actions will be taken as needed. | 12/13/2013 (approved completion date) | TBD | Admits | ReliabilityFirst reviewed Lakewood's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Lakewood is subject to its parent company's (Essential Power) compliance program, which is a well-documented and widely disseminated program within Lakewood. The internal compliance program is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the Chief Compliance Officer supervises the internal compliance program and has independent access to the Chief Executive Officer and the Board of Directors. When assessing the penalty for the alleged violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these alleged violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The instant alleged violations are Lakewood’s first violations of PRC-005-1 and VAR-002-1.1a R2. Entities affiliated with Lakewood have previous violations of PRC-005-1 and VAR-002-1.1a R2. A Settlement Agreement covering violations of VAR-002-1 R1, VAR-002-1.1b R2 and PRC-005-1 R1 and R2 for EP Ocean Peaking Power, LLC was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R1 and R2 for EP Rock Springs, LLC was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst determined that the prior violations by Lakewood's affiliates should not serve as a basis for aggravating the penalty because the violations occurred concurrently and all Essential Power facilities are subject to the same compliance program, and therefore operate to a common set of policies and procedures. Therefore, once an issue arises with one facility, the remaining facilities will most likely have the same issue. As a result, ReliabilityFirst did not consider a single issue at multiple plants to constitute repetitive issues. This includes Lakewood’s PRC-005-1 issues and its VAR-002-1.1a R2 issue. Once Essential Power identified the issue at one facility, it investigated its other facilities and filed self reports for Lakewood as well. As a result, ReliabilityFirst did not consider Lakewood’s violation history in the penalty determination as an aggravating factor as understanding the root cause and the extent of a violation, which is essential to the mitigation of risk, is a desired proactive behavior.
ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2013011965 | Settlement Agreement | On February 18, 2013, Lakewood submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1a R2. During an internal self assessment, Lakewood discovered that it was unable to provide evidence that it maintained the generator voltage schedule as directed by its Transmission Operator (TOP) prior to the installation of its current data storage medium, Pi Historian, on July 19, 2011. In addition, after the installation of Pi Historian, Lakewood discovered that on several occasions, it failed to comply with the voltage schedule provided by its TOP because the metering for the Lakewood voltage was difficult to see. The metering is located behind a lot of items and not easily seen by the operators making it difficult for the operators to know they were not following their voltage schedule. On November 11, 2012, Lakewood exceeded the 238.185 kV voltage limit by 1.02%, and on December 5, 2012, Lakewood exceeded the limit by 0.2%. | VAR-002-1a | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the duration of the violation and Lakewood's failure to recognize that it must demonstrate compliance with the Requirement. These factors increased the likelihood that Lakewood would have a voltage excursion that impacted grid reliability. ReliabilityFirst determined that the violation posed a moderate risk because during the two voltage excursions, which were relatively minor excursions, the Automatic Voltage Regulator was in automatic voltage control mode. In addition, during the two voltage excursions, voltage did not exceed PJM Interconnection, LLC’s (PJM) normal high voltage limit of 242 kV, nor did the excursions trigger any notifications or directives from either PJM or the interconnected Transmission Owner. | 8/28/2008 (when Lakewood was registered as a GO) | 8/30/2013 (Mitigation Plan completion) | $0 (for RFC2012011198, RFC2012011199, and RFC2013011965) | Self-Report | To mitigate this violation, Lakewood: 1) installed Pi Historian; 2) will install visual alarms on Pi Historian so operators can see when Lakewood is operating outside the voltage schedule; and 2) will update its VAR-002 procedure to reflect the operational changes, and notify all operating staff of the changes. | 2013-08-30 | TBD | Admits | ReliabilityFirst reviewed Lakewood's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Lakewood is subject to its parent company's (Essential Power) compliance program, which is a well-documented and widely disseminated program within Lakewood. The internal compliance program is managed and operated independently from those departments responsible for ensuring compliance with Reliability Standards. Furthermore, the Chief Compliance Officer supervises the internal compliance program and has independent access to the Chief Executive Officer and the Board of Directors. ReliabilityFirst also considered that it discovered the violations through self reports and applied mitigating credit. Effective oversight of the reliability of the bulk power system depends on robust and timely self reporting by Registered Entities. Lakewood identified and reported the violations at issue in this Agreement due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self reporting, characterized by spontaneous detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these alleged violations. When assessing the penalty for the alleged violations at issue in this Agreement, ReliabilityFirst considered whether the facts of these alleged violations constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. The instant alleged violations are Lakewood’s first violations of PRC-005-1 and VAR-002-1.1a R2. Entities affiliated with Lakewood have previous violations of PRC-005-1 and VAR-002-1.1a R2. A Settlement Agreement covering violations of VAR-002-1 R1, VAR-002-1.1b R2 and PRC-005-1 R1 and R2 for EP Ocean Peaking Power, LLC was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R1 and R2 for EP Rock Springs, LLC was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst determined that the prior violations by Lakewood's affiliates should not serve as a basis for aggravating the penalty because the violations occurred concurrently and all Essential Power facilities are subject to the same compliance program, and therefore operate to a common set of policies and procedures. Therefore, once an issue arises with one facility, the remaining facilities will most likely have the same issue. As a result, ReliabilityFirst did not consider a single issue at multiple plants to constitute repetitive issues. This includes Lakewood’s PRC-005-1 issues and its VAR-002-1.1a R2 issue. Once Essential Power identified the issue at one facility, it investigated its other facilities and filed self reports for Lakewood as well. As a result, ReliabilityFirst did not consider Lakewood’s violation history in the penalty determination as an aggravating factor as understanding the root cause and the extent of a violation, which is essential to the mitigation of risk, is a desired proactive behavior.
ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (RRP) | NCR03009 | RFC2013012075 | Settlement Agreement | On February 27, 2013, RRP submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. RRP reported that, due to its misunderstanding of what it means to be "fully monitored," it failed to perform testing as required by PRC-005-1 for certain DC control circuitry. Specifically, RRP believed that its entire facility qualified as “fully monitored” as described in the NERC Technical Reference document RRP uses as its basis for DC circuitry testing. Fully-monitored protection systems can require less on-site testing to be compliant with PRC-005. RRP’s program relied on monitoring for DC control circuitry. However, in preparation for a Compliance Audit, RRP performed a self-assessment of its PRC-005 compliance and identified nine of 142 relays that are electromechanical and therefore, not fully monitored (electromechanical relays are not capable of self-monitoring; the NERC Technical Reference self-monitoring levels assume microprocessor-based relaying). As a result, RRP failed to maintain and test the DC control circuitry associated with those nine relays. | PRC-005-1 | R2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Nine out of 142, or six percent, of RRP’s DC control circuitry devices were not maintained or tested as required by the Standard. RRP’s facility is protected by a distributed control system architecture, which contributes to reliability by isolating malfunctioning system components. RRP experienced no misoperations on any of the Protection System equipment through the duration of the violation, and all relays were tested and monitored according to RRP’s Protection System maintenance and testing program, in addition to the continuous monitoring on all but nine of the relays. Lastly, RRP’s 349 MW output passes through two substations, each providing additional protection in the event of a failure of relaying at RRP’s facility. | 12/8/2009 (when RRP registered as a GO) | 12/10/2012 (when RRP modified its maintenance and testing programs to include the DC control circuitry) | $0 (for RFC2013012163 and RFC2013012075) | Self-Report | To mitigate this violation, RRP modified its Protection System maintenance and testing program to include intervals and a summary table for DC control circuitry devices. RRP will schedule and perform testing of the DC control circuitry associated with the relays that were thought to be fully monitored. | 4/4/2014 (approved completion date) | TBD | Admits | ReliabilityFirst reviewed RRP's internal compliance program and considered certain aspects of it to be mitigating factors in the penalty determination. For example, RRP employees receive annual training on NERC compliance-related topics, and RRP conducts internal compliance reviews with NAES Corporation staff and reviews its compliance program annually.
ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (RRP) | NCR03009 | RFC2013012163 | Settlement Agreement | On February 27, 2013, RRP submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. RRP reported that, due to its misunderstanding of what it means to be "fully monitored," it failed to perform testing as required by PRC-005-1 for certain DC control circuitry. Specifically, RRP believed that its entire facility qualified as “fully monitored” as described in the NERC Technical Reference document RRP uses as its basis for DC circuitry testing. Fully-monitored protection systems can require less on-site testing to be compliant with PRC-005. RRP’s program relied on monitoring for DC control circuitry. However, in preparation for a Compliance Audit, RRP performed a self-assessment of its PRC-005 compliance and identified nine of 142 relays that are electromechanical and therefore, not fully monitored (electromechanical relays are not capable of self-monitoring; the NERC Technical Reference self-monitoring levels assume microprocessor-based relaying). As a result, RRP failed to maintain and test the DC control circuitry associated with those nine relays. Because RRP believed all of its DC circuitry was subject to full protection system monitoring, it did not include maintenance and testing intervals in its program for those devices. Therefore, ReliabilityFirst extended RRP’s Self-Report to include a violation of PRC-005-1 R1. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Nine out of 142, or six percent, of RRP’s DC control circuitry devices were not maintained or tested as required by the Standard. RRP’s facility is protected by a distributed control system architecture, which contributes to reliability by isolating malfunctioning system components. RRP experienced no misoperations on any of the Protection System equipment through the duration of the violation, and all relays were tested and monitored according to RRP’s Protection System maintenance and testing program, in addition to the continuous monitoring on all but nine of the relays. Lastly, RRP’s 349 MW output passes through two substations, each providing additional protection in the event of a failure of relaying at RRP’s facility. | 12/8/2009 (when RRP registered as GO) | 12/10/2012 (when RRP modified its maintenance and testing programs to include the DC control circuitry) | $0 (for RFC2013012163 and RFC2013012075) | Self-Report | To mitigate this violation, RRP modified its Protection System maintenance and testing program to include intervals and a summary table for DC control circuitry devices. RRP will schedule and perform testing of the DC control circuitry associated with the relays that were thought to be fully monitored. | 4/4/2014 (approved completion date) | TBD | Admits | ReliabilityFirst reviewed RRP's internal compliance program and considered certain aspects of it to be mitigating factors in the penalty determination. For example, RRP employees receive annual training on NERC compliance-related topics, and RRP conducts internal compliance reviews with NAES Corporation staff and reviews its compliance program annually.
ReliabilityFirst Corporation (ReliabilityFirst); Southwest Power Pool Regional Entity (SPP RE); Texas Reliability Entity, Inc. (Texas RE) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (ReliabilityFirst); Public Svc. Co. Of Oklahoma & SW Ele Pwr Co. (SPP RE); AEP Texas North Co, AEP Texas Central Co, and Public Service of Oklahoma (Texas RE) (AEP) | NCR00682; NCR01056; NCR04006 | RFC2012010261; SPP2012010129; TRE2012010184 | Settlement Agreement | On May 1, 2012, AEP submitted Self-Reports to the Regions stating that, as a Transmission Owner (TO) and Generator Owner (GO), it was in violation of PRC-005-1 R2. AEP failed to include evidence that certain Protection System devices were maintained and tested within the defined intervals. AEP has separate Protection System maintenance and testing programs for AEP Transmission and AEP Generation. During an inventory review pursuant to a revision to its transmission Protection System maintenance and testing program, AEP Transmission discovered that it failed to perform maintenance and testing within the defined intervals on 20 of 20,326 relays, 2 of 1,428 associated communications systems, and 889 of 20,326 voltage and current sensing devices in ReliabilityFirst; 133 of 5,386 voltage and current sensing devices, 28 of 5,386 relays, 3 of 12,707 direct current control circuits, and 3 of 462 associated communications systems in SPP RE; and 40 of 4,546 relays, 3 of 324 associated communications systems, and 353 of 4,546 voltage and current sensing devices in Texas RE. During a review of maintenance and testing activities completed since AEP revised and expanded its Generation Protection System maintenance and testing program, AEP Generation discovered that it had not performed maintenance and testing on one of its direct current control circuits and four protective relays. Upon further review, AEP Generation identified that it had not performed maintenance and testing on an additional seven direct current control circuits and four protective relays in accordance with its Protection System maintenance and testing program. In addition, AEP Generation discovered that it did not have historic records of maintenance and testing activities for one battery in ReliabilityFirst and two batteries in SPP RE. AEP Generation also discovered that it had not performed maintenance and testing on one battery in ReliabilityFirst and one battery in SPP RE within the defined intervals. When AEP Generation conducted an inventory of all of its Protection System devices, it determined that it had missed maintenance and testing on 7 of 870 direct current control circuits, 4 of 2,079 protective relays, and 2 of 90 batteries in ReliabilityFirst and 1 of 300 direct current control circuits, 4 of 738 protective relays, and 3 of 49 batteries in SPP RE. AEP determined that the cause of the violations was that Protection System devices were not properly classified in AEP's asset tracking database. As a result, the devices were not being identified for maintenance and testing. On November 23, 2011, AEP experienced a Misoperation at its Diana substation in SPP RE. The Misoperation occurred when a relay tripped unnecessarily, and no resulting loss of load occurred. AEP failed to perform maintenance and testing on the direct current control circuit paths associated with this relay due to improper identification in AEP’s asset tracking database. Although AEP determined that testing may have prevented the Misoperation, failure to perform maintenance and testing was not the cause of the Misoperation. | PRC-005-1 | R2 | High | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to perform maintenance and testing on Protection System devices increases the likelihood of adverse impact to reliability when faults occur. The duration of this violation increased the risk of realizing this adverse impact. However, the Regions determined that the violation posed a moderate risk because AEP has backup and/or redundant protection in place for devices at certain locations. AEP inspected the AEP Transmission facilities containing the devices at issue at least every 90 days as a part of other maintenance activities, during which AEP reviews the facilities and equipment for abnormal conditions. In addition, the AEP Generation facilities containing the devices at issue are manned locations where individuals are more likely to observe malfunctioning or at-risk equipment where possible. In addition, while three of the batteries at issue lacked historic records, AEP was maintaining and testing these batteries at the time of discovery. Thus far, AEP has found all of the devices tested to be in working condition. | ReliabilityFirst, SPP RE: 6/18/2007 (when the Standard became mandatory and enforceable) Texas RE: 6/28/2007 (the date AEP registered as a TO and GO) | present | $0 (for RFC2012010261, SPP2012010129, and TRE2012010184) | Self-Report | To mitigate this violation, AEP will: 1) develop a discussion guide pertaining to the AEP Transmission Protection System maintenance and testing program, identify transmission personnel, and complete distribution of the discussion guide to applicable transmission protection and control personnel; 2) complete an inventory of transmission carrier and relays and complete and schedule applicable maintenance and testing activities on the identified Protection System devices; and 3) develop and deploy training for plant staff on the AEP Transmission Protection System maintenance and testing program. In addition, AEP will create a bar coding inventory system to track Protection System devices. To mitigate this violation, AEP will take certain actions to mitigate the violation in ReliabilityFirst and SPP RE only: 1) develop and deploy training for plant staff on the AEP Generation Protection System maintenance and testing program; 2) review generation batteries to ensure that all applicable batteries are identified; and 3) schedule newly-identified batteries for maintenance and testing. | 4/15/2014 (approved completion date) | TBD | Admits | The Regions reviewed AEP’s internal compliance program (ICP) and considered it to be a mitigating factor. AEP’s compliance officer has independent access to the chief executive officer, executive committee, and board of directors. In addition, AEP’s reliability compliance committee is responsible for ensuring implementation and oversight of AEP’s ICP. The NERC Compliance Steering Committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. AEP’s ICP provides an annual schedule of standards to review and internal assessments of compliance by each affected business unit and by independent staff, such as internal audits and regulatory services. AEP also utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. The Regions also considered that they discovered the violations through Self-Reports and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self reporting by Registered Entities. AEP identified and reported most of the violations described here due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. AEP Transmission has internal systems in place to identify data inconsistencies and thereby discover gaps such as the instant violations. AEP Transmission uses queries and reviews to search for data inconsistencies, reviews these reports for completeness and accuracy, and applies changes to a dashboard that is refreshed daily and is accessible to all employees. These queries informed AEP that it had identified inaccurately the instrument transformers in the asset tracking database. Since the discovery of these instrument transformers, AEP has clarified the asset tracking database for this component type and facilitated the appropriate scheduling and tracking of maintenance and testing activities. Similarly, AEP Generation discovered the control circuits and protective relays through an internal corporate engineering controls process. These efforts include reviewing maintenance and testing evidence to ensure completeness and accuracy and review of daily unit status reports to identify generating unit liabilities that may impact applicable Protection Systems. The Regions determined that a monetary penalty is not warranted for the violations. This is in part based on AEP's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. AEP’s discoveries also led to its inventory efforts and the discovery of the extent of condition. In its Mitigation Plan, AEP committed to strengthening its internal controls by creating and implementing a bar coding inventory system to track Protection System devices. AEP continuously looks for opportunities to find potential gaps in its measures to improve its assurance of compliance with the Reliability Standards. Furthermore, AEP has recognized the need to develop controls aligned with the unique needs of the individual functional entities. The Regions seek to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations. The Regions considered that the present violation constitutes AEP's fifth violation of PRC-005-1 R2. AEP has previous violations of PRC-005-1 R2 in the Regions with similar facts and circumstances as the instant PRC-005-1 R2 violations (see, e.g., NP12-30-000 (filed May 30, 2012)). As a result, the Regions considered AEP’s violation history as an aggravating factor in the penalty determination. The Regions are committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. AEP's response to the violations is behavior that the Regions seek to encourage, as these are proactive steps to prevent recurrence of noncompliance. Therefore, despite AEP's compliance history, and in light of the lower risk posed by the instant violations and AEP's improvements following the findings, the Regions determined that a monetary penalty was not necessary or appropriate in this case, as it would neither incent desired behavior nor improve the reliability of the BPS.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2013012257 | Settlement Agreement | On April 17, 2013, TVA submitted a Self-Report to SERC stating that, as a Generator Owner (GO), it was in violation of PRC-005-1b R2 because it could not locate maintenance and testing records for 29 protective relay devices to demonstrate that maintenance and testing was performed on those devices. On May 20, 2013, May 21, 2013, and twice on May 29, 2013, TVA submitted additional Self-Reports to SERC stating that, as a GO and Transmission Owner, it was in violation of PRC-005-1 R2 and PRC-005-1b R2 because Protection System devices were not maintained or tested within the defined intervals. SERC determined that these violations were related to the initial April 17, 2013 Self-Report and decided to treat the subsequent Self-Reports as an expansion of scope. In the first instance, the contractor that last performed the required maintenance activities in June 2011 did not include calibration test reports in a maintenance report for 29 of 81 protective relays at the Caledonia Combined-Cycle site. Upon further investigation, the contractor and TVA could not locate documentation to demonstrate that it had conducted maintenance on the 29 protective relays. TVA discovered this failure while conducting a review of Protective System devices during a project to transfer asset work processes from one internal organization to another. TVA was able to demonstrate that the remaining 52 protective relays had been tested and calibrated within the defined intervals. In the second instance, TVA did not perform the preventive maintenance (PM) for the quarterly inspection of the 250 V station battery 1 and battery charger at the Sequoyah Nuclear Plant within the required interval and did not approve an extension. TVA was required to complete or extend the deadline for the PM prior to February 26, 2013. TVA, however, did not complete the PM until March 15, 2013, 17 days later. In the third instance, TVA did not perform the PM for the quarterly inspection of two 250 V DC batteries at Widows Creek Units 7 and 8 within the defined interval and grace period. In the fourth instance, TVA did not designate the 161 kV transmission bus differential relay at Paradise Fossil Plant Unit 1 as a NERC-defined protective relay in TVA’s work management system. As a result, TVA did not test or maintain the relay within the defined interval for TVA’s protective relays subject to PRC-005. TVA had previously tested the relay on March 24, 2005, and it should have retested it within four years, with a one-year grace period, pursuant to TVA’s Protection System maintenance and testing program. In the fifth instance, TVA completed the incorrect battery PM on July 18, 2012 at the Hamilton Mississippi Switching Station inspection, completing a 6-month inspection, instead of a 12-month inspection. As a result, TVA failed to perform procedural requirements described in TVA’s Transmission Protective System Maintenance and Test Program to verify the following items: voltage of each cell and battery terminal voltage; inter-cell/inter-unit connection integrity; and inter-cell and intra-cell impedance. TVA reports owning 20,906 protective relays, 1,374 associated communication systems, 28,259 voltage and current sensing devices, 568 station batteries, and 20,906 DC control circuits. Of these Protection System devices, TVA maintained or tested 30 out of 20,906 protective relays (0.143%) and 4 out of 568 station batteries (0.704%) outside of the defined intervals. In total, TVA maintained or tested 34 out of 72,013 Protection System devices (0.047%) outside of the defined intervals. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 29 protective relays at the Caledonia Combined-Cycle plant have backup relays that are designed to operate if the primary relays fail. The 29 protective relays would send alarms to the control room if actuated, and no alarms have issued since May 2007. TVA performed all other PMs for the Sequoyah Nuclear Plant Station Battery 1 despite its failure to perform the PM for the battery and battery charger within the defined interval at the start of 2013. TVA’s previous quarterly battery PMs on Widows Creek Units 7 and 8 250 V DC batteries found no problems. TVA’s previous test on the Paradise Fossil Plant Unit 1 relay was conducted on March 24, 2005 and found no problems. In addition, the differential relay has a redundant differential relay protective system that is designed to operate if the primary differential relay fails. TVA installed the Hamilton Mississippi Switching Station battery in 2010 and TVA completed the initial 12-month inspection on June 15, 2011. In addition, TVA completed 6-month PMs on the battery as scheduled. TVA subsequently tested all the missed Protection System devices and found no problems. | 3/25/2010 (the day after the maintenance and testing of the Paradise Fossil Unit 1 relay should have been completed) | 6/5/2013 (when TVA completed and documented the appropriate testing or maintenance that had been missed) | 24000 | Self-Report | To mitigate this violation, TVA: 1) performed the applicable quarterly PM activities to the Sequoyah Nuclear Plan Station Battery 1; 2) performed the applicable PM activities to the Widows Creek Fossil Plan Units 7 and 8 batteries; 3) reviewed all crew designations associated with NERC PM activities at Widows Creek Fossil Plant; 4) confirmed the identification of NERC PM activities in the work management system for Widows Creek Fossil Plant and began monthly review of PM reports; 5) performed the Hamilton Level 2 Inspection PM; 6) issued a letter from TVA's general manager of regional coal operations to coal generation system engineers instructing them to conduct walk-downs of system components to identify Protection System equipment; 7) performed the Paradise Fossil Plant Unit 1 differential relay PM; 8) completed retesting of the 29 Caledonia Combined-Cycle Plant protective relays with missing documentation; 9) developed Protection System PM redundant monitoring by coal and gas operations generation engineering to track and trend NERC PMs; and 10) reviewed and verified PM performance dates for Browns Ferry and Watts Bar stations to confirm planned PM work orders support required PM intervals. To mitigate this violation, TVA will: 1) revise the TVA nuclear power group's Protection System maintenance and testing program summary to specify PM performance verification requirements, including monthly updates of performance interval verifications; 2) improve the TVA nuclear power group's performance verification requirements for each PM to list the maximum interval allowed and include calculations of intervals and grace periods, performed and planned, based on actual PM and work order dates; 3) develop and implement a change management plan to communicate the impact of actions completed as part of this Mitigation Plan; 4) review its PM procedure to identify whether changes need to be made to the items relevant to NERC within the PM program; 5) complete the review and revision of its protective relay systems maintenance program to outline responsibility of maintenance data review; 6) communicate manual work order entry requirements to affected personnel; and 7) complete TVA's Protection System asset inventory, including the last maintenance and testing dates and the defined maintenance and testing intervals, and communicate it to SERC. | 10/15/2013 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TVA's documented ICP was initially approved in July 2008 and was developed to formally establish the structure of TVA's ICP. TVA’s ICP is disseminated to all business units responsible for compliance with NERC Reliability Standards. TVA’s chief energy delivery officer (CEDO) approves and is responsible for the ICP. TVA’s vice-president of transmission reliability engineer and controls (TREC) oversees the management and operation of the ICP. The CEDO reports to the chief executive officer and has direct access to TVA’s Board of Directors. The Reliability Standards compliance oversight group, which provides guidance and oversight for TVA’s Reliability Standards compliance program, meets monthly and is comprised of vice-presidents and senior management from the business units responsible for compliance with the NERC Reliability Standards. A Notice of Confirmed Violation covering a violation of PRC-005-1 R2 for TVA was filed with FERC under NP09-36-000 on September 25, 2009. On October 23, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering two violations of PRC-005-1 R2 for TVA was filed with FERC under NP10-180-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2 for TVA was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered TVA's previous violations of PRC-005-1 R2 as an aggravating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP201100631 | Settlement Agreement | On July 25, 2011, EDE submitted a Self-Report to SPP RE stating that, as a Transmission Owner and Generation Owner, it was in violation of PRC-005-1 R1. EDE’s written protection system maintenance and testing program (Program) did not include instrument transformers, DC control circuitry, or batteries. As a result, EDE’s Program did not include 628 out of a total of 1,697 Protection System devices (37%). | PRC-005-1 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Instrument transformers were only visually inspected and were not being tested. EDE’s Program provided testing intervals and procedures for protective relays and communications systems. Although the Program did not include DC control circuitry and batteries, EDE was performing testing of DC control circuitry and batteries during the violation period. EDE experienced no device failures or misoperations related to the devices that were not included in the program during the violation time frame. | 6/18/2007 (when the Standard became mandatory and enforceable) | 8/24/2012 (Mitigation Plan completion) | $9,000 (for SPP201100631, SPP201100632, and SPP201100649) | Self-Report | To mitigate this violation, EDE revised its Program to include maintenance and testing procedures and testing intervals for all Protection System devices and to improve compliance documentation and retention of maintenance and testing records. | 2012-08-24 | 2013-01-17 | Neither Admits nor Denies | SPP RE reviewed EDE's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP201100632 | Settlement Agreement | On July 25, 2011, EDE submitted a Self-Report to SPP RE stating that, as a Transmission Owner and Generation Owner, it was in violation of PRC-005-1 R2. Due to a loss of electronic media, EDE lost evidence of maintenance and testing for 30 of its 1,017 protective relays. SPP RE determined that, in addition to the self-reported violation, EDE’s documented protection system maintenance and testing program (Program) did not include testing procedures or provide a testing interval for instrument transformers from June 18, 2007 to August 24, 2011. As a result, SPP RE determined that EDE did not comply with PRC-005-1 R2 for its 491 instrument transformers. In addition, EDE was unable to demonstrate that four of EDE’s 102 DC control circuits were tested. In total, EDE was not compliant with PRC-005-1 R2 for 525 of its 1,697 Protection System devices. | PRC-005-1 | R2; R2.1; R2.2 | High | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although testing evidence was lost for 30 protective relays, EDE attested that the relays were tested pursuant to the defined intervals in its Program. EDE’s instrument transformers were not monitored or alarmed, but were being visually inspected. EDE attested that it had experienced no device failures or mis-operations during the violation time frame as a result of the failure to timely maintain and test the instrument transformers. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/30/2013 (Mitigation Plan completion) | $9,000 (for SPP201100631, SPP201100632, and SPP201100649) | Self-Report | To mitigate this violation, EDE tested all devices that were out of compliance and implemented a new database system for maintaining protective system testing records. | 2013-04-30 | 2013-05-28 | Neither Admits nor Denies | SPP RE reviewed EDE's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 for EDE (SPP201000338) was filed with FERC on September 28, 2012. SPP RE determined that this prior violation should not serve as a basis for aggravating the penalty because SPP20100338 related to an occurrence in which a small number of batteries were not tested within defined intervals. SPP201100632 involves: 1) an issue with the testing program itself regarding instrument transformers and DC control circuitry; and 2) an instance of loss of testing evidence for a small number of relays.
Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP201100649 | Settlement Agreement | On July 27, 2011, EDE submitted a Self-Report to SPP RE stating that, as a Distribution Provider, it was in violation of PRC-008-0 R2. EDE was unable to provide evidence of maintenance and testing for two of its 30 Under Frequency Load Shed (UFLS) relays. EDE reported that the electronic media where EDE stored the records was lost. | PRC-008-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although EDE was unable to locate records for two of its 30 UFLS records due to a media failure, EDE had a documented UFLS maintenance and testing program and was testing its UFLS equipment pursuant to its program. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/30/2013 (Mitigation Plan completion) | $9,000 (for SPP201100631, SPP201100632, and SPP201100649) | Self-Report | To mitigate this violation, EDE implemented a new method for maintaining and storing evidence of UFLS protection system test results, effective January 1, 2010. The new method utilizes a secure central database hosted on a central server. EDE ensured that testing of all devices was current and within defined testing intervals. | 2013-04-30 | 2013-05-28 | Neither Admits nor Denies | SPP RE reviewed EDE's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Service Corp. As Agent For Public Svc. Co. Of Oklahoma & SW Ele Pwr Co. (AEP) | NCR01056 | SPP201100625 | Settlement Agreement | On April 22, 2011, SPP RE conducted a Spot Check of AEP to review compliance with specific Reliability Standards, including TOP-002-2, because of an ice storm event that occurred in parts of AEP’s service territory between January 28, 2010 and February 2, 2010. SPP RE determined that AEP, as a Balancing Authority and Transmission Operator, was noncompliant with TOP-002-2 R19 because the affected substation Supervisory Control and Data Acquisition (SCADA) online display viewed by AEP transmission operators did not reflect removal of a 69 kV transmission line and associated line switch that was decommissioned in 2002. Therefore, the substation SCADA online display incorrectly showed that the line and switch were operational. AEP failed to maintain accurate computer models utilized for analyzing and planning system operations. | TOP-002-2 | R19 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Because an inaccurate system configuration was displayed by AEP’s SCADA system, there was a risk that AEP system operators would respond inappropriately to planned system switching or to unplanned system events. The identified one-line display error was related with a 69 kV line – a radial line carrying one distribution feed with a 7.5 MVA transformer. AEP is unaware of any impact to the system or operations resulting from its noncompliance. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2/5/2010 (Mitigation Plan completion) | $53,000 (for SPP201100625 and SPP201100627) | Spot Check | To mitigate this violation, AEP: 1) updated its energy management system (EMS) to reflect the decommissioned 69 kV transmission line and switch; and 2) confirmed that its SCADA online display reflects accurate system conditions. | 2010-02-05 | 2011-12-07 | Neither Admits nor Denies | SPP RE considered certain aspects of AEP’s compliance program as mitigating factors. AEP’s compliance officer has independent access to the chief executive officer, Executive Committee, and Board of Directors. In addition, AEP’s Reliability Compliance Committee is responsible for ensuring implementation and oversight of AEP’s program to comply with Reliability Standards. The NERC Compliance Steering Committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. AEP’s compliance program provides an annual schedule of Standards to review and internal assessments of compliance by each affected business unit and by independent staff such as internal audits and regulatory services. AEP utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. Furthermore, AEP’s tools and training enable employees to comply with Reliability Standards. Moreover, AEP developed committees that meet at least weekly to discuss BPS reliability and compliance issues. Another mitigating factor was the positive degree and quality of AEP’s cooperation and remedial action during the enforcement process. AEP was cooperative throughout its interactions with SPP RE in connection with the violations and also promptly submitted effective mitigation plans to remediate the violation.
Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Service Corp. As Agent For Public Svc. Co. Of Oklahoma & SW Ele Pwr Co. (AEP) | NCR01056 | SPP201100627 | Settlement Agreement | On June 21, 2011, AEP submitted a Self-Report to SPP RE stating that, as a Balancing Authority, it was in noncompliance with INT-006-3 R1. Upon further review of the facts and circumstances, SPP RE determined that AEP was noncompliant with INT-006-3 R1 because it failed to evaluate and respond to six Reliability Adjustment Requests for Interchange (Reliability Adjustment RFI) electronic tags (e-Tags) (hereinafter, Reliability Adjustment RFI e-Tag(s) or e-Tag(s)) in order to transition the Arranged Interchanges to Confirmed Interchanges prior to the expiration of the reliability assessment period. On February 6, 2011, the Southwest Power Pool Interchange Authority (SPP IA) distributed a Reliability Adjustment RFI e-Tag to AEP for hourly curtailment to relieve projected transmission contingency loading due to a transmission loading relief (TLR) event. As a Balancing Authority, AEP had up to ten minutes to evaluate (e.g., conduct a reliability assessment) the requested interchange (R1.1) and respond to SPP IA by transitioning the Arranged Interchange to a Confirmed Interchange (R1). However, the AEP operator responsible for evaluating and responding to the requested interchange did not initially notice the pending e-Tag on the operating console; as a result, the operator failed to evaluate and respond to the e-Tag within the prescribed ten-minute time period. The operator had another application screen on his montior which covered up the e-Tag approval screen. Consequently, the e-Tag curtailment was passively denied in accordance with industry e-Tag standards. Within the hour, another Reliability Adjustment RFI e-Tag was issued affecting the same TLR flowgate. The operator evaluated the e-Tag and responded to SPP IA by transitioning the Arranged Interchange to a Confirmed Interchange within the ten-minute time period. At three minutes prior to the ramp expiration, the operator contacted SPP IA to re-submit the curtailment request. Ultimately the AEP operator manually initiated the curtailment request through the NERC electronic tagging process only seven minutes after the originally desired ramp implementation expiration. On May 19, 2011, the SPP IA distributed a batch of five separate Reliability Adjustment RFI e-Tags for hourly curtailment reallocation, based on transmission service priority, to relieve projected transmission contingency loading due to a TLR 3A event. Again the operator responsible for evaluating and responding to the Arranged Interchanges did not initially notice the pending e-Tags on the operating console, and as a result, failed to evaluate and respond to the e-Tags within the ten-minute time period. Consequently, the e-Tag curtailment reallocations were passively denied. The following hour, another batch of Reliability Adjustment RFI e-Tags was issued affecting the same TLR flowgate. The operator evaluated the e-Tags and responded to SPP IA by transitioning the Arranged Interchanges to Confirmed Interchanges within the ten-minute time period. | INT-006-3 | R1.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All Reliability Adjustment RFI e-Tags involved curtailment of transmission loading due to TLR events. Curtailments of transmission loading for such events provide anticipated load relief to prevent entities from violating their transmission system limits, e.g., System Operating Limits (SOL) and Interconnection Reliability Operating Limits (IROL). Therefore, AEP’s violation presented a risk that the TLR events could have impaired or degraded the reliability of those transmission systems directly and/or indirectly interconnected to AEP’s transmission systems. There are other controls and monitoring mechanisms in place outside the electronic interchange scheduling curtailment process via Reliability Coordinator (RC) oversight, including other forms of congestion management, and actively monitored RC controls and directives, that are implemented to prevent potential negative reliability impact. AEP was able to obtain curtailment of transmission loading on the affected flowgates by responding to subsequent Reliability Adjustment RFI e-Tags and transitioning the Arranged Interchanges to Confirmed Interchanges within the prescribed ten-minute timeline. The actual impact of AEP’s February 6, 2011 instance was 1 MW of flow on the affected flowgate for 26 minutes. The actual impact of the May 19, 2011 instances totaled 17 MW of flow on the affected flowgate for 60 minutes. Consequently, these small load flows impacted a small percentage of the overall congestion on the transmission lines and were easily absorbed by the BPS. | 2/6/2011 and 5/19/2011 (when the operator(s) failed to evaluate and respond to the e-Tags within the ten-minute time periods) | 2/6/2011 and 5/19/2011 (when the operator(s) evaluated and responded to the e-Tags) | $53,000 (for SPP201100625 and SPP201100627) | Self-Report | To mitigate this violation, AEP: 1) verbally counseled all affected personnel by discussing the instances and the Mitigation Plan; 2) circulated a memo to all affected personnel directing them to continually monitor and use their operator screens to identify and respond to pending RFT e-Tags; and 3) developed and conducted additional training for all affected personnel that reinforced the counseling and circulated memo. | 2011-10-07 | 2011-12-06 | Neither Admits nor Denies | SPP RE considered certain aspects of AEP’s compliance program as mitigating factors. AEP’s compliance officer has independent access to the chief executive officer, Executive Committee, and Board of Directors. In addition, AEP’s Reliability Compliance Committee is responsible for ensuring implementation and oversight of AEP’s program to comply with Reliability Standards. The NERC Compliance Steering Committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. AEP’s compliance program provides an annual schedule of Standards to review and internal assessments of compliance by each affected business unit and by independent staff such as internal audits and regulatory services. AEP utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. Furthermore, AEP’s tools and training enable employees to comply with Reliability Standards. Moreover, AEP developed committees that meet at least weekly to discuss BPS reliability and compliance issues. Another mitigating factor was the positive degree and quality of AEP’s cooperation and remedial action during the enforcement process. AEP was cooperative throughout its interactions with SPP RE in connection with the violations and also promptly submitted effective mitigation plans to remediate the violation.
Western Electricity Coordinating Council (WECC) | Alameda Municipal Power (APAT) | NCR10042 | WECC2012011407 | Settlement Agreement | On November 13, 2012, APAT submitted a Self-Report to WECC stating that, as a Distribution Provider (DP), it was in violation of PRC-005-1 R1. APAT did not establish a complete protection system maintenance and testing program for certain Protection System devices connected to its system. Specifically, APAT's maintenance and testing program did not include, for DC control circuitry, intervals for testing and their basis or a summary of maintenance and testing procedures. APAT reported that its system had two load areas, both of which were served from radial lines, and that a normally-open switch existed between the two radial lines that fed the two load areas. APAT reported that the switch is closed (creating a looped system) only for maintenance purposes. APAT explained that, upon its registration in 2007, it interpreted the NERC Registration Criteria as placing its relays outside the scope of PRC-005. However, after receiving additional training, APAT determined that part of its system could be considered Bulk Electric System facilities, and accordingly, APAT submitted a Self-Report citing non-compliance with PRC-005-1 R1. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although APAT's lack of a maintenance and testing program for certain Protection System devices increased the likelihood that the devices would not function properly or as intended, APAT had established procedures for coordinating potential failures with its Transmission Operator, thereby decreasing the potential for significant reliability issues. Additionally, APAT's configuration is a normally-open system. If the system were to be closed, information would be communicated to APAT's Transmission Operator informing it of the closure. This would help to ensure that lines would be maintained and protected from disturbances. Furthermore, APAT is a small entity with a peak load of 69 MW, lessening the potential impact to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/2/2012 (Mitigation Plan completion) | $8,000 (for WECC2012011407 and WECC2012011412) | Self-Report | To mitigate this violation, APAT: 1) created an updated protection system manual that includes the basis for the maintenance to be performed and a summary schedule for all Protection System equipment and any relays that meet the technical requirements for WECC's Underfrequency Load Shedding Plan, in the event that APAT's relays are included in a future plan; and 2) documented the summary table, the cycle for maintenance, and maintenance requirements to its online maintenance platform. | 2012-04-02 | 2013-02-08 | Agrees/Stipulates | WECC reviewed APAT's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC found that: APAT's ICP is documented; the ICP is disseminated throughout its operations staff; APAT has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; APAT operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; APAT has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; APAT reviews and modifies its ICP regularly; APAT's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and APAT's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Alameda Municipal Power (APAT) | NCR10042 | WECC2012011412 | Settlement Agreement | On November 13, 2012, APAT submitted a Self-Report to WECC stating that, as a Distribution Provider (DP), it was in violation of PRC-005-1 R2. APAT did not include certain Protection System devices in its maintenance and testing program; therefore, it did not have documentation demonstrating that it had implemented its maintenance and testing program for those Protection System devices. APAT did not have a maintenance and testing program for its DC control circuitry. Although APAT had a maintenance and testing program for its relays and voltage and current sensing devices, APAT could not provide evidence of testing pursuant to its established program. In summary, APAT failed to test 1 out of 1 DC control circuits and 4 out of 5 relays. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although APAT's failure to properly maintain and test Protection System devices could have increased the likelihood of device misoperation or unintended operation, the potential risks of APAT's noncompliance were mitigated by procedures implemented by APAT during the violation period. APAT tested all Protection System devices upon commissioning them, and it also conducted real-time monitoring on all of the devices. The real-time monitoring was sent to a station that was monitored 24 hours a day, seven days a week. Furthermore, there was an alarm attached to the equipment, which would indicate if there were any failures or problems. APAT's system configuration and size lessened the potential impact to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 1/11/2013 (when APAT submitted evidence demonstrating that Protection System devices had received maintenance and testing) | $8,000 (for WECC2012011407 and WECC2012011412) | Self-Report | To mitigate this violation, APAT: 1) created an updated protection system manual that includes the basis for the maintenance to be performed and a summary schedule for all Protection System equipment and any relays that meet the technical requirements for WECC's Under Frequency Load Shedding plan in the event that APAT's relays are included in a future plan; 2) conducted maintenance and testing on all of its Protection System devices; and 3) documented the summary table, the cycle for maintenance, and maintenance requirements to its online maintenance platform. A workflow is used to send multiple reminders and escalates to the compliance management team well prior to the due date should the maintenance not be performed. | 1/11/2013 (Mitigation Plan completion) | 2013-04-03 | Agrees/Stipulates | WECC reviewed APAT's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC found that: APAT's ICP is documented; the ICP is disseminated throughout its operations staff; APAT has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; APAT operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; APAT has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; APAT reviews and modifies its ICP regularly; APAT's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and APAT's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
Western Electricity Coordinating Council (WECC) | Southern California Edison - Transmission & Distribution Business Unit (SCET) | NCR05398 | WECC2012011231 | Settlement Agreement | On October 15, 2012, SCET submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of PRC-001-1 R4. In response to a September 8, 2011 outage, SCET conducted an exhaustive review of its intertie overload relays. In reviewing the coordination of these relays, SCET discovered that it failed to coordinate five relay Protection Systems on major transmission lines and interconnections with the California Independent System Operator (CAISO) prior to installation. Specifically, SCET determined the: 1) Devers - Coachella 220 kV Intertie Overload Relay at Devers Substation; 2) Eldorado - McCullough 500 kV Intertie Overload Relay at Eldorado Substation; 3) Laguna Bell - Velasco 220 kV Intertie Overload Relay at Laguna Bell Substation; 4) Lugo - Victorville 500 kV Intertie Overload Relay at Lugo Substation; and 5) Midway - Whirlwind 500 kV Intertie Overload Relay at Whirlwind Substation were not coordinated with CAISO prior to being placed into service. WECC determined that the Protection Systems identified in 1 through 4 above had not been communicated or coordinated with CAISO prior to their installation. WECC also determined that while SCET did communicate the 5) Midway - Whirlwind relay with the CAISO, it failed to coordinate this with its neighboring TOP, Pacific Gas and Electric Company. | PRC-001-1 | R4 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SCET failed to coordinate several Protection Systems with CAISO prior to implementation, SCET did coordinate Protection Systems identified in 1 through 4 with neighboring TOPs. In addition, the new Midway relay at Whirlwind substation was coordinated with CAISO prior to installation. Operators at both interconnections were aware of the Protection Systems; however, formal coordination was not documented. Also, for protection systems identified in 1 through 4, SCET noted that the relays were installed prior to the formation of the CAISO as SCET's Balancing Authority. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/3/2013 (Mitigation Plan completion) | $35,000 (for WECC2012011231, WECC2012011233, and WECC2012011327) | Self-Report | To mitigate this violation, SCET: 1) updated its SCET Interconnection Relay Setting database to include all intertie overload relays and settings; and 2) modified existing System Operating Bulletins, which are used to communicate coordination with SCET's neighboring Generator Operators, TOPs, and Balancing Authorities. | 2013-04-03 | 2013-06-12 | Agrees/Stipulates | WECC reviewed SCET's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: 1) SCET has a comprehensive, established, and documented program; 2) SCET's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; 3) the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; 4) SCET has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; 5) SCET has one position fully dedicated to FERC/NERC compliance; 6) SCET's compliance official has independent access to the chief executive officer or equivalent; 7) SCET's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; 8) SCET has dedicated adequate resources to support its ICP; 9) SCET's ICP has the support and participation of senior management; 10) SCET's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; 11) SCET has distributed the ICP to all employees and, if applicable, contractors and vendors; 12) SCET has fully implemented its program; 13) SCET's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; 14) SCET's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; 15) SCET's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; 16) SCET's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; 17) SCET regularly reviews its ICP at least annually; and, 18) SCET participates in outreach compliance program activities. SCET did not receive mitigating credit for self-reporting because the Self-Report was submitted during a Compliance Audit. On or before October 31, 2013, SCET must submit a narrative to WECC describing how SCET implemented, or a plan to implement, the following additional terms: 1) SCET will develop a process to track deadlines and mitigate timely, minimizing the need for extension requests; 2) SCET will create a monthly coordination meeting between compliance groups (CIP technical groups, business groups, affiliates). This meeting should focus on increasing communication between entities and centralizing issues stemming from information silos; 3) SCET will create an annual compliance awareness training program and measure the degree of understanding. This training program will include a section to prevent recurrence of NERC Reliability Standard violations; and d. SCET will develop a process or set of improvements to processes that help identify the full scope of violations promptly. SCET will develop a process for detecting what controls are needed when new devices are installed.
Western Electricity Coordinating Council (WECC) | Southern California Edison - Transmission & Distribution Business Unit (SCET) | NCR05398 | WECC2012011233 | Settlement Agreement | On October 15, 2012, during a Compliance Audit, SCET submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner (TO), it was in violation of PRC-023-1 R1. In response to the September 8, 2011 outage, SCET conducted an in-depth review of its intertie overload relays. In reviewing the coordination of these relays, SCET found that the 1) Devers - Coachella Valley relays and 2) Midway Vincent path relays had the overcurrent setting lower than the transmission relay loadability requirement for the associated transmission line or path. On July 11, 2012, SCET increased the setting for the Devers - Coachella Valley relays to the next available setting to comply with R1.2. On August 23, 2012, SCET modified the relay scheme for the Midway Vincent path and set the relays to comply with R1.13. WECC determined that SCET set its phase protection relays so they did not operate at or below 115%. SCET's Devers-Coachella and Midway-Vincent relays were set below the 115% limitation (at 114.6% and 110% respectively). | PRC-023-1 | R1 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SCET was operating lower than the transmission relay loadability, the difference represented less than 5% of total loadability. SCET analyzed historical path flow data during the duration of the violation, taking into account the potential impact of the Most Severe Single Contingency (MSSC) during that window in relation to the path relay setting. The analysis only identified 16 hours out of 14,600 hours (0.1% of the total hours) where opening of the path might have been considered plausible were the MSSC to have occurred. | 7/1/2010 (when the Standard became mandatory and enforceable) | 5/25/2012 (when SCET corrected the relay settings) | $35,000 (for WECC2012011231, WECC2012011233, and WECC2012011327) | Self-Report | To mitigate this violation, SCET: 1) selected the next available tap above 115% (tap 8, representing 131% of the line emergency rating) on the Devers - Coachella Valley relays; 2) set the Midway-Vincent relays above 115% of the path rating; and 3) completed training on System Protection Procedure 6 (transmission relay loadability) and NERC Standard PRC-023 transmission relay loadability. | 2013-04-03 | 2013-06-12 | Agrees/Stipulates | WECC reviewed SCET's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: 1) SCET has a comprehensive, established, and documented program; 2) SCET's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; 3) the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; 4) SCET has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; 5) SCET has one position fully dedicated to FERC/NERC compliance; 6) SCET's compliance official has independent access to the chief executive officer or equivalent; 7) SCET's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; 8) SCET has dedicated adequate resources to support its ICP; 9) SCET's ICP has the support and participation of senior management; 10) SCET's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; 11) SCET has distributed the ICP to all employees and, if applicable, contractors and vendors; 12) SCET has fully implemented its program; 13) SCET's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; 14) SCET's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; 15) SCET's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; 16) SCET's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; 17) SCET regularly reviews its ICP at least annually; and, 18) SCET participates in outreach compliance program activities. SCET did not receive mitigating credit for self-reporting because the Self-Report was submitted during a Compliance Audit. On or before October 31, 2013, SCET must submit a narrative to WECC describing how SCET implemented, or a plan to implement, the following additional terms: 1) SCET will develop a process to track deadlines and mitigate timely minimizing the need for extension requests; 2) SCET will create a monthly coordination meeting between compliance groups (CIP technical groups, business groups, affiliates). This meeting should focus on increasing communication between entities and centralizing issues stemming from information silos; 3) SCET will create an annual compliance awareness training program and measure the degree of understanding. This training program will include a section to prevent recurrence of NERC Reliability Standard violations; and d. SCET will develop a process or set of improvements to processes that help identify the full scope of violations promptly. SCET will develop a process for detecting what controls are needed when new devices are installed.
Western Electricity Coordinating Council (WECC) | Southern California Edison - Transmission & Distribution Business Unit (SCET) | NCR05398 | WECC2012011327 | Settlement Agreement | On October 25, 2012, during a Compliance Audit, WECC determined that SCET, as a Transmission Operator (TOP), it was in violation of PRC-001-1 R3. Specifically, SCET failed to coordinate and communicate all new protective systems with its neighboring TOPs. In response, WECC requested SCET to provide evidence of all new protection systems and all protective system changes during the Audit period (October 1, 2010 through October 5, 2012). In return, SCET provided a spreadsheet documenting the status and coordination of all protection systems. The spreadsheet identified a failure in SCET's coordination of protection systems. Specifically, SCET failed to confirm that coordination was done on all changes and additions to the Midway - Whirlwind 500 kV intertie overload relays at the Whirlwind Substation, which went into service on May 25, 2012. WECC concluded that SCET failed to coordinate all new Protection Systems with Pacific Gas and Electric Company (PGAE) before implementing new relay settings, in violation of PRC-001-1 R3. | PRC-001-1 | R3; R3.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SCET failed to timely coordinate Protection System changes, SCET did notify its Balancing Authority (California Independent System Operator) of the changes. Further, pursuant to SCET's transmission relay loadability, SCET has set the phase protection relays so they do not operate at or below 115% of practical limitations. Because SCET has limited its transmission line capability to 115%, and has coordinated this limitation with PGAE for all other transmission relays, SCET made PGAE familiar with SCET's system loadability. In addition, in the event that the relays operate at or below SCET's loadability setting, SCET and PGAE would coordinate prior to taking any remedial action to protect system reliability on the 500 kV line. | 5/25/2012 (when SCET placed the relays in service) | 8/25/2012 (when SCET coordinated and communicated with PGAE) | $35,000 (for WECC2012011231, WECC2012011233, and WECC2012011327) | Audit | To mitigate this violation, SCET included the intertie overload relay settings in System Operating Bulletin (SOB) 065, and issues the revised SOB to neighboring TOPs and Balancing Authorities whenever changes or modifications are made. | 2012-09-26 | 2013-05-03 | Agrees/Stipulates | WECC reviewed SCET's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: 1) SCET has a comprehensive, established, and documented program; 2) SCET's ICP identifies and lists all applicable NERC Reliability Standards and includes a process for updating this list as Standards change; 3) the ICP includes procedures to assess compliance risks and practices related to NERC Reliability Standards on an annual basis; 4) SCET has identified and assigned responsibility and accountability to a compliance officer or other high ranking official; 5) SCET has one position fully dedicated to FERC/NERC compliance; 6) SCET's compliance official has independent access to the chief executive officer or equivalent; 7) SCET's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; 8) SCET has dedicated adequate resources to support its ICP; 9) SCET's ICP has the support and participation of senior management; 10) SCET's ICP requires compliance training for all staff, contractors, and vendors who have direct responsibility for the implementation of the processes and procedures that demonstrate compliance with the NERC Reliability Standards; 11) SCET has distributed the ICP to all employees and, if applicable, contractors and vendors; 12) SCET has fully implemented its program; 13) SCET's ICP includes documentation regarding compensation, awards, employee recognition or other incentives to encourage employee compliance with NERC Reliability Standards; 14) SCET's ICP includes procedures for disciplinary action for employees involved in violations of the Reliability Standards; 15) SCET's ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards on an annual basis; 16) SCET's ICP includes specific procedures to promote prompt detection and self-reporting of possible violations to WECC; 17) SCET regularly reviews its ICP at least annually; and, 18) SCET participates in outreach compliance program activities. On or before October 31, 2013, SCET must submit a narrative to WECC describing how SCET implemented, or plans to implement, the following additional terms: 1) SCET will develop a process to track deadlines and mitigate timely, minimizing the need for extension requests; 2) SCET will create a monthly coordination meeting between compliance groups (CIP technical groups, business groups, affiliates). This meeting should focus on increasing communication between entities and centralizing issues stemming from information silos; 3) SCET will create an annual compliance awareness training program and measure the degree of understanding. This training program will include a section to prevent recurrence of NERC Reliability Standard violations; and d. SCET will develop a process or set of improvements to processes that help identify the full scope of violations promptly. SCET will develop a process for detecting what controls are needed when new devices are installed.