## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Great River Energy (GRE) | NCR00992 | MRO201100335 | Notice of Confirmed Violation | On July 1, 2011, GRE submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it was in violation of FAC-009-1 R1. GRE failed to establish Facility Ratings for its Facilities that were consistent with its Facility Ratings Methodology. During an internal review, GRE discovered that ratings for flexible conductors (jumpers) were omitted from its Facility Ratings database. However, GRE's Facility Ratings Methodology included these flexible conductor ratings as a component used to determine Facility Ratings. GRE has completed a review of its ratings for all of its 345 kV facilities, and has completed a review for some of its 230 kV, 161 kV, and 115 kV facilities. As of March 25, 2014, GRE has identified 36 elements with incorrect ratings. Of the 36 discrepancies, 13 resulted in changes to nine separate Facility Ratings (some facilities had multiple elements with incorrect ratings). As of March 25, 2014, MRO reviewed each of the nine Facility Rating changes. At Benton County, the summer Facility Rating for a 230 kV bus changed from 864 MVA to 561 MVA and the winter Facility Rating changed from 1,131 MVA to 797 MVA. At Dickinson, the 345/115 kV transformer summer Facility Rating for normal operation changed from 448 MVA to 324 MVA. The Dickinson summer Facility Rating for emergency operation changed from 560 MVA to 324 MVA, and the winter Facility Rating for emergency operation changed from 560 MVA to 478 MVA. Additionally, at Dickinson the summer Facility Rating on the 115 kV line from Dickinson to Crow River dropped from 349 MVA to 324 MVA. At Dickinson, the Facility Ratings for both of the 345 kV lines out of Dickinson (to Coon Creek and Parkers Lake) dropped from 1,065 MVA to 896 MVA in the summer and 1,195 MVA to 896 MVA in the winter. MRO analyzed the actual flows on each of GRE's facilities for 2013 and discovered that the Dickinson 345 kV/115 kV transformer operated over its actual limit due to incorrect Facility Ratings. The transformer exceeded its limit by 53 MVA, or 16%, for a total of 46 hours in 2013, including 39 out of 47 contiguous hours between July 1, 2013, and July 3, 2013. | FAC-009-1 | R1 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, incorrect Facility Ratings impact planning models and may impact the Reliability Coordinator’s ability to coordinate an area of the BPS. Dickinson is important for the Minneapolis and Saint Paul (twin cities) area, providing a DC link between western North Dakota generation and a 345 kV ring around the twin cities via connections to both Coon Creek and Parkers Lake 345 kV substations. Benton County also serves as a key substation to the twin cities and has one of the five outlets for another Registered Entities' generating station, which contains the largest generating unit in the MRO region. Additionally, the Dickinson 345/115 kV transformer facility operated over its Facility Rating. However, Dickinson contains a ring bus, and can accommodate a break in the ring. Although Dickinson operated over its limit, the actual limiting elements were jumpers associated with breakers on the low side of the transformer. Since the ring was intact during this time, the load was split between the breakers and the associated jumpers and therefore, was not overloaded. | 6/18/2007 (when the Standard became mandatory and enforceable) | present | 15000 | Self-Report | To mitigate this violation, GRE will: 1) perform a comprehensive review of its Facility Ratings; 2) revise its communication procedures for Facility Ratings to promote clear communication to the parties responsible for implementing and planning the ratings of the GRE Facilities; 3) implement and communicate the correct ratings to MRO; 4) revise its ampacity drawings for each of its substations with inaccurate Facility Ratings; and 5) high priority substations, as determined by the voltage class, will be addressed first according to the Mitigation Plan. | 4/7/2016 (approved completion date) | TBD | Admits | MRO reviewed GRE's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. MRO considered indicators of GRE's culture of compliance as a mitigating factor in the penalty determination. GRE recognized an opportunity to expand its compliance and controls above and beyond those set by the Standard. GRE has created and implemented management practices surrounding its Facilities Ratings and is revising its geographic information system.
Northeast Power Coordinating Council, Inc. (NPCC) | ReEnergy Stratton | NCR10352 | NPCC2012011626 | Settlement Agreement | During a Spot Check conducted from August 14, 2012 through September 24, 2012, NPCC determined that ReEnergy Stratton, as a Generator Owner (GO), was in violation of PRC-005-1 R1.2. ReEnergy Stratton failed to provide a summary of maintenance and testing procedures required by PRC-005-1 R1.2 for its Stratton and Livermore Falls generating facilities. ReEnergy Stratton provided a spreadsheet that documented the relay component, testing interval, and testing basis. However, this spreadsheet did not sufficiently describe all aspects of ReEnergy Stratton's maintenance and testing program. Specifically, ReEnergy Stratton failed to provide a summary that explained testing processes of maintenance and testing procedures for relays, current transformers and potential transformers (CT/PTs), DC control circuits, and batteries. ReEnergy Stratton also failed to provide a total inventory of their DC control circuit devices and CT/PTs. | PRC-005-1 | R1; R1.2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although ReEnergy Stratton did not have a formal maintenance and testing program that satisfied PRC-005-1 R1, ReEnergy did have an excel document showing testing guidelines and basis for that testing. The document included testing requirements for performing relay testing, documentation of relay testing, and listed a device description for relay calibration. Testing requirements for all aspects of performing relay testing were documented and the device description for relay calibration was listed. At the Livermore Falls facility, DC control circuitry is monitored and upon a loss of DC control circuitry an alarm is initiated to the control room that is staffed twenty four hours a day, seven days a week. All relays, with the exception of the main transformer differential relays, were tested satisfactorily according to the relay and maintenance interval testing schedule. The devices that were not tested comprised the facilities 13 kV switchgear and step-up transformer protection. Should these devices not function properly it would have limited exposure to the BPS. Also, ReEnergy performed some testing to verify that the multi-contact relay would function properly when signaled to trip and the associated breakers would trip. This verification provided evidence that the trip coils and multi-contact relays were functional. At Stratton, all CT/PTs readings are monitored on the stations distributed control system that is monitored by control room staff twenty four hours a day, seven days a week. At the Livermore Falls and Stratton 115 kV facilities the CT/PTs, although testing was not performed to verify readings at the relay, verification for the integrity of the CT/PT device was performed with a transformer turns ratio test on a five-year basis which provides assurance that the AC portion of the circuit was functioning properly. Testing was performed and all components tested satisfactorily. Also, during the violation period, real-time relay operations operated as per design and a review determined there were no relay misoperations. | 8/14/2009 (when ReEnergy Stratton registered as a GO) | 11/12/2013 (when the maintenance and testing procedure was completed) | $5,000 (for NPCC2012011626 and NPCC2012011627) | Spot Check | To mitigate the violation, ReEnergy Stratton developed a Protection System maintenance and testing program pursuant to the NERC Reliability Standard PRC-005. | 2014-04-15 | 2014-05-16 | Neither Admits nor Denies | NPCC considered ReEnergy Stratton's internal compliance program (ICP) a neutral factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | ReEnergy Stratton | NCR10352 | NPCC2012011627 | Settlement Agreement | During a Spot Check conducted from August 14, 2012 through September 24, 2012, NPCC determined that ReEnergy Stratton, as a Generator Owner (GO), was in violation of PRC-005-1 R2. ReEnergy Stratton failed to provide evidence that all Protection System devices were maintained and tested within the defined intervals and the date when each Protection System device was last tested/maintained. Specifically, ReEnergy Stratton failed to provide testing data for generator DC control testing, which comprised 2 of 4 of applicable devices or 50%. Also, ReEnergy Stratton failed to provide testing data for current and voltage transformers (CTs/PTs) to verify secondary values to their relays, which comprised greater than 75% of 77 applicable devices. This violation applied to both the Stratton and Livermore Falls generating facilities. In addition, relay testing for the main transformer differential relays could not be provided for the Livermore Falls generating facility, which comprised 7%, or 3 out of 44, applicable devices. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system ( BPS). At the Livermore Falls facility, DC control circuitry is monitored and upon a loss of DC control circuitry, an alarm is initiated to the control room that is staffed twenty four hours a day, seven days a week. All relays, with the exception of the main transformer differential relays, were tested satisfactorily according to the relay and maintenance interval testing schedule. The devices that were not tested comprised the facilities 13 kV switchgear and step-up transformer protection. Should these devices not function properly it would have limited exposure to the BPS. Also, ReEnergy performed some testing to verify that the multi-contact relay would function properly when signaled to trip and the associated breakers would trip. This verification provided evidence that the trip coils and multi-contact relays were functional. At Stratton, all CT/PTs readings are monitored on the stations distributed control system that is monitored by control room staff twenty four hours a day, seven days a week. At the Livermore Falls and Stratton 115 kV facilities the CT/PTs, although testing was not performed to verify readings at the relay, verification for the integrity of the CT/PT device was performed with a transformer turns ratio test on a five-year basis which provides assurance that the AC portion of the circuit was functioning properly. Testing was performed and all components tested satisfactorily. Also, during the violation period, real-time relay operations operated as per design and a review determined there were no relay misoperations. | 8/14/2009 (when ReEnergy Stratton registered as a GO) | 4/15/2014 (Mitigation Plan completion) | $5,000 (for NPCC2012011626 and NPCC2012011627) | Spot Check | To mitigate the violation, ReEnergy Stratton: 1) developed a Protection System maintenance and testing program pursuant to the NERC Reliability Standard PRC-005; 2) completed maintenance and testing on Protection System devices at issue at Livermore Falls; and 3) completed maintenance and testing on Protection System devices at issue at Stratton. | 4/15/2014 | 2014-05-16 | Neither Admits nor Denies | NPCC considered ReEnergy Stratton's internal compliance program (ICP) a neutral factor in the penalty determination.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company - Fossil and Hydro (GO,GOP) (VEPCO-F&H) | NCR09028 | SERC2013012945 | Settlement Agreement | On September 12, 2013, VEPCO-F&H submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1.1b R3. VEPCO-F&H failed to notify its Transmission Operator (TOP) within 30 minutes of a status or capability change on a generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. In July 2013, VEPCO-F&H initiated a review of its compliance with VAR-002-1.1b R3 as a result of a discovery by an affiliate where the 30-minute notification had not occurred for an event. VEPCO-F&H reviewed the TOP’s dispatcher application and reporting tool tickets and compared the tickets to the generating station operating logs to determine if it notified the TOP within 30 minutes as required. VEPCO-F&H identified 26 total instances of status changes between September 6, 2007, when VEPCO-F&H registered as a GOP and was required to be compliant with the Standard, and September 19, 2013. VEPCO-F&H identified 12 instances where it failed to notify its TOP within 30 minutes of a status change. It was determined that VEPCO-F&H notified the TOP of the 12 instances of status change between 37 minutes to approximately 11 days. VEPCO-F&H determined that its power station personnel and system operations center personnel failed to follow the established protocols in place to communicate status changes to the TOP. | VAR-002-1 | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All generation units met the voltage schedules during the associated period of non-compliance. The generation output of the units during the periods of non-compliance ranged from 70 MW to 540 MW while the system load ranged from 12,000 MW to 19,000 MW. Each of the reactive power capability changes involved in the violation occurred at different times; therefore, there was no instance that impacted more than one generation unit. Furthermore, the TOP did not identify any of the impacted zones as areas with stability concerns. No harm is known to have occurred. | 6/29/2008 (when the first instance of non-compliance occurred) | 8/22/2013 (when the last instance of non-compliance occurred) | $16,000 (for SERC2013012945 and SERC2013013278) | Self-Report | To mitigate this violation, VEPCO-F&H: 1) provided interim direction and instructions to station management personnel to ensure increased generator operator awareness of the VAR-002 requirements. These interim instructions required generator operators, when reporting a status or capability change on any generator reactive power resource, to inform the system operation center (SOC) operator that the TOP must be notified within 30 minutes of the occurrence, including the expected duration of the change in status or capability. It also required generator operators to inform the SOC operator that the notification is a NERC Reliability Standard requirement; 2) provided refresher training to SOC personnel on the reporting requirements of VAR-002. The training reviewed the VAR-002 requirements and the TOP's reporting requirements, and reinforced the 30 minute time limit for reporting the status change to the TOP; 3) trained power generation operations station personnel and modified the reporting protocol for status or capability changes on any generator reactive power resource such that the generator operator is required to call the market operations center (MOC) and the SOC to report any status or capability change. The MOC will then notify the TOP on behalf of the generator operator about the change in status or capability; 4) trained MOC personnel who will receive the information of the status or capability change on any generator reactive power resource how to provide the status or capability change to the TOP; and 5) implemented changes in the reporting protocol and procedures to reflect the new protocol. | 2013-12-16 | 2014-05-16 | Neither Admits nor Denies | SERC reviewed VEPCO-F&H's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is managed on a day-to-day basis by the NERC compliance policy group of VEPCO-F&H's parent company, Dominion Resources, Inc. The ICP is posted on the NERC compliance policy group's website and can be reviewed at any time. The ICP is overseen by the chief compliance officer of VEPCO-F&H's parent company, who reports to the senior vice president of law, public policy, and environment, state and federal affairs, who in turn reports to the chief executive officer. This structure allows for direct and independent access to the chief executive officer and the board of directors. Senior management is fully supportive of the ICP. The ICP is reviewed annually and provides for annual NERC awareness training of employees with NERC compliance responsibilities and targeted training as appropriate. Employees also receive annual compliance and ethics training to remind them of their responsibility to report any perceived violation of a NERC Reliability Standard. The ICP also provides for internal mock audits from time-to-time. The ICP allows for discipline of employees, pursuant to the discipline policy, for conduct that violates NERC Reliability Standards or a failure to report potential violations of NERC Reliability Standards.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company - Fossil and Hydro (GO,GOP) (VEPCO-F&H) | NCR09028 | SERC2013013278 | Settlement Agreement | On December 19, 2013, VEPCO-F&H submitted a Self-Report stating that, as a Generator Operator, it was in violation of VAR-002-2b R3. VEPCO-F&H failed to notify its Transmission Operator (TOP) within 30 minutes of a status or capability change on a generator Reactive Power resource, including the status of each power system stabilizer (PSS) and the expected duration of the change in status or capability. At approximately 5:30 p.m. on November 17, 2013, VEPCO-F&H notified the TOP via the Transmission Owner’s system operations center (SOC) that VEPCO-F&H was going to change the status of the automatic voltage regulator (AVR) from automatic to manual operation. While making this notification, VEPCO-F&H also incorrectly notified the SOC that the PSS would remain in service, which was not possible as the PSS could only operate while the AVR was in automatic mode. The SOC then failed to provide notification regarding the correct status of the PSS to the TOP within 30 minutes. VEPCO-F&H notified the TOP via the SOC of the correct status of the PSS on November 18, 2013 at approximately 5:19 a.m., almost 12 hours later. The VEPCO-F&H generator operator on duty at the time of the violation had completed a training class on the reporting requirements of VAR-002 in August 2013 as part of the approved Mitigation Plan for NERC Violation ID SERC2013012945. | VAR-002-2b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEPCO-F&H maintained the voltage schedule during the violation. VEPCO-F&H notified the TOP of the change in status of the AVR from automatic to manual within 30 minutes as required. Only the Chesterfield #8 generator, which represented less than 1% of VEPCO-F&H’s total generation at the time of the violation, was affected. Based on VEPCO-F&H’s review of this event, the grid was stable during the violation. No harm is known to have occurred. | 11/17/2013 at 6:00 p.m. (30 minutes after VEPCO-F&H notified the TOP that the AVR was being placed in automatic but failed to notify the TOP of the PSS status change) | 11/18/2013 at 5:19 a.m. (when VEPCO-F&H notified the TOP of the correct status of the PSS) | $16,000 (for SERC2013012945 and SERC2013013278) | Self-Report | To mitigate this violation, VEPCO-F&H: 1) reviewed and emphasized its NERC compliance procedure for VAR-002 and control room operator performance expectations with relevant personnel; 2) revised the station-specific startup procedure to include PSS operation; 3) developed a quick reference checklist and posted it by each market operations center (MOC) and SOC direct-dial phone for use whenever there is a change in status or availability of a unit's reactive power capability, voltage regulator, or PSS; and 4) disciplined the control room operator and shift supervisor in accordance with the established corporate discipline policy and agreements for union and non-union employees. | 2013-12-26 | 2014-05-16 | Neither Admits nor Denies | SERC reviewed VEPCO-F&H's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is managed on a day-to-day basis by the NERC compliance policy group of VEPCO-F&H's parent company, Dominion Resources, Inc. The ICP is posted on the NERC compliance policy group's website and can be reviewed at any time. The ICP is overseen by the chief compliance officer of VEPCO-F&H's parent company, who reports to the senior vice president of law, public policy, and environment, state and federal affairs, who in turn reports to the chief executive officer. This structure allows for direct and independent access to the chief executive officer and the board of directors. Senior management is fully supportive of the ICP. The ICP is reviewed annually and provides for annual NERC awareness training of employees with NERC compliance responsibilities and targeted training as appropriate. Employees also receive annual compliance and ethics training to remind them of their responsibility to report any perceived violation of a NERC Reliability Standard. The ICP also provides for internal mock audits from time-to-time. The ICP allows for discipline of employees, pursuant to the discipline policy, for conduct that violates NERC Reliability Standards or a failure to report potential violations of NERC Reliability Standards.
Texas Reliability Entity, Inc. (Texas RE) | GEUS | NCR04075 | TRE2013012892 | Settlement Agreement | On August 30, 2013, GEUS submitted a Self-Certification stating that, as a Generator Owner, it was in violation of PRC-005-1 R1. Specifically, GEUS’s Protection System Maintenance Program (PSMP) was found to only cover relay maintenance and testing intervals and their basis and a summary of their maintenance and testing procedures for all of its 10 relays. GEUS did not include the other Protection System device types which include seven DC circuits, one battery, and 29 current transformers (CTs)/potential transformers (PTs) in its PSMP. GEUS therefore did not have maintenance and testing intervals and their basis nor did GEUS have a summary of its maintenance and testing intervals for 78.7% of its Protection System devices. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Over three quarters (78.7%) of the GEUS devices were not included in its PSMP during the violation period. Consequently, these devices and their associated blackstart unit(s) may not have operated as intended during an Electric Reliability Council of Texas, Inc. (ERCOT) recovery from a blackout. However, the risk to the reliability of the BPS was mitigated because testing was completed on the unit(s) per ERCOT’s blackstart unit testing requirements. In addition, GEUS’s blackstart capability was only 26 MW for 2010 and 2011. During 2012 and 2013 the total blackstart capability was 25.2 MW. Further, the blackstart units were monitored by the GEUS control system and controlled by the employees at the plant; therefore, any situations out of the normal would have be noted by those groups and GEUS’s response to those situations would be coordinated between the two groups. Finally, no actual impacts were reported for the GEUS blackstart units during the violation period. | 6/15/2010 (the day after the completion of the Mitigation Plan for the PRC-005 R1 issue found during the GEUS 2010 Audit) | 1/31/2014 (Mitigation Plan completion) | $20,000 (for TRE2013012892 and TRE2013012893) | Self-Certification | To mitigate this violation, GEUS: 1) defined maintenance and testing intervals and their basis for all applicable generation Protection System devices. 2) worked with subject matter experts to document and consolidate maintenance and testing procedures for all applicable generation Protection System devices. In addition to the actions outlined in its Mitigation Plan, GEUS is taking the following actions to remediate the violation: 1) hired a full-time compliance manager; 2) purchased compliance management software; 3) updated internal compliance program (ICP); 4) utilized compliance calendar to include action items and reminders set in advance of the next testing date, which will assure that maintenance and testing is performed on all applicable Protection System devices within the defined intervals; 5) designated the compliance manager as a single point of coordination for managing compliance documentation; 6) instituted an ongoing process for including on the compliance calendar the annual review of the PSMP; 7) instituted an ongoing process for monitoring the Standards in development and Standards subject to future enforcement; and 8) instituted an ongoing process for having applicable compliance personnel attend Webinars, conferences, meetings, etc. and utilize the resources on the Texas RE and NERC websites to reinforce knowledge of requirements, best practices, compliance processes and procedures, and their applicability to GEUS. | 2014-01-31 | 2014-04-09 | Neither Admits nor Denies | Texas RE reviewed GEUS’s ICP and considered it to be a neutral factor in the penalty determination. GEUS did not develop a compliance program until December 2013, but has since taken strides towards a strong program. A Notice of Confirmed Violation covering violations of PRC-005-1 R1 for GEUS was filed with FERC under NP11-133-000 on February 28, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE considered the entity’s compliance history to be a neutral factor in determining the penalty. GEUS mitigated the prior violation of PRC-005-1 R1 by incorporating in tis Relay Test Periodicity Policy document a statement that NERC “Protection System Maintenance- A Technical Reference” document, dated September 13, 2007, will be used as the basis behind the maintenance and testing intervals.
Texas Reliability Entity, Inc. (Texas RE) | GEUS | NCR04075 | TRE2013012893 | Settlement Agreement | On August 30, 2013, GEUS submitted a Self-Certification stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. Specifically, GEUS’s blackstart unit in 2007, 2008, 2010, and 2011 only had evidence Protection System devices were maintained and tested within the defined intervals and the date each Protection System device was last tested/maintained for all of its 16 relays. GEUS could not provide evidence that the other Protection System devices were maintained and tested within the defined intervals or the date each Protection System device was last test tested/maintained. These devices include two DC circuits, one battery, and 11 current transformers (CT)/potential transformers (PTs). These devices make up 46.7% of GEUS’ Protection System devices. | PRC-005-1 | R2; R2.1; R2.2 | High | Moderate | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, GEUS failed to produce evidence that it had tested 46.7% of its blackstart unit Protection System devices within reasonable intervals. It also could not produce evidence of the last tested/maintained date for 46.7% its Protection System devices. Consequently, these devices may not have operated as intended during an Electric Reliability Council of Texas, Inc. (ERCOT) recovery from a blackout. However, the risk to the reliability of the BPS was mitigated because testing was completed on the unit per ERCOT’s blackstart unit testing requirements. In addition, GEUS’s blackstart capability was only 26 MW for 2007, 2008, 2010, and 2011. Further, the blackstart units were monitored by the GEUS control system and controlled by the employees at the plant; therefore, any situations out of the normal would have be noted by those groups and GEUS’s response to those situations would be coordinated between the two groups. Finally, no actual impacts were reported for the GEUS blackstart units during the violation period. | 6/28/2007 (when GEUS registered as a GO) | 12/31/2011 (the last date there was a unit with a missing test date) | $20,000 (for TRE2013012892 and TRE2013012893) | Self-Certification | To mitigate this violation, GEUS: 1) performed testing for all Protection System devices for which it was unable to produce the most recent test record or had no records of maintenance done within proper intervals; 2) hired a full-time compliance manager; 3) purchased compliance management software; 4) updated internal compliance program (ICP); 5) utilized compliance calendar to include action items and reminders set in advance of the next testing date, which will assure that maintenance and testing is performed on all applicable Protection System devices within the defined intervals; 6) designated the compliance manager as a single point of coordination for managing compliance documentation; 7) instituted an ongoing process for including on the compliance calendar the annual review of the PSMP; 8) instituted an ongoing process for monitoring the Standards in development and Standards subject to future enforcement; 9) instituted an ongoing process for having applicable compliance personnel attend Webinars, conferences, meetings, etc. and utilize the resources on the Texas RE and NERC websites to reinforce knowledge of requirements, best practices, compliance processes and procedures and their applicability to GEUS; 10) created its consolidated Protection System Maintenance Program (PSMP) with clearly defined intervals, minimum maintenance activities, and applicable Protection System component types; and 11) created a list of applicable equipment by device that lists the, most recent test date, previous test date, and date testing will be due according to intervals defined in the PSMP. | 2014-02-27 | 2014-04-09 | Neither Admits nor Denies | Texas RE reviewed GEUS’s ICP and considered it to be a neutral factor in the penalty determination. GEUS did not develop a compliance program until December 2013, but has since taken strides towards a strong program. A Notice of Confirmed Violation covering violations of PRC-005-1 R1 for GEUS was filed with FERC under NP11-133-000 on February 28, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE considered the entity’s compliance history to be a neutral factor in determining the penalty. GEUS mitigated the prior violation of PRC-005-1 R1 by incorporating in its Relay Test Periodicity Policy document a statement that NERC “Protection System Maintenance- A Technical Reference” document, dated September 13, 2007, will be used as the basis behind the maintenance and testing intervals.
Western Electricity Coordinating Council (WECC) | Colorado Springs Utilities (CSU) | NCR05106 | WECC2013011934 | Settlement Agreement | On February 15, 2013, CSU submitted a Self-Report stating that, as a Generator Operator, it had previously provided incorrect information to WECC during a Compliance Audit of PRC-001-1 R1 conducted from April 16, 2012 through April 26, 2012. During the Compliance Audit, WECC had determined that CSU complied with this Standard. CSU reported that at the time of the data request, a supervisor had identified five generator operators as having completed a computer-based training class. The supervisor later disclosed to management that he had submitted inaccurate evidence to the WECC audit team. Only one of the five operators had completed the class. In response to CSU's Self-Report, WECC issued a new data request to CSU for training records or other evidence demonstrating that the operators at the plant were familiar with Protection Systems. CSU indicated it had no training records for the four operators at issue at the time of the Compliance Audit. CSU did, however, provide training records demonstrating that since submitting its Self-Report, all operators at the plant had completed the class. WECC determined CSU was in violation of PRC-001-1 R1 for failing to provide evidence that the generator operators were familiar with the purpose and limitations of the Protection System schemes applied in its area. | PRC-001-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to understand the purpose and limitations of the Protection Systems at this plant could lead to incorrect analysis of Protection System operations, which could lead to improper response by the operators in the control room. This could potentially result in tripping of generation equipment leading to the loss of 480 MW summer/490 MW winter of available generation at this plant. Although CSU could not demonstrate through training records that its operators were familiar with the purpose and limitation of the Protection System scheme, WECC determined the violation posed a minimal risk due to the fact that the generation protection scheme is equipped with real-time monitoring and alarming. For abnormal conditions, alarming will alert the operators and allow them to respond properly to the abnormal condition. Further, CSU has implemented a strong on-the-job training program that it used to train the operators at issue. The training includes identifying the multiple Protection System elements and functions that encompass all aspects of the operation of the plant. CSU also has a Protection System engineering group that analyzes Protection System operations to identify the cause of the operations and determine whether the Protection System operated correctly. | 6/18/2007 (when the Standard became mandatory and enforceable) | 10/31/2012 (when CSU confirmed the knowledge of each operator concerning the purpose and limitations of Protection System schemes applied in that area) | 10000 | Self-Report | To mitigate this violation, CSU: 1) investigated the circumstances surrounding the preparation of the WECC audit data response; 2) verified the accuracy of all of the information in the response for each of its three power plants involved; 3) confirmed the knowledge of each operator concerning the purpose and limitations of Protection System schemes applied for the generator units at the plant; 4) required the operators at the plant at issue to complete the on-line training class in order that the organization would have a training record for each of these individuals; and 5) terminated the supervisor from his position with the organization. | 2013-01-03 | 2014-04-28 | Neither Admits nor Denies | WECC reviewed CSU's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC considered CSU's compliance history and determined there were no relevant instances of noncompliance.