## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Minnkota Power Cooperative, Inc. (MPC) | NCR01013 | MRO2012010744 | Notice of Confirmed Violation | During a Compliance Audit conducted from April 16, 2012 through April 19, 2012, MRO determined that MPC, as a Transmission Owner, was in violation of FAC-009-1 R1. MPC failed to establish Facility Ratings for its solely and jointly owned Facilities that were consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. Upon discovering the equipment and Facility Rating errors, MPC performed a full review of its ratings and determined that 19 out of 38 (50%) Facilities had incorrect ratings. Eleven of the incorrect ratings were for Facilities operated above 200 kV. Of the 230 kV and 345 kV Facility Rating errors, 4 of the 11 (36.4%) were due to incorrectly documented bus jumper ratings and 7 of the 11 (63.6%) were due to current transformer (CT) ratings that were omitted or incorrectly documented. For the 230 kV and 345 kV Facilities, a total of 25 equipment rating issues were discovered, some of which did not impact a Facility Rating. On the Center to Jamestown 345 kV line, MPC applied an incorrect rating factor to a metering CT on a free-standing CT stack. The Facility Rating changed from 720 MVA for both normal and emergency to 598 MVA normal rating and 657 MVA emergency rating. This line is an important part of the transmission system that delivers North Dakota generation to northwestern Minnesota. This line also has a North Dakota generation runback Special Protection System associated with it. On the Drayton 230 kV/115 kV Transformer T1, MPC had a metering CT rating factor that was assumed to be 1.5, but no actual rating factor was documented on nameplate. The Facility’s previous ratings ranged from 140 MVA (summer normal) to 175 MVA (winter emergency). However, the correct CT rating was 120 MVA. On the Drayton to Letellier 230 kV line, MPC failed to document the bus jumper rating. The Facility's summer normal rating was documented as 478 MVA when the correct rating was 439 MVA. This line is an important part of the interface between the United States and Canada. This line also has an Interconnection Reliability Operating Limit associated with it. On the Prairie to Ramsey 230 kV line, MPC did not document the circuit breaker bushing metering CT. The Facility’s summer and winter ratings were documented as 391 MVA and 478 MVA when the correct ratings were 321 MVA and 451 MVA. After determining that it had been using Facility Ratings which were greater than the respective most limiting elements, MPC reviewed the operational history of those Facilities and found that there were no instances where a Facility was loaded above the rating of its most limiting element. | FAC-009-1 | R1 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Nineteen of MPC’s Facility Ratings were incorrect. Eleven of the incorrect ratings were for Facilities operated above 200 kV. Out of eleven errors, seven errors were greater than 10%, and the two greatest errors were over 30%. Ten out of the eleven 230 kV and 345 kV facilities were rated higher than their most limiting element. Planning and operating simulation-based studies require accurate ratings. The results of these studies are used to plan construction of reinforcements and to establish operating criteria such that the system can withstand a variety of pre-determined contingencies. The use of inaccurate ratings compromises the validity of these studies. However, MRO determined that this violation did not pose a serious or substantial risk to the BPS because according to historical loading data, none of the Facilities operated above the actual rating of their most limiting element. Furthermore, the equipment rating discrepancies at the most critical facilities were for CTs or bus jumpers, both of which could be replaced without long outages should the need arise to change the facility’s rating back to the higher value. It should also be noted that the primary concern with overloading CTs is not that they would be physically damaged but rather that their measurement values would temporarily become less accurate. All of the CT rating issues on the more critical facilities were for metering CTs, whose accuracy would not affect Protection Systems and would therefore have a lesser impact on the BPS when overloaded. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/27/2014 (Mitigation Plan completion) | 0 | Compliance Audit | To mitigate this violation, MPC: 1) gathered and cataloged all required nameplate data and specifications for 230 kV and 345 kV transmission lines, and power transformers; 2) applied appropriate rating methodology and performed associated calculations, for 230 kV and 345 kV transmission lines, and power transformers; 3) created a spreadsheet for each facility to document associated equipment, application of appropriate rating methodology, and to summarize the overall Facility Rating for 230 kV and 345 kV transmission lines, and power transformers; 4) performed a detailed review of Facility Ratings for all remaining MPC Facilities (mainly 115 kV facilities); 5) tested new facilities databases by entering facilities data; 6) completed BPS line verification surveys; 7) reviewed substation bus conductor designs and configurations for 230 kV and 345 kV transmission lines, power transformers, and generation Facilities; 8) performed a detailed review of terminal equipment; and 9) populated the new Facility Ratings database with data from the information collected in the spreadsheets. | 2014-05-27 | 2014-06-04 | Admits | MRO reviewed MPC's internal compliance program and considered it to be a neutral factor in the penalty determination. MPC has invested $105,000.00 in a new NERC compliance management system, which will serve as a document management system. The system will streamline and automate many of the manual processes MPC currently performs to organize, generate, and report on evidence related to NERC compliance. MRO considered this investment as a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Brooklyn Navy Yard Cogeneration Partners, L.P. (BNYCP) | NCR10237 | NPCC2013013096 | Notice of Confirmed Violation | On October 9, 2013, BNYCP submitted a Self-Report stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2.1. During the 2013 transition of the facility to new ownership and operations, an internal review of BNYCP's current Protection System management and testing program was performed. BNYCP determined that there was no evidence of previous relay secondary verification testing of 54 current transformers (CTs) and 5 potential transformers (PTs). Therefore, NPCC determined that BNYCP was in violation of PRC-005-1 R2.1 because BNYCP failed to perform secondary verification of its PTs and CTs which comprise 100% of BNYCP's applicable Protection System devices. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By failing to perform secondary verification of its CTs and PTs to their relays creates the potential that these Protection System devices might not have operated as intended. However, the risk was mitigated because although CT and PT verification was not performed, all other aspects of their relay protection testing was performed within the defined intervals. According to its records and past practices, BNYCP was following what was considered the industry standard for CTs and PTs, which included testing on commissioning, cleaning in place, visual inspection and replacement if necessary. Further, during the violation period, real-time relay operations operated as per design and a review determined there were no relay mis-operations. In addition the CTs and PTs go to Microprocessor relays and BNYCP operators would see an alarm in the control room indicating trouble which they would investigate immediately. | 4/8/2008 (when BNYCP registered as a GO) | present | 0 | Self-Report | To mitigate the violation, BNYCP 1) completed commissioning of new relays and installing of new CTs and PTs; 2) completed review of historical testing and documentation associated with the Protection System devices; 3) reviewed and updated its relay maintenance and testing procedure to include testing of CTs and PTs; 4) identified CTs and PTs to be tested, methodology of performing testing, and updated its database to incorporate testing requirements for testing; and 5) scheduled CT/PT testing. To mitigate the violation, BNYCP will: 6) complete testing of transformer CT/PTs; and 7) complete testing of CT/PTs associated with the 138 kV line. | 12/31/2014 (approved completion date) | TBD | Does Not Contest | NPCC considered that this was BNYCP's first violation of PRC-005-1 and that the violation was self-reported when assessing a zero dollar penalty for the violation. Although the violation resolved by this agreement involves a minimal risk issue that would otherwise be eligible for Find, Fix, and Track (FFT) treatment, the mitigating activities cannot be completed within or near the 90 day limit for unmitigated FFTs as BNYCP needed to coordinate an outage to facilitate the remaining testing. Therefore, NPCC and BNYCP are resolving this violation via the instant Notice of Confirmed Violation with no associated monetary penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Entergy Nuclear Generation Company (ENGC) | NCR07072 | NPCC2013012287 | Settlement Agreement | During a Compliance Audit conducted from November 7, 2012 through December 17, 2013, NPCC determined that ENGC, as a Generator Owner (GO) and Transmission Owner (TO), was in violation of PRC-005-1 R1.1 and R1.2. ENGC does not include the verification of current transformers (CT), potential transformers (PT), and coupling capacitor voltage transformers (CCVT) secondary output values to the inputs of the associated protective relays in its Protection System maintenance and testing program. The program also does not verify the proper secondary values as well as the wiring continuity and integrity from the sensing devices to their associated protective relays. The protective relays ENGC utilizes for the generator, generator step-up transformer, and the switchyard equipment do not self-monitor or self-check the AC voltage and current input integrity from their associated CTs, PTs or CCVTs, and they do not initiate failure alarms (associated with AC input signal integrity) which are annunciated to a twenty-four hours a day, seven days a week staffed operations center that can initiate an investigation of the problem. | PRC-005-1 | R1; R1.1; R1.2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation created a moderate risk because of the potential that these devices might not have operated as intended. However, the risk was mitigated because, although verification of secondary values of CTs, PTs, and CCVTs is not in ENGC's Protection System maintenance and testing program, ENGC performed other testing which provides assurance that the AC portion of the circuit is functioning properly. For CTs, ENGC includes monthly visual inspections of CT leads, six-year preventative maintenance of the CT leads, verification of tightness of bolted electrical connections, resistance measurements through bolted connections, insulation resistance test (megger) of CT circuit, ratio testing, and excitation testing. For PTs, fuses are replaced on a twelve-year interval. For CCVTs, monthly visual inspections and six month corona surveys are performed, and six-year maintenance is performed to verify tightness of bolted electrical connections, resistance measurements through all bolted connections, device cleaning, and power factor testing. Entergy has a detailed maintenance and testing program. Its testing is up to date and well documented. With the exception of the CT/PT/CCVT verification of inputs to the relay, ENGC performs all other required testing and testing has been performed according to its intervals. Also, during the violation period, real-time relay operations operated as per design and a review determined there were no relay misoperations. | 6/21/2007 (when ENGC registered as a GO and TO) | present | $20,000 (for NPCC2013012287 and NPCC2013012288) | Compliance Audit | To mitigate the violation, ENGC: 1) revised ENGC's maintenance procedure for relay input verification testing; 2) scheduled performance of relay input verification testing; 3) performed relay input verification testing; and 4) submitted a lessons learned into the Entergy Fleet Operating Experience Program. | 12/31/2014 (approved completion date) | TBD | Does Not Contest | NPCC considered ENGC's internal compliance program (ICP) as a mitigating factor in the penalty determination. ENGC's ICP is a multi-layered program that presents policy, procedural, control and behavioral expectations to employees, agents and contractors to prevent and detect violations of regulatory requirements and has the full commitment of senior management. Training and communications are afforded to keep personnel familiar with the requirements and updated on changes. Open lines of communication are available for employees to communicate with management without fear of retaliation.
Northeast Power Coordinating Council, Inc. (NPCC) | Entergy Nuclear Generation Company (ENGC) | NCR07072 | NPCC2013012288 | Settlement Agreement | During a Compliance Audit conducted from November 7, 2012 through December 17, 2013, NPCC determined that ENGC, as a Generator Owner (GO) and Transmission Owner (TO), was in violation of PRC-005-1 R2.1 and 2.2. ENGC does not include the verification of current transformers (CT), potential transformers (PT), and coupling capacitor voltage transformers (CCVT) secondary output values to the inputs of the associated protective relays in its Protection System maintenance and testing program. The program also does not verify the proper secondary values as well as the wiring continuity and integrity from the sensing devices to their associated protective relays. The protective relays ENGC utilizes for the generator, generator step-up transformer, and the switchyard equipment do not self-monitor or self-check the AC voltage and current input integrity from their associated CTs, PTs or CCVTs, and they do not initiate failure alarms (associated with AC input signal integrity) which are annunciated to a twenty-four hours a day, seven days a week staffed operations center that can initiate an investigation of the problem. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation created a moderate risk because of the potential that these devices might not have operated as intended. However, the risk was mitigated because, although verification of secondary values of CTs, PTs, and CCVTs were not performed, ENGC performed other testing which provides assurance that the AC portion of the circuit is functioning properly. For CTs, ENGC includes monthly visual inspections of CT leads, six-year preventative maintenance of the CT leads, verification of tightness of bolted electrical connections, resistance measurements through bolted connections, insulation resistance test (megger) of CT circuit, ratio testing, and excitation testing. For PTs, fuses are replaced on a twelve-year interval. For CCVTs, monthly visual inspections and six-month corona surveys are performed, and six-year maintenance is performed to verify tightness of bolted electrical connections, resistance measurements through all bolted connections, device cleaning, and power factor testing. Entergy has a detailed maintenance and testing program. Its testing is up to date and well documented. With the exception of the CT/PT/CCVT verification of inputs to the relay, ENGC performs all other required testing and testing has been performed according to its intervals. Also, during the violation period, real-time relay operations operated as per design and a review determined there were no relay misoperations. | 6/21/2007 (when ENGC registered as a GO and TO) | present | $20,000 (for NPCC2013012287 and NPCC2013012288) | Compliance Audit | To mitigate the violation, ENGC: 1) revised ENGC's maintenance procedure for relay input verification testing; 2) scheduled performance of relay input verification testing; 3) performed relay input verification testing; and 4) submitted a lessons learned into the Entergy Fleet Operating Experience Program. | 12/31/2014 (approved completion date) | TBD | Does Not Contest | NPCC considered ENGC's internal compliance program (ICP) a factor in the penalty determination. ENGC's ICP is a multi-layered program that presents policy, procedural, control and behavioral expectations to employees, agents and contractors to prevent and detect violations of regulatory requirements and has the full commitment of senior management. Training and communications are afforded to keep personnel familiar with the requirements and updated on changes. Open lines of communication are available for employees to communicate with management without fear of retaliation.
Northeast Power Coordinating Council, Inc. (NPCC) | Milford Power, LLC | NCR07143 | NPCC2013012750 | Notice of Confirmed Violation | On July 31, 2013, Milford Power, LLC , submitted a Self-Report stating that as a Generator Owner (GO), it was in violation of PRC-005-1 R2.1. During an internal review of PRC-005, Milford Power, LLC determined that Protection System devices were not maintained and tested within the defined intervals. Specifically, 31 out of 33 DC control circuits (94%) were not tested end to end, 168 instrument transformers (100%) were not secondary tested to the relay, and 11 out of 103 relays (11%) were not tested within the defined testing interval. For the DC control circuit testing, individual breaker testing had been completed, but for 31 circuits the entire circuit was not tested to determine proper operation of the DC control circuitry. All 168 instrument transformers had been tested according to the InterNational Electrical Testing Association (NETA) Standards since 1992, but verification from the sensing transformer to the protective device had not been performed. The transformers had not been included in the inventory of devices subject to testing under PRC-005-1. The failure to test all of the DC control circuitry was a result of an incomplete understanding of the requirements for maintenance and testing. | PRC-005-1 | R2; 2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Protection System devices that are not properly tested can lead to misoperations and damage to other equipment if they are not functioning correctly during an event. However, there were no relay misoperations during the period of the violation, and station trips that occurred had minimal impact on the BPS. In addition the CTs and PTs go to microprocessor relays and Milford operators would see an alarm in the control room indicating trouble which they would investigate immediately. | 6/21/2007 (when Milford Power, LLC registered as a GO) | 12/20/2013 (Mitigation Plan completion) | 12000 | Self-Report | To mitigate this violation, Milford Power, LLC: 1) completed testing of all Protection System devices at issue; and 2) updated the inventory of components subject to the maintenance and testing of PRC-005 to include the components previously not listed, including the basis for testing, testing intervals, and required testing date(s). | 2013-12-20 | 2014-03-20 | Does Not Contest | NPCC reviewed Milford Power, LLC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC found that Milford Power, LLC utilizes its parent company GDF SUEZ Energy Generation NA's ICP which addresses compliance for all its regulated subsidiaries. The ICP describes the roles and responsibilities for all employees and discusses compliance structure, oversight, monitoring, audits, reporting requirements, training, and the tasks required to comply with all mandatory NERC Reliability Standards. The ICP is developed, approved, and overseen by senior management, independent from the departments responsible for compliance with the NERC Reliability Standards. NPCC also considered the cooperation of Milford Power, LLC while processing the violation, as well as the fact that the violation was self-reported as mitigating factors in assessing the penalty. A Settlement Agreement covering two violations of PRC-005 R2 for ANP Blackstone Energy Company, a Milford Power, LLC affiliate, was filed with FERC under NP14-40-000 on April 30, 2014. On May 29, 2014 , FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005 R2 for ANP Bellingham Energy Company was filed with FERC under RC13-9-000 on May 30, 2013. The 60-day review period passed on July 29, 2013. NPCC considered the violation history of Milford Power, LLC's affiliates when deciding to apply a penalty to the present violation.
SERC Reliability Corporation (SERC) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | SERC2013012999 | Settlement Agreement | On August 23, 2013, SERC sent ODEC a notice of a Compliance Audit scheduled for February 3, 2014 through February 21, 2014. On October 1, 2013, ODEC submitted a Self-Report to SERC stating that, as a Generator Owner, it was in violation of PRC-005-1b R1. ODEC failed to implement its Protection System maintenance and testing program for its DC control circuits because it misinterpreted the Standard and requirement. SERC reviewed the evidence and determined that the issue was in fact a violation of PRC-005-1 R2.1 rather than PRC-005-1b R1. ODEC’s Protection System maintenance and testing program included DC control circuits. However, ODEC did not test these devices in accordance with its Protection System maintenance and testing program. SERC reviewed spreadsheets compiled by ODEC which provided a complete inventory of its Protection System devices. The spreadsheets also included each device’s defined intervals and all test dates for each Protection System device. Of the 460 Protection System devices included in these spreadsheets, ODEC failed to test and maintain 100% of its DC control circuitry devices within the defined intervals. ODEC's 82 DC control circuitry devices made up 17.8% of its total number of Protection System devices. The 82 DC control circuitry devices are located at the Louisa and March Run generating stations. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because if the DC control circuitry had failed, ODEC could have lost 1,000 MW of generation. ODEC failed to test 100% of its DC control circuits. The DC control circuitry maintenance and testing program was set at five-year intervals. Initially, the Louisa generating facility was commissioned in 2003 and the March Run generating facility was commissioned in 2004, the devices should have been tested in 2009. ODEC missed the interval by four years. However, the generators involved, totaling approximately 1,000 MW, are located at two separate locations, reducing the risk of simultaneous loss of the generators, and the generators represent less than 1% of the total generation in the Balancing Authority and Reliability Coordinator areas. In addition, one of the areas of untested DC control circuitry trips about 400 feet of overhead line within the fenced area of each generation plant, making a fault unlikely on that section. Finally, the Transmission Owner and each generation plant have overlapping differential protection schemes that could isolate a fault and minimize disruption or damage to a larger section of the BPS. | 5/28/2009 (when ODEC should have tested the Marsh Run DC control circuit devices) | 10/26/2013 (Mitigation Plan completion) | $15,000 | Self-Report | To mitigate this violation, ODEC: 1) tested the DC control circuitry at the Louisa Generating Facility and the Marsh Run Generating Facility; and 2) incorporated its testing information from these tests and all DC control circuitry and the required intervals into its testing and maintenance planning/scheduling system. | 2013-10-26 | 2014-05-09 | Admits | SERC reviewed ODEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ODEC's ICP has been in place since December 21, 2011 and was updated most recently on October 2, 2013. ODEC has posted its ICP on a company-wide, publicly available website, making it available to all ODEC employees. ODEC has a NERC compliance officer who has overall approval authority for, and internal oversight of, the ICP. The NERC compliance officer also has direct access to ODEC's chief executive officer and the ODEC board of directors. ODEC has a NERC compliance specialist responsible for overseeing the implementation of and day-to-day compliance with the NERC Reliability Standards. ODEC's NERC compliance specialist conducts an annual internal audit of the ICP, and ODEC performs interim reviews of its procedures in light of new Standards, new versions of Standards, or other NERC guidance documents. ODEC conducts annual training on complying with the NERC Reliability Standards and publishes a newsletter each quarter which addresses timely topics for compliance. ODEC did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered ODEC's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Project II, LLC (Smoky II) | NCR10316 | SPP201000201 | Settlement Agreement | On January 18, 2010, Smoky II submitted a Self-Certification stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. During a Compliance Audit conducted from July 8, 2013 through July 9, 2013, SPP RE determined that Smoky II performed testing of it Protection System devices in December of 2012, but did not maintain all of the equipment identified in its Program. Specifically three transformer fans on Smoky II’s step-up transformer, which were identified as Protection System devices in Smoky II’s Program, did not work properly, and Smoky II had not repaired the failed fans. SPP RE determined that Smoky II did not have evidence that all 30 of its Protection System devices (5 relays, 1 DC circuitry, 3 capacitor coupled voltage transformers, 18 multi-ratio bushing CTs, 2 associated communications, and 1 battery bank) were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (Program). Although all of Smoky II’s Protection System devices were functionally tested during the commissioning of Smoky II in September of 2008, only its five Protection System relays had current tests reports on record (tested in February 2010) when Smoky II implemented its Program on November 2, 2010 (Version 1.0). Subsequent to implementation of Version 1.0 and a one calendar year interval for maintenance and testing of all of its Protection System devices, Smokey II failed to maintain or test all 30 of its Protection System devices in 2011. | PRC-005-1 | R2; R2.1, R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Smoky II provided evidence that it tested all of its Protective System devices during commissioning in 2008. Subsequent to the commissioning tests, five relays (16.7% of the Protection System devices) were tested in 2010 and all Protection System devices were tested in 2012. Although testing was not performed within the one-year interval established in the Smoky II Program, the testing was, with the exception of a battery bank, performed within the maintenance and testing intervals for Protection System devices established in the NERC Protection System Maintenance Technical Reference. The deficiencies relating to the three transformer fans identified during the testing performed in 2012 do not relate to Protection System equipment, and except for Smoky II including its step-up transformer in its Program, would not have resulted in a violation of PRC-005 R2. Because Smoky II is a wind farm with a maximum capacity of 148.5 MW, SPP RE views the transformer maintenance deficiencies as a minimal threat to BPS reliability. | 4/3/2009 (when Smoky II registered as a GO) | 5/22/2013 (Mitigation Plan completion) | $28,000 | Self-Certification | To mitigate this violation, Smoky II: 1) collected PRC-005 related documents and centralized them, and dispersed a new PRC-005 manual to employees; 2) trained employees on its PRC-005 manual; and 3) tested its Protection System devices in accordance with the PRC-005 manual. | 2013-05-22 | 5/27/2014 | Neither Admits nor Denies | SPP RE reviewed Smoky IIs internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Enel Green Power - North America (EGPNA) represents Smoky II regarding compliance matters. EGPNA did not provide evidence that it had completed the mitigation plan for its violation of PRC-005-1 R2 in a timely manner. Similarly, EGPNA did not provided adequate status updates for its Mitigation Plan prior to completion. The SPP RE Compliance Audit Team noted that during the audit conducted from July 8, 2013 through July 9, 2013, EGPNA missed required audit evidence submission dates, provided insufficient compliance documentation, submitted documentation with discrepancies and errors, and failed to provide status reports explaining the progress of its audit evidence submittals. SPP RE considered EPGNA's unresponsiveness as an aggravating factor in penalty determination. EGPNA noted that this referenced violation took place at a time when the company was developing a formal NERC Compliance Program and subsequent audits have indicated a more mature program and approach to NERC matters today. SPP RE considered the improvements to the EPGNA ICP as a mitigating factor in the penalty determination. A Notice of Confirmed Violation covering a violation of PRC-005-1 R2 for Smoky Hills Wind Project, LLC (Smoky I), an affiliate of Smoky II, was filed with FERC under NP14-34-000 on February 27, 2014. On March 28, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Notwithstanding the closure of the Smoky I violation on March 28, 2014, the Smoky II violation occurred approximately one year before the Smoky I violation. Therefore, SPP RE did not consider the Smoky I violation a prior violation and an aggravating factor in the penalty determination.
Western Electricity Coordinating Council, Inc. (WECC) | Elk Hills Power, LLC (EHP) | NCR05143 | WECC2014013887 | Settlement Agreement | During a Compliance Audit conducted from May 21, 2014 through May 22, 2014, WECC determined that EHP, as a Generator Owner, was in violation of PRC-005-1 R1. EHP’s Protection System maintenance and testing program (PMTP) failed to define intervals for relays and instrument transformers. EHP’s PMTP contained a requirement to test relays every three to five years. However, EHPs program also allowed that “if extenuating circumstances occur which prevent testing within five years or if it is determined that the five year time period has lapsed for a device, testing shall be on a documented scheduled [sic] to take place in the next planned maintenance outage.” There was no limitation placed on the number of times the exception may be used, consecutively or otherwise. As such, this exception, if used, created an instance where there is no interval in which a device must be tested. Regarding instrument transformers, EHP’s PMTP included testing of current transformers (CT) upon commissioning in 2003, but required no further routine maintenance or testing. Potential transformer (PT) testing was only required when “performance is suspect.” Neither required an interval-based maintenance and testing schedule. WECC determined that EHP’s failure to include defined intervals in its PMTP for 100% of its relays and for 100% of its instrument transformers is a violation of PRC-005-1 R1. WECC determined that although EHP had a Protection System maintenance and testing program for Protection Systems that affect the reliability of the bulk power system (BPS), the maintenance and testing intervals and their basis were missing or incomplete. WECC further determined that the root cause of the violation was EHP's lack of compliance understanding. | PRC-005-1 | R1; R1.1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. EHP failed to define maintenance and testing intervals for instrument transformers and relays. As a result, EHP could not provide documentation evidencing that these devices were being tested and maintained. Maintaining and testing Protection System devices helps to determine if the devices are reliable to limit the effects of disturbances in a system network. If the systems are not maintained and tested, the systems cannot be certified to operate as planned and forestall disturbances that may damage the transmission system and/or generation plants. If instrument transformers are not maintained and tested, incorrect values could be fed to the relays, potentially causing a relay misoperation. Similarly, failure to maintain and test relays could lead to a relay trip, or the failure of a relay to trip when required. Such failures could lead to a loss of 550 MW of load. As a compensating controls, there is no evidence to suggest that EHP ever used the relay maintenance exception. Also the subset of transformer devices that are visible are subject to monthly inspections. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/28/2014 (Mitigation Plan completion) | $0 (for WECC2014013887 and WECC2014013888) | Compliance Audit | To mitigate this violation, EHP: 1) modified its maintenance and testing program to eliminate the exception language; 2) modified its maintenance and testing program to include intervals and maintenance activity for voltage and current sensing devices; and 3) provided training on the modified programs. | 5/28/2014 | TBD | Does Not Contest | A Settlement Agreement covering violations of PRC-005-1 R1 and PRC-005-1 R2 for EHP was filed with FERC under NP10-124-000 on July 6, 2010. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that EHP's compliance history should not serve as a basis for aggravating the penalty. In the violations filed under NP10-124-000, WECC determined that EHP failed to have a complete PMTP that covered all Protection System devices. After these violations, EHP submitted a Mitigation Plan. On August 22, 2008, WECC accepted the Mitigation Plan. EHP completed its Mitigation Plan and on October 1, 2008, WECC verified completion of EHP’s Mitigation Plan. In verifying completion, WECC relied on evidence provided by EHP. That evidence indicated that the Protection System maintenance and testing program language at issue in the current violation was present on completion of EHP’s 2008 Mitigation Plan. Enforcement recognizes that WECC’s approval of the 2008 Certification of Mitigation Plan Completion with respect to having a PMTP which was not compliant with the Standard perpetuated EHP's error with respect to having defined maintenance and testing intervals for relays and instrument transformers, resulting in the current violation. Because WECC failed to find the current violation after review of EHP's Certification of Mitigation Plan Completion, WECC determined a zero dollar penalty was warranted.
Western Electricity Coordinating Council, Inc. (WECC) | Elk Hills Power, LLC (EHP) | NCR05143 | WECC2014013888 | Settlement Agreement | During a Compliance Audit conducted from May 21, 2014 through May 22, 2014, WECC determined that EHP, as a Generator Owner, was in violation of PRC-005-1 R2. EHP's Protection System maintenance and testing program (PMTP) did not include intervals for all relays and instrument transformers. As a result, EHP could not provide evidence of maintenance and testing for all relays and instrument transformers that affect the reliability of the bulk power system (BPS). EHP's PMTP does require monthly visual inspections of transformers, however, these inspections only include visible devices. EHP failed to provide evidence that most instrument transformers have received any maintenance, testing or inspection following commission. WECC determined that EHP’s failure to provide evidence indicating that its Protection System devices were tested and maintained is a violation of PRC-005-1 R2. WECC determined the root cause of the violation was EHP's lack of compliance understanding. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. EHP failed to define maintenance and testing intervals for instrument transformers and relays. As a result, EHP could not provide documentation evidencing that these devices were being tested and maintained. Maintaining and testing Protection System devices helps to determine if the devices are reliable to limit the effects of disturbances in a system network. If the systems are not maintained and tested, the systems cannot be certified to operate as planned and forestall disturbances that may damage the transmission system and/or generation plants. If instrument transformers are not maintained and tested, incorrect values could be fed to the relays, potentially causing a relay misoperation. Similarly, failure to maintain and test relays could lead to a relay trip, or the failure of a relay to trip when required. Such failures could lead to a loss of 550 MW of load. As compensating controls, there is no evidence to suggest that EHP ever used the relay maintenance exception. Also the subset of transformer devices that are visible are subject to monthly inspections. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/28/2014 (Mitigation Plan completion) | $0 (for WECC2014013887 and WECC2014013888) | Compliance Audit | To mitigate this violation, EHP: 1) maintained relays and instrument transformers in accordance with EHP's updated maintenance and testing program; and 2) maintained relevant test records on site. | 2014-05-28 | TBD | Does Not Contest | A Settlement Agreement covering violations of PRC-005-1 R1 and PRC-005-1 R2 for EHP was filed with FERC under NP10-124-000 on July 6, 2010. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that EHP's compliance history should not serve as a basis for aggravating the penalty. In the violations filed under NP10-124-000, WECC determined that EHP failed to have a complete PMTP that covered all Protection System devices. After these violations, EHP submitted a Mitigation Plan. On August 22, 2008, WECC accepted the Mitigation Plan. EHP completed its Mitigation Plan and on October 1, 2008, WECC verified completion of EHP’s Mitigation Plan. In verifying completion, WECC relied on evidence provided by EHP. That evidence indicated that the Protection System maintenance and testing program language at issue in the current violation was present on completion of EHP’s 2008 Mitigation Plan. Enforcement recognizes that WECC’s approval of the 2008 Certification of Mitigation Plan Completion with respect to having a PMTP which was not compliant with the Standard perpetuated EHP's error with respect to having defined maintenance and testing intervals for relays and instrument transformers, resulting in the current violation. Because WECC failed to find the current violation after review of EHP's Certification of Mitigation Plan Completion, WECC determined a zero dollar penalty was warranted.