## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Minnesota Power (Allete, Inc.) (MP) | NCR00674 | MRO2012011503 | Notice of Confirmed Violation | During a Compliance Audit conducted from September 24, 2012 through September 28, 2012, MRO determined that MP, as a Generator Owner and Transmission Owner, was in violation of PRC-005-1 R2. MP failed to provide evidence its Protection System devices were maintained and tested within the defined intervals, as required by PRC-005-1 R2.1, and failed to provide the date that each Protection System device was last tested/maintained, as required by PRC-005-1 R2.2. During the Compliance Audit, MP did not provide evidence that four Protection System station batteries were maintained and tested within their defined intervals. For the four station batteries, eight requested records were not provided. While mitigating the issue, MP performed a comprehensive review of its Protection System maintenance and testing records. MP has 7,959 Protection System devices subject to PRC-005-1 R2, including 2,032 relays, 95 associated communication systems, 94 station batteries, 573 DC control circuits, 4,369 current transformers (CTs), and 796 potential transformers (PTs). During this comprehensive review, MP discovered that its Protection System preventative maintenance technicians did not download the relay settings of microprocessor relays to verify the settings were set as designed as required by its program. MP identified 586 microprocessor relays with incomplete records. In addition to the 586 microprocessor relay records, MP identified 202 missing or incomplete device maintenance and testing records related to station batteries, DC control circuitry, current and voltage sensing devices and Protection System communication devices. In total, MP was not able to provide maintenance and testing records for 788 devices, or approximately 10% of its Protection System devices. The root cause of this violation was that MP's technicians were not following the Protection System maintenance and testing program, which led to incomplete testing and documentation. MP reported that technician training was not consistent, and therefore, documentation was not consistently retained. Additionally, some of MP's customers performed the maintenance and testing, which led to inconsistent performance and documentation. | PRC-005-1 | R2: R2.1; R2.2 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The missing Protection System maintenance and testing records represented assets from small hydro generators all the way up to the 500 kV switchyard at Forbes, which is associated with an Interconnection Reliability Operating Limit (IROL) flow gate. Although MP was not able to provide approximately 10% of its Protection System maintenance and testing records, the risk was partially mitigated by continuous monitoring of the DC control circuitry and CTs/PTs and Protection System communications devices, which represented 25% of the missing or incomplete maintenance and testing records. | 6/18/2007 (when the Standard became mandatory and enforceable) | present | $0 (for MRO2012011503 and MRO2012011504) | Compliance Audit | To mitigate this violation, MP: 1) performed a comprehensive review of its maintenance and testing of Protection System devices; 2) performed maintenance and testing on the Protection System devices with missing records; 3) Tech System technicians assumed responsibility for testing all MP Protection System batteries, including those at generating facilities, and customer owned batteries; 4) provided training to the Protection System technicians to ensure all technicians understood the required maintenance and testing of Protection System devices and documentation of the work completed; 5) purchased software to facilitate testing required by PRC-005-1; 6) added CTs, PTs and DC control circuitry to the database; and 7) scheduled maintenance and testing to be completed on all devices by September 1, 2014. | 10/1/2015 (approved completion date) | TBD | Admits | MRO reviewed MP's internal compliance program and considered it to be a neutral factor in the penalty determination. After the Compliance Audit, MP invested approximately $800,000 in software and consulting services to improve compliance, internal controls, and document retention for PRC-005-1 and PRC-008-0. MP also created test routines, created import and export settings for test results, and developed internal procedures to be used with the new software system. MRO considered these investments as mitigating factors which reduced the penalty.
Midwest Reliability Organization (MRO) | Minnesota Power (Allete, Inc.) (MP) | NCR00674 | MRO2012011504 | Notice of Confirmed Violation | During a Compliance Audit conducted from September 24, 2012 through September 28, 2012, MRO determined that MP, as a Distribution Provider and Transmission Owner, was in violation of PRC-008-0 R2. MP failed to provide evidence of maintenance and testing records for Under Frequency Load Shedding (UFLS) equipment, as required by PRC-008-0 R2. During the Compliance Audit, MRO discovered that MP did not have evidence of maintenance and testing for Riverton Substation (potential transformer (PT) testing) and Brainerd Substation (PT and DC Control Circuitry testing). The Brainerd UFLS was installed in 2008. Upon discovering the issue, MP performed a comprehensive review of its UFLS maintenance and testing records. The review identified an additional eight UFLS elements (PTs) that did not have any documentation of voltage checks. MP has 162 UFLS devices subject to PRC-008-0 R2, including 48 relays, 48 control circuits, 33 PTs, and 33 batteries. MP failed to provide maintenance and testing evidence for 10 devices, or approximately 6%. Prior to the Compliance Audit, MP UFLS equipment maintenance was performed by MP staff, contractors and MP customers. After the audit, MP added all customer-owned equipment into its Maximo database in order to more effectively manage maintenance of the UFLS elements identified in its UFLS program. The root cause of this violation was that MP's technicians were not following the UFLS maintenance and testing program, which led to incomplete testing and documentation. MP reported that technician training was not consistent, and therefore, documentation was not consistently retained. Additionally, some of MP's customers performed the maintenance and testing, which led to inconsistent performance and documentation. | PRC-008-0 | R2 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MP failed to provide maintenance and testing records for ten UFLS devices. MP's UFLS obligation to the BPS is 420 MW. The circuits at issue represent 50% (211 MW) of MP's overall load shed capability. However, any disruptions to the protection system would be identified and an alarm sent to the control center. After MP completed the maintenance and testing of the UFLS devices, only one relay required recalibration to the desired set point and all other elements functioned as expected. Therefore, MRO determined that this violation posed a moderate risk to the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2/28/2014 (Mitigation Plan completion) | $0 (for MRO2012011503 and MRO2012011504) | Compliance Audit | To mitigate this violation, MP: 1) completed maintenance and testing of UFLS devices; 2) discussed proper completion of the UFLS function test forms with MP technicians at a staff meeting; 3) performed independent maintenance and testing of customer-owned UFLS relays and batteries to ensure that it was completed correctly; 4) added all customer-owned UFLS relays to the Maximo work order system to ensure timely notification of upcoming testing and maintenance requirements to ensure accurate records and notification of upcoming required maintenance activities and will facilitate the continuation of an existing internal control whereby random samples of testing records are reviewed on a periodic basis; and 5) completed a comprehensive review of maintenance and testing records for all MP and customer-owned UFLS relays. | 2014-02-28 | 2014-04-07 | Admits | MRO reviewed MP's internal compliance program and considered it to be a neutral factor in the penalty determination. After the Compliance Audit, MP invested approximately $800,000 in software and consulting services to improve compliance, internal controls, and document retention for PRC-005-1 and PRC-008-0. MP also created test routines, created import and export settings for test results, and developed internal procedures to be used with the new software system. MRO considered these investments as mitigating factors which reduced the penalty. A Settlement Agreement covering a violation of PRC-008-0 R2 (MRO200900095) for MP was filed with FERC under NP11-8-000 on November 5, 2010. On December 3, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. MRO did not consider MP’s PRC-008-0 R2 compliance history to be an aggravating factor in the penalty determination because in that case, MP failed to test one of its UFLS relays and the issue posed a minimal risk to the BPS.
SERC Reliability Corporation (SERC) | Southern Company Services, Inc. - Trans (SCS-Trans) | NCR01320 | SERC2013012359 | Settlement Agreement | On May 2, 2013, SCS-Trans submitted a Self-Report to SERC stating that, as a Transmission Operator, it was in violation of TOP-002-2.1b R11. On two occasions, SCS-Trans’ updated Bulk Electric System (BES) studies failed to reflect current system conditions. Specifically, two unscheduled outages of Protection System components, one for a 500 kV transmission line and one for a 230 kV transmission line, were not considered in SCS-Trans’ operating studies. On December 4, 2012, the Scherer – O'Hara 500 kV line was removed from service as part of a planned and coordinated capital construction project. On December 10, 2012, a field engineer opened the relay cut-out switches in the Plant Scherer substation, according to normal practice, in order to prevent an inadvertent relay operation while updating relay settings in the line protection panel on the Scherer end of the Scherer – O'Hara 500 kV line. This field engineer did not tag the abnormal position of the relay protection cutouts. When the field engineer disabled the line protection, the operator received an alarm and acknowledged it after discussion with the field engineer. Once acknowledged, the alarm automatically moved from the active alarm page in the energy management system (EMS) to a separate acknowledged alarm page. Later that night, pursuant to routine practice, the acknowledged alarms were deleted from the acknowledged alarm page. However the abnormal status of the relay cutout switches remained available to operations personnel in another EMS display. On December 11, 2012, the field engineer completed the relay work but failed to return the cut-out switches to their normally closed position and did not complete the final checks required by procedures before contacting the system operator to notify him or her of the completion of work activities. On December 17, 2012, the Scherer – O'Hara line was returned to service without the line protection in service. The operator who switched the line back into service failed to notice the abnormal status of these relay cutout switches in the EMS before completing the switching. The line protection on the Scherer end of the line remained out of service until January 8, 2013, when the engineer realized the error, notified the Georgia Control Center and returned the relays to service. On July 26, 2013, SCS-Trans informed SERC that, during its internal assessment of this violation, it identified another instance where studies did not reflect current system conditions. SCS-Trans’s operating studies did not reflect an unscheduled outage of Protection System components for a 230 kV transmission line that was removed from service as part of a planned capital construction outage at the Lansing Smith substation, beginning in February 2013. Similar to the incident involving the Scherer – O’Hara line, the relay cutout switches were left in an abnormal position without being tagged. Once the work was completed, field personnel associated with the capital construction work did not return the relay cutout switches to their normally closed position and the required final checks were not completed before the line was returned to service. On April 17, 2013, SCS-Trans returned the Lansing Smith – Callaway 230 kV transmission line to service without restoring the line protection. The operator who switched the line back into service failed to associate an acknowledged alarm with the Lansing Smith – Callaway 230 kV transmission line relay protection scheme. SCS-Trans determined that this error was due to the use of an aggregated alarm that made it difficult to distinguish the Lansing Smith – Callaway 230 kV relay cutout switch alarms from other expected equipment alarms associated with the capital construction work. The line protection remained out of service until June 2, 2013, when the Gulf Control Center recognized the error, notified the protection and control group, and returned the relays to service. SCS-Trans determined that this violation resulted from the combination of two human errors: (1) the failure of field personnel to properly follow documented guidelines and procedures and (2) the failure of system operators to notice abnormal conditions for the two transmission lines prior to returning the lines to service. SCS-Trans did not experience any real-time operational issues resulting from its failure to evaluate the unscheduled outages of Protection System components on either the Scherer-O’Hara or the Lansing Smith – Callaway lines. The violations impacted current-day and next-day studies. Current day studies did not accurately reflect system conditions for the period when the lines were placed in service without protection until the protection schemes were returned to service. Next-day studies did not accurately reflect system conditions. | TOP-002-2.1b | R11 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SCS-Trans’ BES studies failed to reflect current system conditions which resulted in analyses which did not include all the lines and generation that could have been lost had a fault occurred. A fault on either could have resulted in the loss of additional lines and/or generation depending on the type and location of the fault. However, the other lines at both the Scherer and Lansing Smith substations had protection schemes in service at the time of the violation. In addition, the failures occurred in different locations at different times. Also, SCS-Trans subsequently conducted informal assessments for the Scherer – O’Hara incident that included contingency analyses evaluating the system for the period during which the Protection Systems were out of service. These assessments did identify some potential overload conditions, but a review of the identified conditions indicated that they could have been mitigated utilizing congestion management tools such as system reconfiguration, generation redispatch, and transaction curtailments. The protection schemes on the other three lines at the Scherer 500 kV substation were in service when the O’Hara 500 kV line was returned to service on December 17, 2012. All of the lines connected to the Scherer substation have primary distance, primary pilot, secondary distance, and secondary pilot relay protection schemes. Both pilot schemes employ directional comparison un-blocking schemes and both distance schemes employ step zone distance schemes. In addition, the Scherer substation is configured in a breaker and a half configuration with redundant primary and secondary bus differential protection schemes employed on both collector buses. These protection schemes and all generation unit and generator step-up transformer relay protections were also in service. The Protection Systems on the other five lines, the 230/115 kV autobank transformer, and generator step-up (GSU) transformer at the Lansing Smith 230 kV substation were in service when the Callaway 230 kV line was returned to service on April 17, 2013. All five lines had primary and secondary protection schemes (a mix of directional comparison blocking, permissive over-reaching transfer trip, and step distance schemes). Three of the five lines had ground overcurrent protection. The autobank had primary and secondary differential and backup high-side overcurrent schemes and the autobank ring terminal had bank high-side and low-side differential schemes. The GSU transformer had a GSU differential that wraps the generator and transformer and neutral overcurrent protection. In addition, all the breakers in the ring bus had breaker failure protection. In addition to the informal assessment for the Scherer-O’Hara incident, SCS-Trans also reviewed TPL Category D studies for both incidents. For the Scherer – O’Hara incident, the TPL studies found that, despite the loss of the Scherer substation and all 500 kV lines connected to it, resulting in the loss of approximately 3,500 MW of generation and 102 MW of load (100 MW of which is station service load for Plant Scherer), there would be no voltage or thermal problems. In the Lansing Smith – Callaway incident, the TPL Category D studies assumed the loss of all three Lansing Smith generating units, all five 230 kV transmission lines out of Lansing Smith, and the Lansing Smith 230/115 kV autobank. These TPL studies, which assumed summer peak demand, found there would be an anticipated loss of 751 MW of generation and approximately 175 MW of load near the Lansing Smith area due to thermal and voltage issues in the area. However, the Lansing Smith – Callaway incident occurred during the spring, when loads would be lower than summer peak demands, so the potential impact would be less than that anticipated by the TPL studies and would be confined to the Lansing Smith area. Based on these studies, SCS-Trans believes that it could have managed any adverse impacts resulting from the failure to return the Protection Systems to service using system reconfiguration, generation redispatch, and/or transaction curtailments, as necessary, to maintain the reliability of the BPS in the event that either line experienced an issue during this period. | 12/16/2012 (when the next-day study was conducted with inaccurate system conditions on the Scherer – O’Hara 500 kV line) 4/16/2012 (when the next-day study was conducted with inaccurate system conditions on the Lansing Smith – Callaway 230 kV line) | 1/8/2013 (when the Scherer – O’Hara 500 kV line protection was back in service and studies were conducted with accurate system conditions) 6/2/2013 (when the Lansing Smith – Callaway 230 kV line protection was back in service and studies were conducted with accurate system conditions) | $9,000 | Self-Report | To mitigate this violation, SCS-Trans: 1) re-emphasized the importance of accurate information on Protection System outages that may affect the reliability performance of the transmission system. The system operations manager in the power coordination center issued a correspondence to the managers in each of the local control centers re-emphasizing the importance of accurate information on Protection System outages that may affect the reliability performance of the transmission system; and 2) reviewed a sample of protective relays on in-service transmission lines across the system to ensure that protection is in-service and the issue that precipitated this Self-Report is not more pervasive. | 10/25/2013 | 2014-07-27 | Admits | SERC reviewed SCS-Trans' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SCS-Trans follows Southern Company’s compliance framework manual, which has been in place since January 8, 2001. Details of the ICP are available internally through the intra-company web site. Compliance related information is regularly communicated through various means including, e-mail, newsletters, web-based, and classroom training sessions. SCS-Trans has a compliance officer, who reports directly to the senior vice-president and general counsel and has direct access to Southern Company's chief operating officer. Southern Company’s ICP is fully supported by company officers and senior management. Southern Company's ICP is regularly reviewed by senior management and is subject to internal audit. The individual performance of employees is evaluated on a regular basis. These evaluations include an assessment of how the employee complied with laws, regulations and company policies. Additionally, SCS-Trans completed or will complete the following actions, which SERC considered to be a mitigating factor in the penalty determination. SCS-Trans revised its standard design specification for new Protection System installations to include logic in the control settings to prevent energizing a transmission line without protection in service. SCS-Trans has also committed to increase staffing at its Georgia Transmission control center to add several new system operator positions. SCS-Trans has completed design modifications to substation relay alarm schemes in Gulf Power to improve situational awareness and will implement those modifications during future planned substation construction projects. Finally, a special team of representatives from all SCS-Trans affiliate companies met and applied the principles of the NERC cause code assignment process to identify potential causes that led to this violation. This team determined that human performance was a prominent factor in the violation and Southern Company management decided it was appropriate and necessary to re-emphasize existing procedures and alarm management practices. This effort was conducted via a top-down approach from management to system operators and field maintenance personnel. To avoid problems similar to the Lansing-Smith situation from reoccurring on existing Protection System installations, SCS-Trans has completed design modifications to the relay alarm schemes at another substation to ensure that alarms uniquely identify the equipment asserting an alarm instead of relying on aggregated alarms that apply to multiple pieces of equipment or relay terminals. SCS-Trans has also scheduled design work to perform similar relay alarm modifications for existing Protection System installations at two additional substations. As existing protection schemes undergo major overhaul during future capital construction projects, SCS-Trans will consider bringing them up to the new standard developed for new Protection System installations as discussed above. SCS-Trans has also revised its policies and procedures as needed to improve work practices and clarify expectations and communicated the resulting changes in the policies and procedures to the appropriate personnel. SCS-Trans shared lessons learned from these violations with appropriate personnel in protection and control and system operations to re-emphasize the importance of following procedures.
SERC Reliability Corporation (SERC) | Tenaska Virginia Partners, L.P. (TVP) | NCR01339 | SERC2014013844 | Settlement Agreement | On May 13, 2014, TVP submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-005-1 R1. SERC subsequently determined that the violation was more appropriately addressed as a violation of PRC-005-1 R2. TVP failed to implement its Protection System maintenance and testing program for all its Protection System devices. As part of its internal compliance program (ICP), TVP disseminated an enhanced relay training presentation to use as a template for its generating units. After reviewing this presentation, TVP determined that the steam turbine exciter power potential transformer over current protection relays, the associated current transformers (CTs), and DC control circuitry for all three phases were not being tested or maintained within the intervals defined in its Protection System maintenance and testing program. TVP incorrectly believed that the relays only tripped the supply breaker to the excitation system. However, TVP determined that the relays also directly trip the lockout relay associated with the generator breaker. Therefore, the devices should have been tested and maintained within the intervals defined within the Protection System maintenance and testing program. In addition to reviewing the Protection System program documents, SERC reviewed an inventory spreadsheet compiled by TVP which included a complete listing of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. Based on this review, SERC determined that TVP failed to have documentation of the date that its Protection System devices were tested or maintained for three of 41 protective relays (7.3%), three of 131 voltage and current sensing devices (2.3%), and three of 41 DC control circuitry (7.3%). In total, nine of 225 Protection System devices (4%) lacked documentation of the date that they were last tested or maintained. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to maintain or test these Protection System devices could result in a loss of generation due to incorrect operation of these Protection System devices and/or reliance on the Protection System devices of the associated Transmission Owner. However, overlapping zones of protection provided by other relays at this facility minimize the potential risk. Also, these devices are at a steam turbine generator rated at 390 MW with a combined cycle facility rated at 885 MW. TVP has a long-term contract with another entity that is on a capacity contract with PJM. Dispatch of the TVP units generally occurs when market prices are high. | 6/18/2007 (when the Standard became mandatory and enforceable) | 11/28/2014 (Expected Mitigation Plan completion date) | 0 | Self-Report | To mitigate this violation, TVP: 1) reviewed this issue during the internal Tenaska fleet-wide monthly NERC call and commenced an investigation for cause and potential risk to the BPS; 2) reviewed this issue during the plant monthly training; 3) added the steam turbine exciter power potential transformer relay, current transformers, and control circuitry to the PRC-005 equipment list; 4) conducted multiple independent reviews of site drawings to determine whether other Protection System elements were missed.; and 5) reviewed the event during the annual Protective Relay training. To mitigate this violation, TVP will: 1) perform testing on these missed Protection System elements in accordance with PRC-005-2 during the fall of 2014 planned outage. | 11/28/2014 (approved completion date) | TBD | Admits | SERC reviewed TVP’s ICP and considered it to be a mitigating factor in the penalty determination. TVP follows Tenaska Operations, Inc.’s (TOI) reliability standards internal compliance program. TVP has followed this ICP since April 8, 2008 with the most recent update coming on December 12, 2013. TVP’s ICP is distributed to all TOI and appropriate TVP employees that have direct or indirect responsibility for TOI compliance with the Reliability Standards. The ICP is overseen by the senior vice president of operations and asset management who reports directly to the chief executive officer (CEO) and meets regularly with the CEO and the board of stakeholders. Employees are subject to disciplinary action for violation of Reliability Standards. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005 R2 for Tenaska Gateway Partners, Ltd., a TVP affiliate, was filed with FERC under RC13-2-000 on November 30, 2012 The 60-day review period passed on January 29, 2013. SERC determined that TVP's affiliate's compliance history should not serve as a basis for aggravating the penalty. For the instant violation, TVP incorrectly believed that the relays in question were not part of the Protection system maintenance program. For the previous violation, the affiliate failed to sufficiently perform and document maintenance and testing in a sufficient manner to demonstrate compliance with PRC-005 R2.