## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Minnesota Power (Allete, Inc.) (MP) | NCR00674 | MRO2012011502 | Notice of Confirmed Violation | During a Compliance Audit conducted from September 24, 2012 through September 28, 2012, MRO determined that MP, as a Transmission Owner and a Generator Owner, was in violation of FAC-009-1 R1. MP failed to establish Facility Ratings for its solely and jointly owned Facilities, that were consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. The MRO Audit team found that in a sample of 33 elements used to calculate Facility Ratings, three elements were incorrect. Two of these errors were due to inadequate communication between MP and the customer regarding changes to equipment at their facility. The third error is assumed to be a data entry error. As part of mitigation, MP conducted a review of 86 of its Bulk Electric System (BES) facilities, including all three of its 500 kV facilities, all 37 of its 230 kV facilities, and 46 of its 115 kV and 138kV facilities. No discrepancies were found on the three 500 kV facilities. Twenty-four of the 37 230 kV facilities had issues with individual elements, resulting in five incorrect Facility Ratings. Three of the five incorrect Facility Ratings of 230kV facilities were off by less than 3%. The remaining two incorrect Facility Ratings included two parallel 230 kV lines. One of which had an incorrect bus current transformer (CT) rating, causing the winter rating to drop from 697 MVA to 478 MVA (31%), and the summer rating to drop from 594 MVA to 478 MVA (20%). The other line had an incorrect bus switch rating at one end, causing the winter rating to drop from 637 MVA to 478 MVA (25%) and the summer rating to drop from 595 MVA to 478 MVA (20%). MRO determined that MP operated above the limit on each line at least once for periods of time ranging from three minutes, following a trip on the parallel line, to four days, when the parallel line was taken out of service for maintenance. Additionally, 29 of the 46 115 kV and 138 kV facilities reviewed had issues with individual elements leading to 20 incorrect Facility Ratings. Eleven of these 20 Facility Ratings were off by less than 1% (rounding error) and seven errors resulted in increases in the Facility Ratings associated with sub-200 kV facilities. | FAC-009-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Planning and operating simulation-based studies depend on accurate ratings. The results of these studies are used to plan construction of reinforcements and to establish operating criteria such that the BPS can withstand a variety of pre-determined contingencies. Twenty-nine percent of MP's Facility Ratings were determined to be incorrect. The use of inaccurate ratings compromises the validity of planning and operating studies and could present a serious or substantial risk to the BPS. In this instance, the risk to the BPS was not serious or substantial because the problems were primarily associated with MP's lower-voltage facilities (115 kV and 138 kV), of which most were trivial discrepancies (less than 1%) or increases in ratings. No issues were discovered with MP's 500 kV facilities. While there were two errors associated with the 230 kV facilities that presented risk to the BPS, both of the subject lines are limited by common bus section equipment (rather than the transmission lines themselves), which have been designed using a breaker-and-a-half scheme. MP's approach is to rate transmission line facilities utilizing the most conservative element rating associated with the Facility and its terminal, regardless of the alternate power flow paths through the bus associated with an intact breaker-and-a-half scheme. It was discovered in both instances where the 230 kV Facility Ratings were exceeded, the breaker-and-a half scheme was intact. Therefore, the most limiting elements (bus CT, bus switch) for these facilities were not actually overloaded as they were not the sole source of flow from these parallel lines into the buses. Therefore, MRO determined that this violation posed a moderate risk to reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | 0 | Compliance Audit | To mitigate this violation, MP: 1) updated transmission line database deficiencies; 2) verified the calculation of all transmission line conductor ratings; 3) developed a new internal control for Facility Ratings associated with both newly installed and modified equipment; 4) developed a new internal control for periodic reviews of Facility Ratings information; 5) trained effected personnel on the new internal controls; 6) added a full-time Transmission Planning Engineer position to be primarily focused on transmission asset management activities; 7) performed a comprehensive review of all customer-owned equipment (138 kV) related to Facility Ratings (some equipment, which requires an outage to inspect, will be completed by 9/20/2016); 8) performed a comprehensive review of all MP 230 kV and 500 kV equipment related to Facility Ratings (some 230 kV equipment requires an outage to inspect, will be completed by 9/20/2016); and 9) will perform a comprehensive review of all 115 kV equipment. | 9/30/2016 (approved completion date) | TBD | Admits | MRO reviewed MP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MP has an established NERC Compliance Steering Committee (Committee), a cross-functional group whose primary role is to provide guidance and oversight in the areas of BPS reliability compliance and to serve as a resource for its subject matter experts (SMEs). This Committee generally meets weekly and is sponsored by the chief operating officer (who is also a member), the ALLETE controller and vice president-business support, and the vice president-transmission and distribution. The Committee along with senior management provides strategic direction and approvals for all NERC compliance related activities. In its proposed penalty assessment, MRO considered MP's investment in additional resources following the Compliance Audit. MP is in the process of adding a transmission compliance specialist to its staff. This position will assist with the implementation of MP's comprehensive, cross-functional transmission regulatory compliance programs. It is anticipated that this individual will join MP's staff in November 2014. MP has also added a position to assist System Operations with full time support and oversight of applicable NERC Reliability Standards (32 total). The estimated total annual cost of these two positions is $230,000. Additionally, MP reorganized its Tech Systems department to establish a Compliance and System Protection Group that is responsible for all NERC compliance activities within Tech Systems, including the supervision of technical resources for those activities. While this restructuring maintains current overall staffing levels and costs, MRO considered this departmental restructuring as indicative of MP's commitment to continuously improve its compliance with NERC Reliability Standards. MP considered these investments as mitigating factors in assessing a penalty. MRO considered MP's compliance history and determined there were no relevant instances of noncompliance.
Northeast Power Coordinating Council (NPCC) | Materials Innovation and Recycling Authority (MIRA) | NCR07045 | NPCC2013013112 | Settlement Agreement | On October 17, 2013, the Connecticut Resources Recovery Authority (CRRA) submitted a Self-Report stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. In June of 2012, CRRA had a change in its maintenance contractor due to performance issues. After the contractor had been replaced, CRRA performed a review of its maintenance records and discovered that documentation for many areas of the plant was destroyed or removed. CRRA determined it did not have testing documentation for 4 of 110 relays, 110 of 110 DC Circuits, 186 of 186 current transformers (CTs)/potential transformers (PTs), 6 of 6 battery banks, and 6 of 6 battery chargers. This accounts for 75% of all applicable devices within its maintenance and testing program. On June 6, 2014, MIRA was established as the successor authority to CRRA. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC determined that the violation posed a moderate risk because of the potential that these devices might not have operated as intended. In 2008, NPCC performed a spot check of MIRA's relays and found them to be compliant. MIRA owns two facilities with a total output of 286 MW, which would be covered under the ISO New England's reserves. No misoperations were known to have occurred. | 6/21/2007 (when MIRA registered as a GO) | 4/11/2014 (Mitigation Plan completion) | 10000 | Self-Report | To mitigate this violation, MIRA: 1) replaced its maintenance contractor; 2) performed maintenance and testing on missed Protection System devices; and 3) created a spreadsheet to track the maintenance and testing documentation and included the intervals associated with each device. | 2014-04-11 | 2014-09-12 | Does Not Contest | NPCC reviewed MIRA's internal compliance program and considered it to be a mitigating factor in the penalty determination. MIRA maintains an internal structure for compliance which utilizes internal staff working with a NERC compliance consultant. MIRA's day-to-day operations are handled by MIRA's senior engineer (supported by the operations manager) and reports directly to MIRA's Director of Operations and Environmental Affairs who has assigned responsibility for compliance activities. NPCC considered MIRA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013012230 | Settlement Agreement | During a Compliance Audit conducted from April 1, 2013 through April 12, 2013, WECC determined that AVA, as a Balancing Authority and Transmission Operator, was in violation of EOP-005-1 R6. WECC Enforcement (Enforcement) determined that AVA failed to annually train its operating personnel in the implementation of its restoration plan. Enforcement found that in calendar year 2012, AVA failed to train 3 out of 13 operating personnel, in the implementation of its restoration plan. Individuals involved in the violation reviewed AVA’s Standard Operating Procedures, but this review did not include training in the implementation of AVA’s restoration plan, and did not fulfill the requirement of EOP-005-1 R6. The root cause of the violation was a lack of compliance understanding. AVA believed a review of its Standard Operating Procedures would serve as training on the implementation of its restoration plan, but the WECC determined it was not sufficient training. | EOP-005-1 | R6 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AVA failed to train 23% of its system operators (3 out of 13 system operators) for calendar year 2012 on its System Restoration Plan. AVA’s failure to train its operators in the implementation of its restoration plan increased the likelihood that operators would be unprepared to handle potentially damaging outages or Misoperations. Although AVA failed to train a total of three operators in 2012 on its system restoration plan, AVA limited the potential risks by having a fully staffed and experienced workforce. Specifically, each of the operators involved in this violation had received training in prior years and had several years of experience as system operators. Furthermore, the majority of AVA’s operators (10 out of 13), received annual training on AVA’s restoration plan. | 1/1/2012 (when AVA missed training for calendar year 2012) | 8/28/2013 (Mitigation Plan completion) | $27,000 (for WECC2013012230, WECC2013012231, WECC2013012245, WECC2013012247, and WECC2013011979) | Compliance Audit | To mitigate this violation, AVA completed system restoration simulation training on its restoration plan for calendar year 2013. | 2013-08-28 | 2014-06-16 | Neither Admits nor Denies | WECC reviewed AVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AVA has a comprehensive, established, and documented program; that AVA has identified and assigned responsibility and accountability to a compliance officer or other high-ranking official who has independent access to the chief executive officer or equivalent; and AVA's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. AVA voluntarily agrees to conduct a comprehensive assessment of its ICP activities to further enhance its processes and procedures supporting compliance with NERC Reliability Standards applicable to AVA. AVA agrees to: submit a plan to WECC detailing certain actions AVA will take to assess its ICP processes and procedures; hire a third party to assist AVA with the assessment of its ICP processes and conduct compliance assessments of all NERC Reliability Standards applicable to AVA by December 31, 2015; submit status reports to WECC detailing how AVA implemented the plan and assessments on or before December 31, 2014 and December 31, 2015; and following an on-site audit by WECC in 2016, AVA will re-evaluate and discuss whether any further assessment of its ICP or independent compliance assessment of applicable NERC Reliability Standards is warranted. WECC considered AVA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013012231 | Settlement Agreement | During a Compliance Audit conducted from April 1, 2013 through April 12, 2013, WECC determined that AVA, as a Balancing Authority (BA) and Transmission Operator (TOP), was in violation of EOP-008-1 R1, specifically R1.6. WECC Enforcement (Enforcement) determined that AVA failed to train two operators on its contingency plans in calendar year 2011. EOP-008-0 R1 requires AVA, as a TOP and BA, to create contingency plans to maintain reliability operations and to provide training records demonstrating that AVA trained its operators on its contingency plan on an annual basis. AVA could not produce training records for two operators (15.39% of the operators); accordingly, Enforcement determined that AVA failed to train two operators in calendar year 2011 on its contingency plans. The root cause of the violation was a lack of process regarding training. | EOP-008-0 | R1; R1.6 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Enforcement found that AVA failed to train two operators on its contingency plans for calendar year 2011. AVA’s failure increased the likelihood that its operators may not handle potentially damaging misoperations in a proper manner. The potential risks associated with this violation were limited due to additional measures implemented by AVA. Specifically, AVA’s other 11 operators received contingency plan training and were familiar with the purposes of the contingency plan. Additionally, the operators involved in the incident were undergoing NERC Certification training and were being monitored by AVA senior operators for a portion of calendar year 2011. | 1/1/2011 (when AVA missed training for calendar year 2011) | 10/19/2012 (Mitigation Plan completion) | $27,000 (for WECC2013012230, WECC2013012231, WECC2013012245, WECC2013012247, and WECC2013011979) | Compliance Audit | To mitigate this violation, AVA: 1) trained the two operators in question; 2) required the two system operators to perform a required annual review of the procedure for activation of the back-up control center (BUCC); 3) ensured the two system operators participated in the 2012 annual BUCC activation exercise; and 4) began conducting its back-up control center activation exercises twice per year to allow for more flexibility in scheduling the participation of all its system operators. | 2012-10-19 | 2014-06-16 | Neither Admits nor Denies | WECC reviewed AVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AVA has a comprehensive, established, and documented program; that AVA has identified and assigned responsibility and accountability to a compliance officer or other high-ranking official who has independent access to the chief executive officer or equivalent; and AVA's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. AVA voluntarily agrees to conduct a comprehensive assessment of its ICP activities to further enhance its processes and procedures supporting compliance with NERC Reliability Standards applicable to AVA. AVA agrees to: submit a plan to WECC detailing certain actions AVA will take to assess its ICP processes and procedures; hire a third party to assist AVA with the assessment of its ICP processes and conduct compliance assessments of all NERC Reliability Standards applicable to AVA by December 31, 2015; submit status reports to WECC detailing how AVA implemented the plan and assessments on or before December 31, 2014 and December 31, 2015; and following an on-site audit by WECC in 2016, AVA will re-evaluate and discuss whether any further assessment of its ICP or independent compliance assessment of applicable NERC Reliability Standards is warranted. WECC considered AVA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013012245 | Settlement Agreement | During a Compliance Audit conducted from April 1, 2013 through April 12, 2013, WECC determined that AVA, as a Planning Authority, was in violation of FAC-010-2.1 R1, specifically R1.3. WECC Enforcement (Enforcement) determined that AVA was required to create a System Operating Limit (SOL) methodology that described how it identified the subset of SOLs that qualify as Interconnection Reliability Operating Limits (IROLs). Enforcement found that AVA’s SOL methodology did not differentiate between SOLs and IROLs and, therefore, the SOL methodology failed to describe how AVA identified the subset of SOLs that qualify as IROLs. Enforcement determined that this violation began on June 4, 2012, the date the WECC Reliability Coordinator (RC) created an SOL Methodology including a process for identifying IROLs. The root cause of the violation was a lack of compliance process. | FAC-010-2.1 | R1; R1.3 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Enforcement found that AVA failed to have a SOL methodology that described how it identified the subset of SOLs that qualify as IROLs. AVA’s failure impacted its ability to properly plan for potential operations in the area. Furthermore, AVA’s failure increased the likelihood that AVA’s SOLs may be improperly calculated thereby increasing the opportunity for misoperations to occur. The risks posed by AVA’s noncompliance were limited due to AVA’s compensating measures. Specifically, AVA participates in regional study groups that conduct reviews of neighboring systems in order to identify potential risks to SOLs. Additionally, AVA has consistently applied its methodology without a clearly defined subset of SOLs and IROLs such that neighboring, potentially affected utilities were not impaired by AVA’s SOL methodology. | 6/4/2012 (when the RC created a SOL methodology requiring AVA to identify IROLs) | 1/1/2014 (Mitigation Plan completion) | $27,000 (for WECC2013012230, WECC2013012231, WECC2013012245, WECC2013012247, and WECC2013011979) | Compliance Audit | To mitigate this violation, AVA revised its SOL methodology to identify the subset of SOLs that qualify as IROLs. | 2014-01-01 | 2014-06-13 | Neither Admits nor Denies | WECC reviewed AVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AVA has a comprehensive, established, and documented program; that AVA has identified and assigned responsibility and accountability to a compliance officer or other high-ranking official who has independent access to the chief executive officer or equivalent; and AVA's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. AVA voluntarily agrees to conduct a comprehensive assessment of its ICP activities to further enhance its processes and procedures supporting compliance with NERC Reliability Standards applicable to AVA. AVA agrees to: submit a plan to WECC detailing certain actions AVA will take to assess its ICP processes and procedures; hire a third party to assist AVA with the assessment of its ICP processes and conduct compliance assessments of all NERC Reliability Standards applicable to AVA by December 31, 2015; submit status reports to WECC detailing how AVA implemented the plan and assessments on or before December 31, 2014 and December 31, 2015; and following an on-site audit by WECC in 2016, AVA will re-evaluate and discuss whether any further assessment of its ICP or independent compliance assessment of applicable NERC Reliability Standards is warranted. WECC considered AVA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013012247 | Settlement Agreement | During a Compliance Audit conducted from April 1, 2013 through April 12, 2013, WECC determined that AVA, as a Transmission Owner (TO), was in violation of PRC-004-WECC-1 R1. WECC Enforcement (Enforcement) determined that AVA, as a TO, operates major transmission path facilities and therefore, was required be compliant with this Standard. Enforcement determined that AVA experienced 33 operations of its Protection Systems or Remedial Action Schemes (RASs) between October 1, 2011, and April 12, 2013 that required review and analysis by AVA. Enforcement determined that for 20 of the 33 (60.6%) Protection System operations, AVA failed to demonstrate that its System Protection personnel conducted an analysis, within 20 business days, of the operations for correctness to characterize whether a Misoperation had occurred that may not have been identified by system operators. The root cause of the violation was a lack of compliance understanding. | PRC-004-WECC-1 | R1; R1.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AVA’s System Protection personnel failed to analyze 20 out of 33 Protection System operations within 20 days as required by the Standard, and resulted in possible Misoperations being misidentified and not properly corrected. The potential risks associated with this violation were limited due to additional steps taken by AVA during the pendency of the violation. For a majority of the Protection System operations, the review was conducted but not documented. Specifically, 33 of the operations were reviewed within 24 hours by AVA System Operators. Furthermore, 13 of the operations were analyzed properly by AVA’s System Protection personnel. Finally, AVA’s procedure document requires that all Protection System operations be analyzed as required by the Standard. | 10/25/2011 (when AVA failed to analyze the first operation of its Protection Systems) | 2/1/2013 (Mitigation Plan completion) | $27,000 (for WECC2013012230, WECC2013012231, WECC2013012245, WECC2013012247, and WECC2013011979) | Compliance Audit | To mitigate this violation, AVA implemented a new database system to track its Protection System operations analysis. | 2013-02-01 | 2014-06-13 | Neither Admits nor Denies | WECC reviewed AVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AVA has a comprehensive, established, and documented program; that AVA has identified and assigned responsibility and accountability to a compliance officer or other high-ranking official who has independent access to the chief executive officer or equivalent; and AVA's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. AVA voluntarily agrees to conduct a comprehensive assessment of its ICP activities to further enhance its processes and procedures supporting compliance with NERC Reliability Standards applicable to AVA. AVA agrees to: submit a plan to WECC detailing certain actions AVA will take to assess its ICP processes and procedures; hire a third party to assist AVA with the assessment of its ICP processes and conduct compliance assessments of all NERC Reliability Standards applicable to AVA by December 31, 2015; submit status reports to WECC detailing how AVA implemented the plan and assessments on or before December 31, 2014 and December 31, 2015; and following an on-site audit by WECC in 2016, AVA will re-evaluate and discuss whether any further assessment of its ICP or independent compliance assessment of applicable NERC Reliability Standards is warranted. WECC considered AVA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013011979 | Settlement Agreement | On December 31, 2012, WECC notified AVA that it would be conducting an on-site Compliance Audit at AVA from April 1, 2013 through April 12, 2013. On February 26, 2013, AVA submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it was in violation of PRC-005-1b R2. AVA reported that it had failed to test five of its associated communication system devices in calendar year 2012. WECC Enforcement (Enforcement) determined that AVA had a transmission Protection System maintenance and testing program which required annual testing of associated communication system devices. Enforcement determined that AVA failed to conduct annual maintenance and testing on 5 out of 87 (5.75%) associated communication system devices in calendar year 2012. The root cause of the violation was human error and a lack of compliance process, causing AVA to miss testing all its associated communication system devices. | PRC-005-1b | R2; R2.1 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AVA failed to conduct required maintenance and testing on five associated communication system devices, creating a situation where its associated communication system devices could not be certified to operate correctly. The risks posed by AVA’s actions were limited due to AVA’s compensating measures. AVA’s communication system devices are continuously monitored 24 hours a day 7 days a week. Additionally, the devices are alarmed in the event that any abnormal occurrences exist. Furthermore, this instance involved only 5 out of 87 communication system devices. All other associated communication system devices received the proper testing and were certified as operational. | 1/1/2012 (when AVA failed to conduct maintenance and testing in calendar year 2012) | 1/3/2013 (Mitigation Plan completion) | $27,000 (for WECC2013012230, WECC2013012231, WECC2013012245, WECC2013012247, and WECC2013011979) | Self-Report | To mitigate this violation, AVA: 1) performed the maintenance inspections and testing of the Protection Systems associated communication device; 2) utilizes an automated tracking system to schedule inspection and testing activities for its telecommunications systems, where the system provides a visual alert when due dates are exceeded; and 3) modified the due dates for all maintenance activities in a given year to be November 1 instead of December 31 to ensure maintenance activities are completed with the defined intervals. | 2013-01-03 | 2013-09-18 | Neither Admits nor Denies | WECC reviewed AVA's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that AVA has a comprehensive, established, and documented program; that AVA has identified and assigned responsibility and accountability to a compliance officer or other high-ranking official who has independent access to the chief executive officer or equivalent; and AVA's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. AVA voluntarily agrees to conduct a comprehensive assessment of its ICP activities to further enhance its processes and procedures supporting compliance with NERC Reliability Standards applicable to AVA. AVA agrees to: submit a plan to WECC detailing certain actions AVA will take to assess its ICP processes and procedures; hire a third party to assist AVA with the assessment of its ICP processes and conduct compliance assessments of all NERC Reliability Standards applicable to AVA by December 31, 2015; submit status reports to WECC detailing how AVA implemented the plan and assessments on or before December 31, 2014 and December 31, 2015; and following an on-site audit by WECC in 2016, re-evaluate and discuss whether any further assessment of its ICP or independent compliance assessment of applicable NERC Reliability Standards is warranted. AVA did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. A Settlement Agreement covering violations of PRC-005-1 R2 for AVA was filed with FERC under NP10-26-000 on December 30, 2009. On January 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for AVA was filed with FERC under NP11-108-000 on February 23, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC considered AVA's PRC-005-1 R2 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | EthosEnergy Group (WGCS) | NCR10349 | WECC2014013886 | Notice of Confirmed Violation | On May 30, 2014, WGCS submitted a Self-Report stating that, as a Generator Operator, it was in violation of VAR-002-2b R3. In the Self-Report, WGCS reported that it failed to notify its associated Transmission Operator (TOP) within 30 minutes about a change in the status of its generator reactive power resources and the expected duration of the change in status or capability. Specifically, during the startup of the generator around 10:55 p.m., the breaker closed and the power system stabilizer (PSS) was not enabled. The operator enabled the PSS 10 minutes later, but did not notify the TOP concerning the time that the PSS was not enabled. The operator did not follow the WGCS procedure to check that the PSS was enabled during startup and did not check the email that he received from monitoring software reminding the operator that the PSS was not enabled. Beginning in July 2014, a WECC subject matter expert (SME) began a review of WGCS’s Self-Report, spoke with WGCS personnel, and issued data requests. As a result of the examination, the SME determined that WGCS had a possible violation of VAR-002-2b R3. Specifically, the SME determined that WGCS failed to notify its TOP within 30 minutes about change in status of its generator reactive power resources and the expected duration of the change in status or capability. The operator was going through the generator start-up procedure and noticed that the PSS was turned off. The operator immediately turned the PSS on, in accordance with the start-up procedure. The operator was aware of the requirement to notify the TOP about the PSS change, but incorrectly believed that the standard allowed for 24 hours before notification to the TOP was required, instead of the required 30 minutes. WGCS has a database that generates an email reminding the operator of the requirement to notify the TOP, but the operator did not check the email. WECC Enforcement reviewed the Self-Report and SME findings. Based on this review, WECC Enforcement determined that WGCS failed to notify its TOP within 30 minutes about change in status of its generator reactive power resources and the expected duration of the change in status or capability, resulting in a violation VAR-002-2b R3. The root cause of this issue was human error and a training issue. The operator involved in the issue was using the wrong procedure. | VAR-002-2b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WGCS’s generator that did not have the PSS enabled is rated at 100 MW on the same bus as a host of other generation stations totaling over 400 MW which all had their PSS in automatic mode. As a result, any voltage response would be handled by the online generation and would compensate for the unit with the PSS in manual mode. WGCS has a procedure to review control screens during shift change. The status change of the reactive power resources can be detected during the review and corrected if required. WGCS has good preventative controls. Specifically, WGCS generates an email notification via PI historian in the event of a PSS status change. The email notification provides the details of WGCS's procedure to be followed if the PSS status changes and the time within which TOP is required to be informed. WGCS also implemented strong corrective controls. WGCS has a generator start-up procedure that requires it to confirm the status of the PSS after the generator is online. If the PSS status is detected as “Manual” or “OFF”, the procedure requires WGCS personnel to change it to “Automatic”. WGCS also has a procedure in the event of PSS status change that requires WGCS's operator to call its TOP. Additionally, WGCS implemented strong compensating controls. Specifically, WGCS had automatic voltage regulator (AVR) and PSS running on the other generating unit and the AVR running on the affected unit. As a result of this, any voltage fluctuation or instability would have been minimized by the other reactive power resources. WGCS’s PSS was also off for only approximately 10 minutes after the generator was online. It took WGCS 37 hours and 50 minutes to inform the TOP about the PSS status change as WGCS's operator was following an incorrect procedure and assumed that WGCS had 24 hours to call the TOP. No harm is known to have occurred. | 5/25/2014 (when WGCS failed to notify the TOP that the PSS was not enabled) | 5/27/2014 (when WGCS notified the TOP about the PSS status change) | 7000 | Self-Report | To mitigate this violation, WGCS: 1) notified the TOP about the PSS status; 2) reprimanded the operator that made the error; and 3) retrained all of the operators on the correct start-up procedure and the VAR Standard Requirements. | 2014-06-13 | 2014-07-28 | Does Not Contest | A Find, Fix, Track and Report informational filing addressing remediated issues for certain registered entities including noncompliance with VAR-002-1.1b R3 for Wood Group Power Operations, an affiliate of WGCS, was filed with FERC under RC12-11-000 on April 30, 2012. The 60-day review period passed on June 29, 2012. WECC considered Wood Group Power Operation's VAR-002-1.1b R3 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Utah Associated Municipal Power Systems (UAMP) | NCR05445 | WECC2014013558 | Notice of Confirmed Violation | During a Compliance Audit conducted from February 25, 2014 through February 26, 2014, WECC determined that UAMP, as a Generator Owner, was in violation of PRC-005-1 R1. WECC determined UAMP's Protection System Maintenance and Testing Program does not include maintenance intervals or a summary of maintenance and testing procedures for fiber optic communications devices between the NEBO substation and the Dry Creek substation. UAMP cites continuous monitoring as the basis for no maintenance interval or defined maintenance testing plan. The root cause of this violation was UAMP's lack of compliance understanding. | PRC-005-1 | R1.1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. If UAMP's communication equipment failed to operate as designed, the line would not trip if a fault occurred. Had the fault occured, it could have caused damage to the line and potentially have caused the loss of up to 220 MVA of transmission capability. However, UAMP provided test intervals for the majority of elements associated with UAMP's Protection System Maintenance and Testing Program. UAMP provided test intervals for its protective relays, voltage and current sensing devices, station DC supply, and DC control circuitry. UAMP continuously monitors the Protection System and is alerted if a problem exists. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $12,000 (for WECC2014013558 and WECC2014013559) | Compliance Audit | To mitigate this violation, UAMP will: 1) modify and adopt UAMP's PRC-005-1 Protection System Maintenance and Testing Program for communication devices to include an additional stated communication system testing interval; 2) complete balance of 2014 scheduled testing (three CT banks); and 3) receive finalized testing documentation. | 12/18/2014 (proposed completion date) | TBD | Does Not Contest | WECC reviewed UAMP's maintenance and testing program and associated evidence from the July 2008 compliance audit and did not find a possible violation of PRC-005 R1. WECC determined that UAMP has had the same maintenance and testing program since the July 2008 compliance audit. Therefore, WECC assessed a $0 penalty for this violation. WECC considered UAMP's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Utah Associated Municipal Power Systems (UAMP) | NCR05445 | WECC2014013559 | Notice of Confirmed Violation | During a Compliance Audit conducted from February 25, 2014 through February 26, 2014, WECC determined that UAMP, as a Generator Owner, was in violation of PRC-005-1 R2. WECC determined UAMP's DC functional testing did not include the date of the last test. WECC also determined UAMP failed to provide evidence of testing for all of its Current Transformers. The root cause of this violation was UAMP's lack of compliance understanding. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. UAMP's failure to perform maintenance and testing could have resulted in the loss of up to 181 MW of generation. However, UAMP employs a contractor that utilizes a Supervisory Control and Data Acquisition system to monitor and control the facilities. UAMP also employs a 24-hour dispatcher who has visibility of the metered quantities at the plant. UAMP's Balancing Authority and Transmission Operator also have visibility at the plant. This violation is limited to UAMP's current transformers and DC Circuitry; UAMP maintained and tested its other Protection System devices. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | Present | $12,000 (for WECC2014013558 and WECC2014013559) | Compliance Audit | To mitigate this violation, UAMP will: 1) modify and adopt UAMP's PRC-005-1 Protection System Maintenance and Testing Program for communication devices to include an additional stated communication system testing interval; 2) complete balance of 2014 scheduled testing (three CT banks); and 3) receive finalized testing documentation. | 12/18/2014 (proposed completion date) | TBD | Does Not Contest | WECC considered UAMP's compliance history and determined there were no relevant instances of noncompliance.