## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Otter Tail Power Company (OTP) | NCR01023 | MRO2012011457 | Notice of Confirmed Violation | During a Spot Check conducted from June 22, 2012 to August 31, 2012, MRO determined that OTP, as a Transmission Owner and a Generator Owner, was in violation of FAC-009-1 R1. OTP failed to establish Facility Ratings for its solely and jointly owned Facilities, that were consistent with the associated Facility Ratings Methodology, as required by FAC-009-1 R1. The Spot Check revealed two equipment rating documentation errors on OTP's system. As part of mitigation, OTP is conducting a full review of its equipment ratings. Mitigation includes a full review and verification of all OTP equipment ratings. This review identified that the only Facility Rating error for a Facility operated above 115 kV was due to a breaker current transformer (CT) at a 230 kV substation. The CT’s rating was incorrectly documented at a lower value than what the nameplate showed, which resulted in an overly conservative (low) rating for the Facility. This Facility is a radial wind generation outlet. OTP has verified the ratings of 633 of the 1,038 (60.98%) pieces of equipment in its Facility Rating documentation. OTP discovered 95 (1.6%) equipment ratings that were either incorrect or missing from the Facility Ratings documentation. These errors resulted in ten incorrect Facility Ratings which consisted of four line switches, one current transformer (CT), one jumper cable, and four relay settings. The root cause of this violation was documentation errors on OTP's system. | FAC-009-1 | R1 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Planning and operating simulation-based studies depend on accurate ratings. The results of these studies are used to plan construction of reinforcements and to establish operating criteria such that the BPS can withstand a variety of pre-determined contingencies. The use of inaccurate ratings compromises the validity of planning and operating studies and could present a serious or substantial risk to the BPS. In this instance, the risk to the BPS was not serious or substantial because the problems were primarily associated with 115 kV voltage facilities. The only Facility Rating error for a Facility operated above 115 kV was due to a breaker CT at a 230 kV substation. The CT's rating was incorrectly documented at a lower value than the nameplate value, which resulted in an overly conservative rating for this radial wind generation outlet Facility. Additionally, a review of hourly loading data from August 1, 2011 through August 1, 2014, revealed that none of the affected Facilities was operated above the correct Facility Rating of its most limiting element. Only three of the Facilities operated over 60%. Finally, OTP has standard fault system protection equipment that would have mitigated the risk of a cascading outage. Therefore, MRO determined that this violation posed a moderate risk to reliability because OTP's operating history demonstrates a low likelihood of operating over the correct Ratings and none of the incorrect Facility Ratings resulted in forced outages. | 2007-06-18 | present | 0 | Spot Check | To mitigate this violation, OTP: 1) fixed all errors that were identified during the Spot Check; 2) developed a new spreadsheet-based relay load limit calculation process; and 3) reviewed all bulk electric system relay minimum trip calculations for accuracy. To mitigate this violation, OTP will: 1) complete its comprehensive review and verification of all OTP equipment ratings, including photographing equipment nameplates and directly measuring conductors in order to determine ratings. | 4/30/2015 (approved completion date) | TBD | Admits | MRO reviewed OTP's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. OTP has an established NERC Reliability Standards Compliance Policy and Compliance Manual which includes a designated reliability compliance officer with independent access to the OTP board of directors and audit committee. MRO considered that OTP has encouraged a culture of self-monitoring and assessment through the adoption of Key Performance Indicators at the business unit level that set a target of no NERC violations stemming from incidents that are not self-reported. MRO also considered that in 2012, OTP launched a periodic compliance meeting titled "Make it REAL," which stands for Reliability Education/Exchange and Lunch. These periodic meetings provide an opportunity for cross-department dialogue and exchange of ideas around compliance/reliability topics, such as, lessons learned from Notices of Penalty, best practices in compliance and/or mitigation, Reliability Standard interpretations, current reliability events, and continuous improvement in the compliance culture and effectiveness of the organization. In deciding not to assess a penalty, MRO considered OTP's purchase of the Aspen Relay Database as a mitigating factor. The database is designed to store information on overcurrent relays, distance relays, and differential relays, circuit breakers, transformers, CTs, potential transformers, communication equipment, etc. Implementation of this software provides OTP with the ability to query devices, settings, and other data points, which will greatly reduce the number of manual steps in its relay management process and provide additional support for its Facility Ratings database. The estimated cost of the software is $26,700. MRO considered OTP's compliance history and determined there were no relevant instances of noncompliance.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEP-Trans) | NCR01214 | SERC2012011323 | Settlement Agreement | On October 24, 2012, VEP-Trans submitted a Self-Report to SERC stating that, as a Transmission Owner (TO), it was in violation of PRC-005-1 R2. VEP-Trans reported that it did not have sufficient evidence demonstrating that some station battery and voltage and current sensing Protection System devices were tested and maintained within the defined interval. however, SERC determined that VEP-Trans had evidence to demonstrate compliance with PRC-005-1 R2 for these devices throughout the entire audit period. On December 12, 2012, VEP-Trans submitted a second Self-Report to SERC stating that it was in violation of PRC-005-1 R2. SERC determined that the December 12, 2012 Self-Report represented an expansion of scope to the October 24, 2012 Self-Report and consolidated the violations. On May 1, 2012, VEP-Trans discovered a VEP-Trans Protection System device in a substation owned by a third party. A completed work order existed for the device from inspections following Virginia’s August 2011 earthquake. However, the VEP-Trans work order management program did not indicate that routine preventative maintenance was required. Corrective maintenance work orders are done off-cycle, and not as part of VEP-Trans’ scheduled Protection System maintenance and testing program scheduled through the work order management program. VEP-Trans also identified certain delivery points where it relied upon wholesale or industrial customer owned devices as Protection System devices, even though those devices were not utilized as Protection System devices for those customers. SERC determined that VEP-Trans was responsible for ensuring that any Protection System devices that it relies on for operation of its facilities, or that might impact the operation of its system, are maintained and tested in accordance with the requirements of the VEP-Trans Protection System maintenance and testing program. The Protection System devices utilized by VEP-Trans but owned by wholesale and industrial customers were not previously included under any documented Protection System maintenance and testing program. In total, VEP-Trans discovered 25 third-party owned devices (12 voltage and current sensing devices and 13 station batteries) that had no maintenance or testing records. VEP-Trans also identified additional instances of non-compliance involving VEP-Trans owned facilities while completing the inventory assessment. VEP-Trans discovered it had 42 relays, 13 voltage and current sensing devices, and 42 DC control circuitry devices without previous testing or maintenance records. SERC reviewed a spreadsheet compiled by VEP-Trans providing a complete inventory of its Protection System devices, with defined intervals, and the last two maintenance and testing dates listed for each Protection System device at both solely owned facilities and jointly owned delivery points. Based on this review, SERC determined that VEP-Trans did not perform maintenance and testing on 42 of 2,088 (2%) protective relays, 25 of 3,372 (0.74%) voltage and current sensing devices, 13 of 309 (4.2%) station batteries and 42 of 2,088 (2%) DC Control Circuits as defined in its Protection System maintenance and testing program. In total, SERC determined that VEP-Trans could not provide evidence that 122 of 8,522 (1.4%) Protection System devices were compliant with PRC-005-1 R2. The root cause of the violation for the third party owned devices is that VEP-Trans did not know they were required to maintain and test the devices. For the other devices, VEP-Trans switched database programs so they did not have the prior test dates. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). VEP-Trans determined that the third-party owners tested or maintained the station batteries and voltage and current sensing devices under internal processes, and that documentation supporting those functions was available. VEP-Trans also conducts equipment health monitoring to verify equipment health, functionality, and communication line integrity. Examples of monitoring include signal check-back tests occurring every four hours for carrier blocking and/or continuous guard tone monitoring for transfer trip protection schemes. This health monitoring should have identified issues with the instrument transformers and station batteries, and alarms would have notified service personnel to investigate if there were problems. VEP-Trans monitors microprocessor protective relays which are designed to alarm in the event of a failure or degradation of a device. This alarm would notify a VEP-Trans operation center resulting in the immediate dispatch of service personnel. VEP-Trans conducted a thorough and extensive outage history review of all delivery points with non-compliant devices and found no outages due to the failure of Protection System components. Subsequent testing of the non-compliant Protection System devices found no problems. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/19/2014 (Mitigation Plan completion) | $0 (for SERC2012011323 and SERC2014013349) | Self-Report | To mitigate this violation, VEP-Trans: 1) deployed an asset bar-coding initiative for substation inspections; 2) deployed an asset management question process; 3) worked with the delivery point entity owners to obtain the appropriate maintenance and testing evidence where available to identify and verify the maintenance activity for those delivery points where that entity owns one or more PRC-005-1 Protection System elements; 4) added non-VEP-Trans owned PRC-005-1 Protection System elements that could impact the BPS to VEP-Trans’ SAP work management system for the purpose of coordinating, monitoring, and tracking future maintenance and testing of these Protection System elements with each entity owner; 5) worked with each delivery point entity owner to bring delivery points where sufficient maintenance and testing evidence of VEP-Trans identified Protection System elements could not be obtained into compliance for maintenance and testing requirements; 6) included separate appendices to its Protection System Maintenance Plan (PSMP) program document for each entity owner that outline the maintenance and testing intervals and their basis for non-VEP-Trans owned delivery point assets that can affect a VEP-Trans BPS relay scheme; 7) revised its FAC-001 facility connection requirements document to establish a formal, clearly defined policy regarding delivery point entity owner expectations pertaining to the maintenance and testing of Protection System elements; and 8) established several evidence stacking processes to capture sufficient documentation to support its maintenance program. | 5/19/2014 | TBD | Neither Admits nor Denies | SERC reviewed VEP-Trans's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is managed on a day-to-day basis by the NERC compliance policy group of VEP-Trans' parent company, Dominion Resources, Inc. The ICP is posted on the NERC compliance policy group's website and can be reviewed at any time. The ICP is overseen by the chief compliance officer of VEP-Trans' parent company, who reports to the senior vice president of law, public policy, and environment, state and federal affairs, who in turn reports to the chief executive officer. This structure allows for direct and independent access to the chief executive officer and the board of directors. Senior management is fully supportive of the ICP. The ICP is reviewed annually and provides for annual NERC awareness training of employees with NERC compliance responsibilities and targeted training as appropriate. Employees also receive annual compliance and ethics training to remind them of their responsibility to report any perceived violation of a NERC Reliability Standard. The ICP also provides for internal mock audits from time-to-time. The ICP allows for discipline of employees, pursuant to the discipline policy, for conduct that violates NERC Reliability Standards or a failure to report potential violations of NERC Reliability Standards. Additionally, VEP-Trans completed or will complete the following above-and-beyond actions, which SERC considered to be a mitigating factor in the penalty determination. VEP-Trans has established a delivery point compliance initiative project. Through this project, VEP-Trans will work with affected delivery points to establish plans for VEP-Trans’ outright ownership of Protection System components. Upon completion of these projects, VEP-Trans will have full responsibility for these newly constructed Protection System components, thus eliminating the need for current third-party maintenance oversight. To date, VEP-Trans has dedicated approximately 1,100 man-hours to bring its compliance up to date, maintain documentation inflow on a regular basis, and create both a short-term initiative along with a long-term solution. This translates to an estimated cost of over $175,000. VEP-Trans began its oversight of the 12 delivery points in October 2012, when it began collecting third-party documentation. VEP-Trans will continue these steps until it has constructed new Protection System components under its ownership. VEP-Trans estimates that completion of this project will cost approximately $5,000,000 based on the anticipated scope of work to date. VEP-Trans did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. On October 8, 2012, SERC sent VEP-Trans an audit detail letter notice of a compliance audit scheduled for February 4, 2013 through February 8, 2013. A Settlement Agreement covering violation of PRC-005 R2 for a VEP-Trans affiliate was filed with FERC under NP10-84-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that VEP-Trans's compliance history should not serve as a basis for aggravating the penalty. For the previous violation, the affiliate entity deviated from the appropriate procedure, failed to follow the proper maintenance intervals, and performed maintenance based on historical practices rather than the appropriate procedure. For the current instance, VEP-Trans believed that it was not required to test the third-party owned devices and for other devices, VEP-Trans switched database programs so it did not have prior test dates.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEP-Trans) | NCR01214 | SERC2014013349 | Settlement Agreement | On January 14, 2014, VEP-Trans submitted a Self-Report to SERC stating that, as a Distribution Provider and Transmission Owner, it was in violation of PRC-005-1 R1. VEP-Trans failed to include certain Protection System devices that affected the reliability of the Bulk Electric System (BES) in its Protection System maintenance and testing program. VEP-Trans previously submitted Self-Reports stating that it was in violation of PRC-005-1 R2 on October 24, 2012 and December 12, 2012, which prompted it to conduct an assessment of its Protection System maintenance and testing program. VEP-Trans determined that voltage and current sensing devices and station batteries owned by cooperatives, municipals, or industrial customers at 12 delivery points had been operating without a documented Protection System maintenance and testing program that addressed those devices. Although VEP-Trans does not own these devices, VEP-Trans relies on those devices as Protection System devices and these devices have the ability to impact Bulk Power System (BPS) transmission lines owned by VEP-Trans. In addition, the cooperatives, municipals or industrial customers do not utilize these devices as Protection System devices. These third party-owned Protection System devices will be tested and maintained under a separate VEP-Trans Protection System maintenance and testing program than the Protection System program for VEP-Trans-owned Protection System devices. Based on VEP-Trans’s assessment and inventory of the 12 delivery points, VEP-Trans determined that the identified Protection System devices were not included in a documented Protection System maintenance and testing program. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. VEP-Trans determined that the third-party owners tested or maintained the station batteries and voltage and current sensing devices under internal processes, and that documentation supporting those functions was available. VEP-Trans also conducts equipment health monitoring to verify equipment health, functionality, and communication line integrity. Examples of monitoring include signal check-back tests occurring every four hours for carrier blocking and continuous guard tone monitoring for transfer trip protection schemes. This monitoring includes either signal check back tests occurring every four hours for carrier blocking, and/or continuous guard tone monitoring for transfer trip protection schemes. This health monitoring should have identified issues with the instrument transformers and station batteries, and alarms would have notified service personnel to investigate if there were problems. VEP-Trans conducted a thorough and extensive outage history review of all delivery points with non-compliant devices and found no outages due to the failure of Protection System components. Subsequent testing of the non-compliant Protection System devices found no problems. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/19/2014 (Mitigation Plan completion) | $0 (for SERC2012011323 and SERC2014013349) | Self-Report | To mitigate this violation, VEP-Trans: 1) deployed an asset bar-coding initiative for substation inspections; 2) deployed an asset management question process; 3) worked with the delivery point entity owners to obtain the appropriate maintenance and testing evidence where available to identify and verify the maintenance activity for those delivery points where that entity owns one or more PRC-005-1 Protection System elements; 4) added non-VEP-Trans owned PRC-005-1 Protection System elements that could impact the BPS to VEP-Trans’ SAP work management system for the purpose of coordinating, monitoring and tracking future maintenance and testing of these Protection System elements with each entity owner; 5) worked with each delivery point entity owner(s) to bring delivery points where sufficient maintenance and testing evidence of VEP-Trans identified Protection System elements could not be obtained into compliance for maintenance and testing requirements; 6) included separate appendices to its Protection System Maintenance Plan (PSMP) program document for each entity owner that outline the maintenance and testing intervals and their basis for non-VEP-Trans owned delivery point assets that can affect a VEP-Trans BPS relay scheme; 7) revised its FAC-001 facility connection requirements document to establish a formal, clearly defined policy regarding delivery point entity owner expectations pertaining to the maintenance and testing of Protection System elements; and 8) established several evidence stacking processes to capture sufficient documentation to support its maintenance program. | 2014-05-19 | TBD | Neither Admits nor Denies | SERC reviewed VEP-Trans's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is managed on a day-to-day basis by the NERC compliance policy group of VEP-Trans' parent company, Dominion Resources, Inc. The ICP is posted on the NERC compliance policy group's website and can be reviewed at any time. The ICP is overseen by the chief compliance officer of VEP-Trans' parent company, who reports to the senior vice president of law, public policy, and environment, state and federal affairs, who in turn reports to the chief executive officer. This structure allows for direct and independent access to the chief executive officer and the board of directors. Senior management is fully supportive of the ICP. The ICP is reviewed annually and provides for annual NERC awareness training of employees with NERC compliance responsibilities and targeted training as appropriate. Employees also receive annual compliance and ethics training to remind them of their responsibility to report any perceived violation of a NERC Reliability Standard. The ICP also provides for internal mock audits from time-to-time. The ICP allows for discipline of employees, pursuant to the discipline policy, for conduct that violates NERC Reliability Standards or a failure to report potential violations of NERC Reliability Standards. Additionally, VEP-Trans completed or will complete the following above-and-beyond actions, which SERC considered to be a mitigating factor in the penalty determination. VEP-Trans has established a delivery point compliance initiative project. Through this project, VEP-Trans will work with affected delivery points to establish plans for VEP-Trans’ outright ownership of Protection System components. Upon completion of these projects, VEP-Trans will have full responsibility for these newly constructed Protection System components, thus eliminating the need for current third-party maintenance oversight. To date, VEP-Trans has dedicated approximately 1,100 man-hours to bring its compliance up to date, maintain documentation inflow on a regular basis, and create both a short-term initiative along with a long-term solution. This translates to an estimated cost of over $175,000. VEP-Trans began its oversight of the 12 delivery points in October 2012, when it began collecting third-party documentation. VEP-Trans will continue these steps until it has constructed new Protection System components under its ownership. VEP-Trans estimates that completion of this project will cost approximately $5,000,000 based on the anticipated scope of work to date. SERC considered VEP-Trans's compliance history and determined there were no relevant instances of non-compliance.
Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2014013452 | Settlement Agreement | On February 26, 2014, MEID submitted a Self-Report stating that, as a Transmission Owner, Generator Owner and Distribution Provider, it was in violation of PRC-005-1 R1. WECC determined that MEID was in violation of PRC-005-1 R1 for failing to have a Protection System Maintenance and Testing Program (PSMP) that includes all Protection System devices. Specifically, MEID’s PSMP: 1) does not contain a summary of the maintenance and testing procedures for electromechanical relays; 2) does not contain a summary of the maintenance and testing procedures for instrument transformers; 3) does not contain intervals or a summary of maintenance and testing procedures for battery chargers; and 4) uses a condition-based maintenance schedule for Nickel-cadmium batteries rather than a time-based interval as required under the Standard. The root cause of the violation was a lack of process. | PRC-005-1 | R1; R1.1; R1.2 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to regularly maintain and test Protection System devices could lead to Protection System Misoperations, potentially resulting in the loss of the Protection Systems associated with three 115 kV substations which could lead to a loss of 87 MW of load and 94.5 MW of generation. However, as preventative and detective controls, MEID’s Transmission Operators (TOPs) utilize automation systems which provide alarms and notifications for Protection System failures throughout MEID’s facilities. The TOPs provide notification to MEID as events occur. The TOPs also have control of facility equipment and may operate it to reduce impacts. MEID also implemented corrective controls in that this violation was found through the use of an outside consultant reviewing its program. MEID implemented maintenance on Protection System devices in accordance with manufacturer guidelines as a compensating measure. No harm is known to have occurred. | 6/17/2007 (when the Standard became mandatory and enforceable) | 11/4/2014 (Mitigation Plan completion) | $15,000 (for WECC2014013452 and WECC2014013453) | Self-Report | To mitigate this violation, MEID created a PSMP that includes ongoing maintenance; verification that components work correctly; monitoring routine operation; calibration of equipment; and the restoration of malfunctioning equipment to proper operation. | 11/4/2014 | 2014-12-04 | Admits | MEID did not receive mitigating credit for self-reporting because the Self-Report was submitted during the self-certification period. In 2010, WECC conducted a Compliance Audit of MEID and did not find any possible violations of PRC-005 R1. WECC recognizes that WECC’s previous audit findings perpetuated MEID’s error with respect to having a deficient PSMP, resulting in the current violation. MEID agreed to implement the following Reliability Focused Terms: (a) internal compliance program – (i) MEID will complete WECC’s internal compliance program assessment (ICPS); (ii) based on results or weaknesses identified by MEID in its ICPA, develop, augment, or improve and implement internal compliance program (ICP); and (iii) distribution the ICP to all applicable employees, contractors, and vendors; and (b) PRC-005-2 – (i) prepare for version 2 transition by updating the PSMP for version 2 compliance and MEID must remain version 1 compliant, which requires a basis for intervals, and train applicable employees, contractors and vendors on updated testing requirements; and (ii) provide a narrative to WECC on MEID’s implementation by February 20, 2015. WECC considered MEID's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2014013453 | Settlement Agreement | On February 26, 2014, MEID submitted a Self-Report stating that, as a Transmission Owner, Generator Owner and Distribution Provider, it was in violation of PRC-005-1 R2. WECC determined that MEID was in violation of PRC-005-1 R2 for failing to have evidence that it implemented its Protection System Maintenance and Testing Program (PSMP) within the intervals defined in its program. Specifically, MEID lacked evidence that maintenance and testing was performed as mandated by MEID’s program on 100% of MEID’s 39 DC control circuits. The root cause of the violation was a lack of compliance understanding. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to regularly maintain and test Protection System devices could lead to Protection System Misoperations, potentially resulting in the loss of the Protection Systems associated with three 115 kV substations which could lead to a loss of 87 MW of load and 94.5 MW of generation. However, as preventative and detective controls, MEID’s Transmission Operators (TOPs) utilize automation systems which provide alarms and notifications for Protection System failures throughout MEID’s facilities. The TOPs provide notification to MEID as events occur. The TOPs also have control of facility equipment and may operate it to reduce impacts. MEID also implemented corrective controls in that this violation was found through the use of an outside consultant reviewing its program. As compensating controls, MEID implemented maintenance on Protection System devices in accordance with manufacturer guidelines. No harm is known to have occurred. | 6/17/2007 (when the Standard became mandatory and enforceable) | present | $15,000 (for WECC2014013452 and WECC2014013453) | Self-Report | To mitigate this violation, MEID will: 1) produce evidence that Protection System devices are maintained and tested within their defined intervals; and 2) provide the date each Protection System device was last tested or maintained. | 9/17/2015 (approved completion date) | TBD | Admits | MEID did not receive mitigating credit for self-reporting because the Self-Report was submitted during the self-certification period. A Settlement Agreement covering violations of PRC-005-1 R2 for MEID was filed with FERC under NP11-10-000 on November 5, 2010. On December 3, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that MEID's compliance history should not serve as a basis for aggravating the penalty. In the previous violation, MEID failed to test, on two occasions, current transformers and differential transformers within the interval specified in its maintenance and testing program. MEID’s documentation of the maintenance was also incomplete. WECC considered the similar nature of the present violation to the prior violation but further considered MEID first violated the Standard in 2008.
Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC) | NCR05390 | WECC2014013776 | Settlement Agreement | During a Compliance Audit conducted from April 21, 2014 through May 2, 2014, WECC determined that SPPC, as a Transmission Operator, was in violation of TOP-007-0 R1. On February 27, 2013, another entity's transmission facility adjacent to Path 76 underwent a scheduled outage. Normally, Path 76 has a -300/+270 MW System Operating Limit (SOL). However, during the scheduled outage, SPPC imposed a limit for the flow on Path 76 to +/-30 MW. This limit, while artificially low, was represented at the time to be the new SOL for the outage condition. During the scheduled outage, at 4:59:00, SPPC's West Tracy Combustion Turbine #8 tripped. When this generator trip occurred, the tie flow increased above the new SOL, and SPPC was alerted to the exceedance by its alarms. The SPPC operator requested the Northwest Power Pool provide reserve assistance at 05:01. At 05:02:00, Path 76 reached its maximum flow of 45.1 MW. At 05:03, SPPC reduced flow on Path 76 to under the SOL by adjusting the Bordertown Phase Shifter. SPPC then immediately notified the Reliability Coordinator (RC) at 05:04:36. During the conversation between SPPC and the RC, SPPC indicated that it had requested reserves and reported a Disturbance Control Standard event that had already been resolved. SPPC did not reference an SOL exceedance and did not verbally inform the RC of the mitigating steps taken in response, in violation of TOP-007-0 R1. WECC determined that SPPC was in violation of TOP-007-0 R1 because it failed to inform the RC of an SOL exceedance on February 27, 2013 and the actions being taken to return the system to within limits as required by the Standard. The root cause of this violation is the operator's confusion around what the SOL of the line was and whether the issue was an SOL exceedance. | TOP-007-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPC experienced an SOL exceedance. While SPPC informed the RC of the precipitating event that resulted in the SOL exceedance - the trip of a generator - SPPC did not verbally inform the RC of the exceedance and the actions being taken to return the system to within limits. In general, failure to operate the system within the Interconnection Reliability Operating Limit (IROL) and SOL limits could lead to instability, uncontrolled separation, cascading outages and/or the loss of SPPC's 2,084 MW summer peak load. However, while SPPC experienced an exceedance, SPPC's operators were able to remediate the exceedance within approximately five minutes. During the Compliance Audit period, SPPC reported two other brief SOL exceedances, with one occurring before and one after the event at issue. In both those instances, the SPPC operators contacted the RC, verbally informed them of the SOL exceedance, and verbally informed the RC of the actions being taken to bring the system to within limits, evidencing proper training of system operators. Also, at the time of the violation, SPPC was operating under conservative SOLs and at no time was the exceedance at or near the actual path rating of the line in question. As compensating measures, three weeks prior to the exceedance, SPPC provided documentation to the RC stating the actions SPPC would take in the event of exceedances on Path 76. Also, the operational position of SPPC's Bordertown Phase Shifter is directly telemetered to the RC, therefore the RC would have been continuously aware of the status of the facility. For these reasons, and because no harm is known to have occurred, WECC determined this violation posed minimal risk to the reliability of the BPS. | 2/27/2013 (when SPPC failed to inform the RC of the SOL exceedance and the actions being taken to return the line within the SOL) | 2/27/2013 (when SPPC returned the line to within the SOL) | $0 | Compliance Audit | To mitigate this violation, SPPC: 1) conducted training sessions for System Operators emphasizing that verbal notification to the RC should accompany the various electronic information supplied to the RC that conveys the status of SOLs and the flow control actions being taken; 2) issued an operator instruction requiring proper logging of SOLs and noting completion of verbal notification to the RC; and 3) enhanced the operator log template to clarify the information that operators must track for SOL exceedances. | 7/29/2014 | 10/24/2014 | Neither Admits nor Denies | WECC reviewed SPPC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPC's ICP illustrates a comprehensive program designed to ensure that SPPC complies with NERC Reliability Standards. The program is detailed and well organized in a manner that is easily understood. The goals of SPPC are clearly stated and the document is a great representation of the efforts of SPPC to comply with NERC Reliability Standards. Specifically, WECC determined several areas of SPPC's ICP provide exemplary practices for all entities with similar characteristics. First, SPPC's ICP is reviewed following possible violations during the Mitigation Plan process to determine whether any changes to the ICP or other processes or procedures are necessary to prevent the likelihood of repeat violations. Second, SPPC has a comprehensive self-auditing procedure. Finally, SPPC has a complete system for identifying, maintaining, and updating applicable NERC Reliability Standards. WECC also considered the unique nature of this particular SOL exceedance as a mitigating factor. Specifically, WECC considered that the SOL set by SPPC on this occasion was artificially low. Upon exceeding the SOL, the SPPC System Operator promptly took action and was able to return the system to within the limits in under five minutes. In instances before and after the instance at issue in which an actual SOL was exceeded, SPPC contacted the RC with the correct information, evidencing that SPPC's System Operators are well-trained to handle situations in which actual SOLs are exceeded.