## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP201100549 | Settlement Agreement | On April 27, 2011, the SPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1 R1.1 and 1.2. Specifically, SPA’s Protection System maintenance and testing program (Program) did not document maintenance and testing intervals or their basis for DC control circuitry and associated communication systems per R1.1. SPA’s PRC-005-1 R1 violation included 11% (230 of 2,038) of SPA’s Protection System devices. Additionally, SPA’s Program did not include a summary of maintenance and testing procedures for its DC control circuitry per R1.2. The root cause of the violation was SPA employee oversight during the annual review of its policies and procedures. The violation was found during a SPA internal assessment and promptly self-reported. | PRC-005-1 | R1; R1.1; R1.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Not including a basis or intervals for its DC control circuitry and associated communication systems in SPA’s Program per R1.1 presented a risk that testing for those Protection System devices could have been missed. However, SPA tested its DC control circuitry on a 24-month interval and performed continuous monitoring of its associated communication systems. The 24-month interval falls within the NERC Protection System Maintenance Technical Reference, i.e., five years for unmonitored DC control circuits. The NERC Protection System Maintenance Technical Reference does not require periodic testing for telecom devices that are continuously monitored. SPA verified the functionality of DC circuits associated with protective relays during regularly scheduled circuit breaker maintenance. SPA’s associated communication systems are monitored through its supervisory control and data acquisition (SCADA) system, which will trigger an alarm at a continuously manned operations center if equipment failures occur. SPA confirmed that when the involved Protection System devices were tested, none of the devices were operating improperly. The lack of a summary of procedures (R1.2) for testing the DC control circuitry is documentation in nature. As discussed above, SPA was testing its DC control circuitry within the interval established in the NERC Protection System Maintenance Technical Reference. | 3/1/2008 (the beginning of non-compliance as indicated in SPA’s Self-Report) | 4/20/2011 (Mitigation Plan completion) | None | Self-Report | To mitigate the violation SPA: revised its Program documentation to include: 1) maintenance and testing intervals and their basis for DC control circuitry and associated communication systems,; and 2) a summary of maintenance and testing procedures for DC control circuitry. | 2011-04-20 | 2013-07-29 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective Reliability Standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff including subject matter experts attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP201100550 | Settlement Agreement | On April 27, 2011, SPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2.1. SPA did not have evidence that all its Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (Program). Specifically, SPA did not have evidence of testing consistent with its Program for 72 of 136 (52.94%) DC control circuits , 585 of 1,330 (43.98%) voltage and current sensing devices, 21 of 432 (4.86%) protective relays , and 2 of 94 (2.13%) associated communication systems. SPA’s violation of PRC-005-1 R2.1 involved 680 of 1,992 (34.14%) of its Protection System devices. The root cause of this violation was SPA employee oversight of testing the devices within the defined intervals and not properly documenting the test results. However, the violation was found through a SPA internal assessment and, as a result, promptly self-reported. | PRC-005-1 | R2; R2.1 | High | Moderate | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to test Protection System devices presents a risk that vulnerabilities within such devices could go undetected, which could lead to Protection System misoperations. Although SPA could not provide evidence to support testing of its Protection System devices within the intervals defined in its Program, SPA was testing its Protection System devices and had systems in place to monitor the performance of its Protection System devices. The maintenance and testing intervals defined in SPA’s Program are more conservative than the intervals defined in the NERC Protection System Maintenance Technical Reference. SPA’s voltage and current sensing devices, microprocessor relays, and associated communication systems are monitored through its supervisory control and data acquisition (SCADA) system, which will trigger an alarm at a continuously manned operations center if an internal test fails or device parameters exceed established limits. SPA confirmed that when the affected Protection System devices were tested, none of the devices were operating improperly. SPA conducts quarterly substation inspections. The substation inspections include confirming the DC control circuit through the trip coil, visually checking the current and sensing devices, visually checking for battery cell leakage, terminal corrosion, and battery rack integrity. SPA’s substations have alarms for low DC voltage, battery charger failure, and battery room temperature changes. The alarm is communicated to a continuously manned operations center. Also, thorough testing is conducted on both DC control circuits and instrument transformers during commissioning. | 7/17/2007 (when the first testing occurred outside of a testing interval) | 8/9/2012 (Mitigation Plan completion) | None | Self-Report | To mitigate this violation, SPA: 1) tested all devices that had missed intervals; 2) maintained all devices that had missed intervals; and, 3) instituted a CASCADE tracking system that aids in the identification of approaching maintenance/testing dates, and provides for automated notifications of those dates for all PRC-005 devices. | 2012-08-09 | 2013-10-07 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into Agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective Reliability Standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff and subject matter experts attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2012010989 | Settlement Agreement | During a Compliance Investigation conducted from November 2, 2010 to October 6, 2011, NERC determined that SPA, as a Balancing Authority (BA), was in violation of BAL-005-0.1b R6. On January 12, 2010, SPA experienced the loss of its primary control center supervisory control and data acquisition (SCADA) system. The event caused the SPA system operators to lose system visibility and control, and resulted in the curtailment of the system telemetry operating data transmitted to the Reliability Coordinator (RC). On January 12, 2010, SPA failed to calculate Area Control Error (ACE) for one hour and 27 minutes during the SCADA event and did not specifically notify the RC that ACE was not being calculated. The root cause of the violation was SPA’s system operators’ failure to execute SPA’s operational directive for manually calculating ACE when automatic calculation is not functioning (i.e. during the SCADA event) and to specifically inform the RC that ACE was not being calculated. | BAL-005-0.1b | R6 | Medium | Severe | SPP RE determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPA did not take steps to manually calculate its ACE during the SCADA event, the event duration was short and SPA took steps to mitigate deviations in ACE. During the event, SPA attempted to maintain “Zero” ACE by comparing Net Scheduled Interchange (NSI) to its generator outputs and adjusting generation as required. SPA adjusted one generator to meet its new NSI during the SCADA event. The BA scheduler on shift verified plant output after the SCADA event and determined that the ACE did not materially deviate from normal. Generator output was used, along with the schedule and tagging system, which was unaffected by the outage, in order to ensure the NSI was being maintained. Although, SPA did not specifically tell the RC it was not calculating ACE, SPA did tell the RC that the SPA SCADA system was down and the RC would have understood that SPA no longer had the ability to calculate ACE without manual intervention. No load shedding or other adverse events occurred as a result of SPA not calculating ACE. | 1/12/2010 (when SPA's ACE calculations were no longer valid) | 1/12/2010 (when the ACE was verified as fully operational) | None | Compliance Investigation | To mitigate this violation, SPA: 1) verified SCADA fully operational; 2) SPA operations management counselled system operators that during events such as the SCADA event, the operators are to specifically notify the RC if they are unable to calculate ACE for 30 minutes or longer; and, 3) SPA operations management counselled system operators that during events such as the SCADA event, the operators should follow SPA’s operating directives and manually calculate ACE. | 2012-05-01 | 2013-07-15 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into Agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective Reliability Standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff and Reliability Subject Matter Experts (RSMEs) attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2012010990 | Settlement Agreement | During a Compliance Investigation conducted from November 2, 2010 to October 6, 2011, NERC determined that SPA, as a Balancing Authority and Transmission Operator, was in violation of COM-001-1.1 R1.4. SPA did not provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information. More specifically, SPA failed to install redundant telecommunication facilities in the Primary Control Center (PCC) local area network supporting its Energy Management System (EMS). During a January 10, 2010 Supervisory Control and Data Acquisition (SCADA) event, a single Cisco switch failed, resulting in a total loss of PCC SCADA communications for one hour and 27 minutes. During the Compliance Investigation, it was discovered the design of SPA’s EMS local area network contained a single point of failure, the PCC network switch. Moreover, SPA did not have the ability to automatically fail over to the backup control center (BCC) in the event the network switch failed. All critical network communications in the PCC and between the primary and backup control centers were routed through this single network switch. The root cause of the violation was SPA’s failure to build a redundant telecommunications path in its PCC EMS local area network for critical PCC communications. | COM-001-1 | R1; R1.4 | High | Severe | SPP RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because SPA did not have a redundant and diversely routed telecommunications at its PCC, when the Cisco switch failed, SPA lost visibility of its control area, creating the risk that system operators would be unaware and thus fail to respond to events affecting system operation. Additionally, SPA’s system operators would not have the ability to exercise control of the SPA system from its PCC. Although SPA did have a spare network switch that could be activated within 15 minutes, it could take longer if a technician were not immediately available to activate the backup switch. During the SCADA event, SPA’s Continuity of Operations Plan and Recovery Plan (Recovery Plan) for Critical Cyber Assets (i.e. Cisco switch) was not activated because SPA system operators believed the PCC would be returned to service in less than one hour. Because of the length of the SCADA event, SPA’s Recovery Plan required an evacuation of the PCC to the BCC. SPA took action to mitigate the risk of the violation short of evacuating to its BCC. SPA was meeting its schedules by comparing Net Scheduled Interchange (NSI) to its generator outputs and adjusting generation as required. SPA contacted the Reliability Coordinator (RC) and informed the RC that their SCADA System was out of service. The SPA BCC was available at all time during the SCADA Event. No load shedding or other adverse events occurred. | 11/08/2008 (when SPA failed to install a redundant system) | 5/13/2013 (Mitigation Plan completion) | None | Compliance Investigation | To mitigate this violation, SPA installed four E1000 cards on its fiber ring that provide multiple communication paths at its PCC and BCC. | 2013-05-13 | 2014-06-12 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into Agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective Reliability Standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff and subject matter experts RSMEs attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2012010991 | Settlement Agreement | During a Compliance Investigation conducted from November 2, 2010 to October 6, 2011, NERC determined that SPA, as a Balancing Authority (BA) and Transmission Operator (TOP), was in violation of COM-002-2 R1.1. On January 12, 2010, SPA experienced the loss of its primary control center supervisory control and data acquisition (SCADA) system. The event caused the SPA system operators to lose system visibility and control, and resulted in the curtailment of the system telemetry operating data transmitted to the Reliability Coordinator (RC). During the SCADA event on January 12, 2010, SPA notified the RC but failed to notify potentially affected neighboring BAs and TOPs of a condition that could threaten the reliability of its area. The root cause of the violation was the SPA operator’s failure to follow SPA’s Emergency Evacuation Procedure and inform neighboring BAs and TOPs that SPA had a SCADA outage and was unaware of the status of its system. | COM-002-2 | R1; R1.1 | High | High | The SPP RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPA did not notify neighboring BAs and TOPs of its SCADA outage, the outage was of a short duration and SPA did take steps to minimize the risk to the BPS. SPA contacted the RC and informed the RC of the SCADA outage. The RC continued to monitor SPA’s transmission system by utilizing its State Estimation tool and real-time data from entities adjacent to or integrated with SPA to perform N-1 contingency analysis. The tool estimates telemetry data where real-time data is no longer updating N-1 contingency data every six minutes. At 15:50, a system operator from one of SPA’s neighboring BA/TOPs contacted SPA to inquire about an unrelated matter and SPA informed the operator that SPA was experiencing a SCADA outage. Although SPA did not specifically contact the neighbor, the neighbor was made aware of the SCADA outage. During the SCADA event, SPA mitigated deviations in its ACE by comparing Net Scheduled Interchange (NSI) to its generator outputs and adjusting generation as required. SPA’s BCC was available at all times during the SCADA Event. No load shedding or other adverse events occurred during the SCADA outage. | 1/12/2010 (when SPA's operators became aware of the SCADA outage) | 1/12/2010 (when the SCADA event ended) | None | Compliance Investigation | To mitigate this violation, SPA operations management counselled operations personnel that during events, especially those that affect the SCADA system, they are to specifically notify neighbor BAs and TOPs in addition to the RC. SPA conducted dispatcher training. | 2012-05-01 | 2013-08-29 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into Agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective reliability standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff and subject matter experts attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined that there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2012010992 | Settlement Agreement | During a Compliance Investigation conducted from November 2, 2010, to October 6, 2011, NERC determined that SPA, as a Balancing Authority (BA) and Transmission Operator (TOP), was in violation of TOP-006-1 R1. On January 12, 2010, SPA experienced the loss of its primary control center (PCC) supervisory control and data acquisition (SCADA) system. The event caused the SPA system operators to lose system visibility and control, and resulted in the curtailment of the system telemetry operating data transmitted to the Reliability Coordinator (RC). During the SCADA event on January 12, 2010, SPA did not know the status of all generation and transmission resources available for use on the SPA system. During the Compliance Investigation, it was discovered the design of SPA’s energy management system (EMS) local area network contained a single point of failure, the primary control center network switch. Moreover, SPA did not have the ability to automatically fail over to the backup control center (BCC) in the event the network switch failed. All critical network communications in the PCC and between the PCC and BCC were routed through this single network switch. Although a spare for the network switch was available, it was not installed in a redundant system and required up to 15 minutes to place in service. During the period between the failure of the network switch and startup of the backup switch, the SPA SCADA system in the PCC is inoperable and the SPA system operators do not have visibility or control of the SPA transmission system. The root cause of the noncompliance was the system design's over-reliance on a single network switch. | TOP-006-1 | R1; R1.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPA failed to maintain awareness of the status of its transmission and generation resources, the duration of the SCADA event was short and SPA did inform the RC that it was experiencing a SCADA outage. The RC monitored SPA’s transmission system by utilizing a State Estimation tool that uses real-time data from entities whose transmission systems are adjacent to or integrated with SPA. The State Estimation tool estimates values when real-time data is no longer updating and provides N-1 reliability data every six minutes. The RC had partial visibility of SPA’s system via its SCADA system during the SPA SCADA event. At 15:50, the operator of one of SPA’s neighboring BA/TOPs was informed that SPA was experiencing a SCADA outage. SPA continued to meet its schedules by comparing Net Scheduled Interchange to its generator outputs and adjusting generation as required. SPA’s BCC was available at all time during the SCADA Event. No load shedding or other adverse events occurred during the SCADA outage. | 1/12/2010 (when SPA's operator became aware of the SCADA outage) | 1/12/2010 (when the SCADA event ended) | None | Compliance Investigation | To mitigate this violation, SPA: 1) conducted system operator training addressing SPA’s Alternate or Temporary Emergency Evacuation and BCC Plan for the loss of control center functionality; and 2) installed an additional workstation at the PCC that uses a discrete termination link through the switch located at the BCC, which allows SPA operators to perform monitoring and control through the SCADA server at the BCC without having to physically relocate to the BCC if a SCADA outage occurs at the PCC . | 2012-07-18 | 2013-07-15 | Neither Admits nor Denies | SPP RE reviewed SPA's internal compliance program (ICP) and considered it to be a mitigating factor. SPA has a NERC Reliability Standards compliance program handbook that describes its internal NERC compliance program (Program) and delineates SPA staff roles, responsibilities, and the processes to implement and maintain NERC compliance. SPA is a federal entity. On August 22, 2014, the United States Court of Appeals for the District of Columbia Circuit, in Southwestern Power Administration, et. al. v. Federal Energy Regulatory Commission, Docket No. 13-1033, ordered FERC to set aside the monetary penalty previously affirmed on rehearing the Commission. Since the District Court decision was not appealed and has become final, penalties are not applicable in this case. With the support of senior management, and to aid in coordination, Program implementation, documentation, and tracking of points of contact within the organization for each Reliability Standard, SPA’s Program framework pairs each Reliability Standard with one or more identified responsible parties (i.e. senior manager or senior subject matter expert). SPA’s Compliance Division staff (Division) works with SPA Agency staff to integrate compliance into daily activities and to incorporate compliance with NERC standards into Agency-wide processes and practices. The Division regularly communicates with staff and their supervisors regarding upcoming Program due dates, current status of evidence on-file, and changing aspects of both the standards and the Program as a whole. The Division collects compliance-related documentation and data from the staff to review against the current standards for appropriateness and sufficiency and to retain in a centralized location. The Division performs gap analyses, evaluates quality of documentation provided, conducts internal review of standards, and coordinates with subject matter experts to prepare for audits. The Division regularly holds Agency-wide internal compliance Program updates to discuss current and upcoming Program requirements with staff. SPA senior management receives regular compliance Program activity status and updates. SPA encourages employees to post questions and concerns regarding operations, processes, and procedures via an anonymous employee forum on its intranet. Senior management posts answers to those questions and concerns on the employee forum. In its Program, SPA specifically assigns staff the respective Reliability Standard(s) for which they are responsible. SPA provides required compliance training for all relevant staff specific to the compliance standards for which each individual is responsible. In-depth training sessions are also held with system operations staff regarding compliance directives and procedures. Division staff and subject matter experts attend SPP RE compliance workshops, NERC annual compliance workshops, and internal audit procedure training. The Division meets regularly: to discuss reliability compliance topics; to provide information on (or respond to a request for) interpretation of specific requirements or standards; to discuss other FERC, NERC or Regional Entity guidance and communications; and to prepare for audits. Along with regular internal audits of its Program, SPA contracts third parties to conduct on-site reviews including gap analyses and perform activities such as staff interviews, control room walk-throughs, and review SPA’s compliance documentation. SPA’s corrective action plans include, but are not limited to, staff training, system or process redesign, revision of its workflow processes, and/or the addition of compliance staff to oversee specific Program activities. To prevent compliance violations, SPA’s Program includes controls such as unannounced spot checks, gap analyses, quarterly evidence reporting, and awareness training. Additionally, compliance staff continually assess the effectiveness of Program tasks performed throughout the Agency. The Division forecasts due dates or key milestones and provides reminders to staff and management. The compliance manager and senior management assess organizational structure and staffing, and recommend or make changes as necessary to prevent violations. SPP RE considered SPA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Newmont Nevada Energy Investment, LLC (NNEI) | NCR00377 | WECC2014014118 | Settlement Agreement | During a Compliance Audit conducted from July 7, 2014 through July 9, 2014, WECC determined that NNEI, as a Generator Owner and Transmission Owner, was in violation of PRC-005-1b R1. On July 2, 2013 NNEI updated its Protection System maintenance and testing program and did not include maintenance and testing intervals and their basis for associated communication systems, voltage and current sensing devices, and DC control circuitry in the updated program. Specifically, NNEI’s updated program stated that for the associated communication systems, voltage and current sensing devices, and DC control circuitry for maintenance and testing there is “No set time because these are continuously monitored.” NNEI personnel stated that they misinterpreted PRC-005-1 R1 and modified their language within their procedure leading to the violation. The previous version of the Protection System maintenance and testing program did specify an interval of seven years for the maintenance and testing of the associated communication systems, voltage and current sensing devices, and DC control circuitry. WECC Enforcement determined that NNEI was in violation of PRC-005-1 R1. WECC Enforcement determined that NNEI failed to include maintenance and testing intervals and their basis for associated communication systems, voltage and current sensing devices, and DC control circuitry in its Protection System maintenance and testing program. The root cause of the violation was a lack of compliance understanding. The lack of compliance understanding was likely caused by insufficient training. NNEI did not understand that "continuously monitored" was not considered an appropriate interval. | PRC-005-1b | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NNEI’s failure to include maintenance and testing intervals and basis in its plan could potentially result in misoperation or failure of the relays, leading to the loss of the generators they protect. NNEI was proactive in its process of updating Protection System maintenance and testing procedure. NNEI had a compliant program prior to July 2, 2013, when it updated the maintenance and testing interval in its program. NNEI updated its Protection System maintenance and testing program from having a seven year interval to having no set interval and using the language "continuously monitored" for maintenance and testing of the associated communication systems, voltage and current sensing devices, and DC control circuitry. This continuous monitoring included a verification, or monitoring system, or an alarming channel. Specifically, NNEI had verification of Protection System tripping in place for the DC Control Circuitry. For the Communications Devices, NNEI had monitoring processes in in place to monitor functions that could lead to communications failures, including checks for proper alarm functioning. It also included monitoring output from current and voltage sensing devices. While NNEI’s program did not include maintenance and testing intervals and their basis for those devices, NNEI did test and maintain its Protection System devices on a five-year basis. No harm is known to have occurred. The devices continued to be monitored and tested on an appropriate interval and no events were known to have occurred during the duration of the violation. | 7/2/2013 (when NNEI revised its maintenance and testing program to include the “continuously monitored” language) | 8/27/2014 (the date NNEI updated its program to include a basis and five-year interval for its relays and associated communication systems, voltage and current sensing devices, and DC control circuitry.) | $16,000 (for WECC2014014118 and WECC2014014119) | Compliance Audit | To mitigate this violation, NNEI modified the language in its procedure to include an interval of five years for the maintenance and testing of all its protection relays, including associated communication systems, voltage and current sensing devices, and DC control circuitry. | 2014-08-27 | TBD | Agrees/Stipulates | As part of the settlement, NNEI agreed to complete WECC’s Internal Compliance Program Assessment (ICPA). NNEI also agreed to implement, develop, and/or improve an Internal Compliance Program (ICP), based on the results of the ICPA and to distribute the ICP to all applicable employees, contractors, and vendors. NNEI shall submit to WECC a narrative describing how NNEI developed or improved, implemented, and distributed its ICP by December 12, 2014. WECC considered NNEI's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Newmont Nevada Energy Investment, LLC (NNEI) | NCR00377 | WECC2014014119 | Settlement Agreement | During a Compliance Audit conducted from July 7, 2014 through July 9, 2014, WECC determined that NNEI, as a Generator Owner and Transmission Owner, was in violation of PRC-005-1 R2. The Audit Team determined that NNEI failed to have evidence that Protection System devices were maintained and tested within the defined intervals. Specifically, NNEI could not verify the intervals for the maintenance and testing records for associated communication systems, voltage and current sensing devices, and DC control circuitry because NNEI did not have the Protection System maintenance and testing intervals and basis as required under R1 for “Prior Test Date” for these devices within its Protection System maintenance and testing program. In addition, NNEI failed to test one relay in 2010 due to operational constraints. In 2010, when the relay was due to be tested, NNEI’s only power supply to the power plant was the 120 kV transmission line, which limited any testing on this system, including the relay that missed testing. NNEI has since installed an alternative back feed system to allow the plant a secondary auxiliary power source, which would enable maintenance and testing to be carried out on the 120 kV system while the plant is down. As a result of its examination, the Audit Team determined that NNEI was in violation of PRC-005-1 R2. WECC Enforcement determined that NNEI failed to have evidence that Protection System devices were maintained and tested within the defined intervals. As a result, Enforcement determined that NNEI was in violation of PRC-005-1 R2. In this case, NNEI was missing evidence that Protection System devices were maintained and tested within the defined intervals for more than 15% of the applicable devices. The root cause of the violation was a lack of compliance understanding. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNEI failed to have evidence that Protection System devices were maintained and tested within the defined intervals. Testing of the Protection Systems helps determine if the devices are reliable to limit the effects of disturbances in a system network. If there is no evidence that the devices were tested according to the program defined by the entity, the devices cannot be entrusted to interrupt disturbances that may damage the transmission system and/or generation plants. NNEI’s TS Power Plant is a 270 MVA (242 MW) coal fired generating unit, with 18/120 kV GSU Transformer, 6.5 miles of 120kV transmission line, and single interconnection point at a substation owned by a neighboring entity at 120kV/345 kV step up transformer. The Protection System devices owned and operated by the neighboring entity should adequately protect the BPS from misoperation of protection devices at NNEI’s power plant. While NNEI’s intervals for maintaining and testing were not consistent with the maintenance and testing procedures, maintenance and testing was being performed on the associated communication systems, voltage and current sensing devices, and DC control circuitry. In addition, NNEI did not test a relay in 2010 due to operational constraints, which according to NNEI, have since been remedied. No harm is known to have occurred. The devices continued to be monitored and tested on an appropriate interval and no events were known to have occurred during the duration of the violation. | 7/23/2008 (when NNEI registered as a Generator Owner and Transmission Owner) | Present | $16,000 (for WECC2014014118 and WECC2014014119) | Compliance Audit | To mitigate this violation, NNEI will test all relays and associated communication systems, voltage and current sensing devices, and DC control circuitry during its annual shutdown. | 4/30/2015 (approved completion date) | TBD | Agrees/Stipulates | As part of the settlement, NNEI agreed to complete WECC’s Internal Compliance Program Assessment (ICPA). NNEI also agreed to implement, develop, and/or improve an Internal Compliance Program (ICP), based on the results of the ICPA and to distribute the ICP to all applicable employees, contractors, and vendors. NNEI shall submit to WECC a narrative describing how NNEI developed or improved, implemented, and distributed its ICP by December 12, 2014. WECC considered NNEI's compliance history and determined there were no relevant instances of noncompliance.