## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2013013258 | Settlement Agreement | On December 12, 2013, Entergy submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2. Entergy failed to have evidence of maintenance of a portion of the Protection System. During an ongoing systematic review of Entergy’s substation work management system (SWMS), Entergy determined that evidence of maintenance did not exist for eight protective relays and one lockout relay in a backup protection panel at Sabine Station’s 230 kV substations. The root cause was inadequate work planning and execution. While SERC was performing its assessment and determining the scope of the violation, Entergy reported the following additional issues: 1. In a second instance, Entergy incorrectly identified three backup Protection System relays at the Lynch Plant 115 kV Substation as not being applicable to PRC-005. Entergy cannot provide evidence that this equipment has been maintained and tested within the required intervals. The root cause was inadequate work planning and execution. 2. In a third instance, Entergy failed to provide evidence that two relays related to a breaker failure protection scheme at Mabelvale 500 kV substation had been maintained and tested within the required intervals. The root cause was that the entity misinterpreted the definition of transmission Protection System to only include equipment operated at 100 kV or above. 3. In a fourth instance, also at Mabelvale, Entergy incorrectly identified three relays as non-PRC-005 applicable. Although these devices primarily protect a shunt reactor at less than 100 kV, they are located in the tertiary circuit of a 500 kV to 115 kV autotransformer. The relays are considered transmission Protection System devices because their failure to trip could cause damage to the autotransformer. The root cause was that the Protection System maintenance and testing program was not sufficient with respect to testing when there are multiple schemes on a panel. 4. In a fifth instance, during a review of upcoming work, an employee identified six relays which had been in the Protection System, but maintenance had incorrectly been suspended in the maintenance database. The protection in question was associated with a 230 kV transmission line at the Freeport 230 kV substation. The 230 kV transmission line was physically removed in 2010. Although the line had been removed, the relays still provided protection for a 27 foot long bus bar in the substation footprint. Entergy cannot provide evidence that this equipment was maintained and tested within the required intervals. The root cause was inadequate work planning and execution. Entergy had 15 relays that should have been included in the Protection System maintenance and testing program but were not. In addition, Entergy did not maintain eight relays in the transmission Protection System in accordance with the maintenance and testing program. Entergy confirmed that the other Protection System devices associated with these 23 relays had been properly maintained. SERC determined that Entergy was in violation of PRC-005-1 R2 because Entergy could not provide evidence Protection System devices were maintained and tested within the defined intervals for eight relays. Entergy also failed to provide evidence of the date each Protection System device was last tested or maintained for 15 relays. Entergy was unable to provide evidence that 23 out of 12,462 (0.18%) relays were tested within the defined interval or the date they were last tested or maintained. In total, Entergy failed to provide evidence that 23 out of 54,452 (0.042%) Protections System devices were tested within the defined interval or the date they were last tested or maintained. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Improper maintenance and testing could result in device failure resulting in equipment damage, and reduction of reliability of a portion of the BPS. However, in the first instance, the risk was isolated to the auxiliary transformer at a single generating station. The affected devices provided backup protection for that transformer and the devices providing primary protection panel had been maintained according to Entergy’s Protection System maintenance program. In the second instance, the affected breaker was a bus tie breaker at a 115 kV substation. The relays in question provide backup protection for the bus tie if the breaker fails to trip. Primary protection relays were properly maintained and available for protection. In the third instance, the relays are in a “fail to trip” scheme and would only have been called upon if the primary and backup relaying failed to trip the breaker. Subsequent testing found no problems with the relays. In the fourth instance, the autotransformer tertiary winding was equipped with internal protective devices that would have operated to protect the transformer. The relays in question successfully cleared a fault in 2009. Subsequent testing found no problems with the relays. In the fifth instance, the relays were associated only with protection of substation bus work 27 feet long, and the probability of a fault at that location is small because there is no connected transmission line. The relays involved are in two separate and redundant trip schemes, and the simultaneous loss of both schemes is unlikely. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | present | $0 | Self-Report | To mitigate this violation, Entergy: 1) completed required maintenance for each identified overdue task; and 2) updated the SWMS to properly identify each of the identified panels as “SERC Applicable” and requiring maintenance, as per PRC-005. To mitigate this violation, Entergy will: 1) update Protection System maintenance procedure(s) to provide guidance on how to handle panels with multiple schemes; 2) reference the NERC "Bulk Electric System Definition Reference Document" along with Section 4.2 of PRC-005-2 in the Planner/Scheduler training for new and existing employees; 3) provide targeted training on the updated procedure(s) and the “Bulk Electric System Definition” to ensure substation supervisors, planner schedulers, and relay technicians are informed of the changes; 4) develop a systematic approach to perform transmission Protection System component inventory validation; and 5) complete validation of transmission Protection System component inventory for all Entergy transmission substations. | 12/18/2015 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed Entergy's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Entergy has a documented ICP, which consists of multiple system policies for all areas of compliance including NERC Reliability Standards. The ICP is reviewed at least annually. The ICP requires that all senior management be responsible for ensuring that their subordinates are aware of and understand the ICP. The corporate compliance committee (CCC) oversees the ongoing development and maintenance of Entergy’s policies and procedures concerning legal compliance issues and business ethics and oversees activities undertaken to promote adherence with such policies and procedures. The CCC meets quarterly and is responsible for the development and the promotion of Entergy’s compliance and business ethics policies and procedures. Entergy’s corporate compliance officer (vice- president, ethics and compliance and member of the CCC) reports directly to the senior vice- president and general counsel, and has independent access to Entergy’s board of directors audit committee. A Settlement Agreement covering a violation of PRC-005 R2 for Entergy was filed with FERC under NP14-6-000 on November 27, 2013. On December 27, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering two violations of PRC-005 R2 for Entergy was filed with FERC under NP13-10-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered Entergy’s PRC-005 R2 compliance history to be an aggravating factor in the penalty determination. As part of its Mitigation Plan, Entergy committed to complete the validation of its transmission Protection System inventory for all of its transmission substations. Entergy estimates that it will spend 13,000 man hours and in excess of $2,500,000 to complete the project. SERC considered Entergy's investment of resources to complete this project a mitigating factor when assessing the penalty.
SERC Reliability Corporation (SERC) | USACE - Fort Worth District (USACE-FW) | NCR11109 | SERC2012011529 | Settlement Agreement | During a Compliance Audit conducted from November 27, 2012 through November 29, 2012, SERC determined that USACE-FW, as a Generator Owner (GO) and Transmission Owner (TO), was in violation of PRC-005-1 R2. The SERC audit team reported that USACE-FW did not have all the documentation to verify that it had completed the maintenance and testing on all of its Protection System devices. SERC reviewed a spreadsheet prepared by USACE-FW that included its Protection System devices and the date of evidence that maintenance and testing had been performed on those Protection System devices. SERC determined that USACE-FW’s Protection System consists of 48 protective relays, 99 voltage and current sensing devices, 32 DC control circuits, and one battery bank. USACE-FW’s Protection System does not use associated communication systems. USACE-FW could not provide evidence that it maintained and tested 34 of the 46 (73.9%) current transformers (CTs) associated with its generator Protection System in previous years. SERC confirmed the audit finding that USACE-FW commonly included DC control system testing in its relay testing but USACE-FW was unable to produce evidence that the tests were performed on all of its DC control circuits. SERC reviewed a sample of completed work orders for DC control circuits testing. SERC reviewed evidence that USACE-FW had been maintaining the single station battery on a monthly and annual basis and reviewed evidence showing previous test dates. Because USACE-FW did not have a Protection System maintenance and testing program that defined the intervals for maintenance and testing, SERC could not verify that USACE-FW had conducted maintenance and testing within the defined interval for any of its Protection System devices, except for the station battery. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. USACE-FW produced evidence that it maintained and tested most of its Protection System devices despite the lack of a formal program. The affected generator units are two 26 MW hydropower peaking units, operate at a capacity factor of approximately four percent, and interconnect to two transmission owners at 138 kV. SERC determined that USACE-FW had maintained and tested all 26 of the 26 (100%) protective relays associated with its generator Protection System in 2012. USACE-FW also had maintained and tested 12 of the 46 (26.1%) CTs and eight of eight (100%) potential transformers (PTs) associated with its generator Protection System in previous years. SERC determined that USACE-FW had maintained and tested 22 of 22 (100%) relays, 36 of 36 (100%) CTs, and nine of nine (100%) PTs associated with its transmission Protection System in previous years. No harm is known to have occurred. | 3/31/2011 (when USACE-FW registered as a GO and TO) | present | No Penalty | Compliance Audit | To mitigate this violation, USACE-FW will: 1) establish testing and maintenance intervals for its Protection System devices (protective relays, CTs, PTs, DC control circuits, and batteries) in its facility and equipment maintenance (FEM) database as part of the Protection System work orders; and 2) create a work order in its FEM database detailing how and when it will complete the testing and maintenance of its Protection System devices using developed or existing testing procedures. | 4/3/2015 (approved completion date) | TBD | Neither Admits Nor Denies | SERC reviewed USACE-FW’s internal compliance program (ICP) and considered it to be a mitigating factor. The ICP is documented and distributed to USACE-FW's operations staff. Training is provided to plant personnel for the Reliability Standards they are responsible for executing. USACE-FW has a reliability compliance program manager (RCPM) who is responsible for the daily operation of the ICP. The RCPM reports directly to the USACE-FW commander, who is the reliability compliance program administrator, who has overall authority over USACE-FW's ICP. The ICP includes self-assessments and self-enforcement of internal controls to prevent recurrence of violations of Reliability Standards. USACE-FW also has started an annual review program of its ICP. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain entities including noncompliance with PRC-005-1 R1 for USACE-FW was posted on the NERC website on June 26, 2014. The 60-day review period passed on August 25, 2014. USACE-FW is a federal entity.
Western Electricity Coordinating Council (WECC) | City of Roseville (CYRO) | NCR05094 | WECC2014013601 | Settlement Agreement | On February 28, 2014, CYRO submitted a Self-Certification stating that, as a Generator Operator, it was in violation of PRC-001-1 R3. WECC determined that CYRO was in violation of PRC-001-1 R3 because on October 17, 2009, CYRO changed a protective system relay setting and did not coordinate with its Transmission Operator (TOP) or Host Balancing Authority (BA). The protective system relay is associated with two separate neutral overcurrent protection elements for auxiliary transformer digital relays. CYRO failed to coordinate the relay setting change with its TOP or Host BA. CYRO discovered this failure on February 10, 2014 while CYRO was performing its Self-Certification review and preparing for a mock audit. The root cause of this violation was human error. During re-wiring and misoperation assessment, CYRO decided to change the setting of the relay that responded to the monitored ground current to help minimize nuisance tripping of the generating unit, while still providing acceptable protection. CYRO could not find any evidence that CYRO staff had consulted with, notified, or coordinated with CYRO's TOP | PRC-001-1 | R3.1 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CYRO's failure to coordinate the relay setting changes with its TOP or BA could have resulted in a relay misoperation and the loss of up to 160 MW of generation. Although CYRO failed to coordinate the relay setting changes, the transformer at issue utilized redundant ground default settings that would detect a ground fault. CYRO utilizes protection relays throughout its facilities that also detect ground faults and protect equipment. CYRO has a Supervisory Control and Data Acquisition (SCADA) system that monitors mechanical and electrical quantities, plant status, and protection relay outputs and alarms. CYRO’s SCADA system issues an alarm if an incident occurs. The auxiliary transformer at issue only provides power for plant loads associated with the generator and only impacts the BPS when a protection action occurs by tripping the generator output breaker and switchyard breakers. CYRO’s generation largely provides for sub-100 kV loads within its distribution system and only a fraction of the power is provided to the BPS. No harm is known to have occurred. | k | 6/27/2014 (when CYRO communicated the protective system relay setting change with its TOP or Host BA) | $17,000 (for WECC2014013601, WECC2014013347, WECC2013013093, WECC2014013567, and WECC2013013094) | Self-Certification | To mitigate this violation, CYRO: 1) communicated to the TOP, the Western Area Power Administration (“WAPA”) and the Host BA of Northern California (BANC) the relay settings that were changed; 2) modified its existing policies and/or procedures for instructing affected personnel to notify BANC and WAPA when changes to protective system equipment are made; 3) provided copies of the modified procedure/policy to affected personnel; and, 4) provided exposure and training to all affected personnel and documented their understanding of the policy | 9/30/2014 | 10/29/2014 | Agrees/Stipulates | WECC has not reviewed CYRO's internal compliance program (ICP). WECC considered CYRO's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | City of Roseville (CYRO) | NCR05094 | WECC2014013347 | Settlement Agreement | On January 15, 2014, CYRO submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-005-1b R1. WECC determined CYRO was in violation of PRC-005-1b R1 because CYRO failed to include battery chargers in its Protection System maintenance and testing program. The root cause of this violation was CYRO’s lack of compliance understanding. CYRO was not aware that NERC revised the definition of "Protection System" to include battery chargers. As a result, CYRO's maintenance and testing program, effective on March 27, 2013, did not mention battery chargers. | PRC-005-1b | R1 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CYRO's failure to identify battery chargers in its Protection System maintenance and testing program could cause CYRO’s Protection System equipment to misoperate when the equipment is needed to protect CYRO’s system. Although CYRO failed to identify battery chargers in its Protection System maintenance and testing program, CYRO did include battery chargers in its maintenance and testing schedule. CYRO also has alarms that are monitored in real-time that alert CYRO’s control room if there are any issues with the battery chargers. CYRO delivers supply to load at two points, each capable of delivering required load if the other fails. The battery chargers were maintained and tested, even though they weren't mentioned in CYRO's maintenance and testing program. This was a documentation error. No harm is known to have occurred. | 4/1/2013 (when NERC revised its definition of Protection Systems to include battery chargers) | 2/20/2014 (when CYRO submitted its revised Protection System maintenance and testing program) | $17,000 (for WECC2014013601, WECC2014013347, WECC2013013093, WECC2014013567, and WECC2013013094) | Self-Report | To mitigate this violation, CYRO updated its SOP 8.10 Protection System maintenance and testing program to include battery chargers. | 2014-02-20 | 2014-04-28 | Agrees/Stipulates | WECC has not reviewed CYRO's internal compliance program (ICP). A Settlement Agreement covering violations of PRC-005 R1 for CYRO was filed with FERC under NP14-6-000 on November 27, 2013. On December 27, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC considered CYRO’s PRC-005 R1 compliance history to be an aggravating factor in the penalty determination. This was CYRO’s second violation of PRC-005-1b R1. The prior violation was assigned NERC Violation ID WECC2012011094. In that case, CYRO did not have a maintenance and testing program for all of its Protection System devices. Specifically, CYRO failed to include certain Protection System devices in its maintenance and testing program. CYRO also failed to detail its maintenance and testing procedures and did not specify its intervals and the basis for those intervals in violation of PRC-005 R1.1 and R1.2.
Western Electricity Coordinating Council (WECC) | City of Roseville (CYRO) | NCR05094 | WECC2013013093 | Settlement Agreement | On October 18, 2013, CYRO submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-005-1b R2. WECC determined that CYRO was in violation of PRC-005-1b R2 because CYRO transitioned to a new software system that failed to include CYRO’s 648 batteries. As a result, CYRO failed to perform monthly battery tests in April, May, June, and July 2013 and quarterly battery tests in the second quarter of 2013 at three seperate generation Protection System locations. CYRO also failed to perform quarterly battery tests in the second and third quarters of 2013 at one substation location and failed to perform quarterly battery tests in the second quarter of 2013 at another substation location. The root cause of this violation was CYRO’s transition to a new software system that, at the time, did not include batteries because they were not input into the software. | PRC-005-1b | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CYRO's failure to perform monthly and quarterly battery tests put the 648 batteries at a higher risk of failure that would not allow the relays to operate and clear a potential fault. A fault could result in the loss of 160 MW of generation. Although CYRO failed to perform monthly and quarterly tests, the potential risk associated with this failure is mitigated because CYRO did perform maintenance and testing on all other Protection System devices. The potential risk was further mitigated because CYRO did perform monthly and quarterly battery tests, other than the four missed monthly tests and the missed quarterly tests in 2013. No harm is known to have occurred from CYRO’s failure to perform these battery tests. | 5/1/2013 (when CYRO failed to provide evidence that its Protection System devices were maintained and tested within defined intervals) | 2/7/2014 (when CYRO completed all deficient battery tests and inspections) | $17,000 (for WECC2014013601, WECC2014013347, WECC2013013093, WECC2014013567, and WECC2013013094) | Self-Report | To mitigate this violation, CYRO: 1) reviewed testing and maintenance records to ensure there were no additional deficiencies; 2) created an Outlook calendar with automatic alerts as a reminder for all battery maintenance and testing; 3) populated the maintenance management software (Maximo) to schedule and plan all required maintenance and testing; 4) added a compliance component to the monthly safety meeting to forecast compliance work; and 5) scheduled and completed all deficient battery tests and inspections. | 2/7/2014 | 7/18/2014 | Agrees/Stipulates | WECC has not reviewed CYRO's internal compliance program (ICP). A Settlement Agreement covering violations of PRC-005 R2 for CYRO was filed with FERC under NP14-6-000 on November 27, 2013. On December 27, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC considered CYRO’s PRC-005 R2 compliance history to be an aggravating factor in the penalty determination. This was CYRO’s second violation of PRC-005-1b R2. The prior violation was assigned NERC Violation ID WECC2013012732. In that case, CYRO was required to test all of its Protection System devices as outlined in CYRO’s Protection System maintenance and testing program. CYRO failed to test or maintain documentation for 21 out 56 relays, 72 out of 168 instrument transformers, 4 out of 7 batteries, and 21 out of 40 DC control circuits resulting in a violation of PRC-005 R2.
Western Electricity Coordinating Council (WECC) | City of Roseville (CYRO) | NCR05094 | WECC2014013567 | Settlement Agreement | On March 3, 2014, CYRO submitted a Self-Certification stating that, as a Distribution Provider, it was in violation of PRC-008-0 R2. WECC determined that CYRO was in violation of PRC-008-0 R2 because CYRO transitioned to a new software system that failed to include batteries. CYRO has batteries at eight substations that provide DC power to the equipment that operates the Under Frequency Load Shedding (UFLS) device CYRO did not perform battery testing in the first quarter of 2013 at four substations. CYRO also did not perform battery testing in the second quarter of 2013 at all eight substations CYRO did not perform Potential Transformer (PT) testing at two of the eleven UFLS PT locations. CYRO did not maintain and/or test eleven sets of PTs and that six battery systems had their monthly maintenance intervals exceeded. The root cause of this violation was CYRO’s transition to a new software system that, at the time, did not include batteries. CYRO also was in the process of filling a staffing vacancy related to substation maintenance and metering. | PRC-008-0 | R2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. If CYRO’s UFLS fails to operate at a station due to battery failure, load would not be shed as required which could cause a slight delay in restoration of acceptable system frequency in CYRO’s local area. If CYRO failed to test PT's there was a possibility of unkown PT failure which may increase risk to the BPS. Failure to maintain and test battery systems could also increase risk to the BPS. Although CYRO failed to perform quarterly UFLS battery maintenance and testing, the potential risk is mitigated because CYRO maintained and tested all other elements and devices associated with its UFLS program. No harm is known to have occurred. | 5/1/2013 (31 days after the battery tests were missed in the first quarter) | 8/5/2014 (Mitigation Plan completion) | $17,000 (for WECC2014013601, WECC2014013347, WECC2013013093, WECC2014013567, and WECC2013013094) | Self-Certification | To mitigate this violation, CYRO: 1) reviewed testing and maintenance records to ensure there were no additional deficiencies; 2) created an Outlook calendar with automatic alerts as a reminder for all battery maintenance and testing; 3) populated the maintenance management software (Maximo) to schedule and plan all required maintenance and testing; 4) followed its maintenance and testing program for battery checks and testing and performed and/or scheduled all subsequent inspections according to schedule; 5) added a compliance component to the monthly safety meeting to forecast compliance work; and 6) performed testing of the PTs at the substations and submitted testing records. | 8/5/2014 | 9/30/2014 | Agrees/Stipulates | WECC has not reviewed CYRO's internal compliance program (ICP). WECC considered CYRO's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | City of Roseville (CYRO) | NCR05094 | WECC2013013094 | Settlement Agreement | On October 18, 2013, CYRO submitted a Self-Report stating that, as a Distribution Provider, it was in violation of PRC-011-0 R2. WECC determined that CYRO was in violation of PRC-011-0 R2 because CYRO transitioned to a new software system that failed to include batteries. CYRO has seven battery banks at six substations that are associated with CYRO’s Undervoltage Load Shedding System (UVLS) maintenance and testing program. CYRO failed to perform first quarter 2013 battery tests at two locations. CYRO failed to perform second quarter 2013 battery tests at six locations. The root cause of this violation was CYRO’s transition to a new software system that, at the time, did not include batteries. CYRO also was in the process of filling a staffing vacancy related to substation maintenance and metering. | PRC-011-0 | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). If CYRO’s UVLS batteries failed, it would not allow the relays to operate and clear a fault which could cause damage to the associated BPS elements. Although CYRO failed to perform quarterly tests of the UVLS batteries, CYRO did perform monthly tests during the period of noncompliance which would have alerted CYRO to any problems. CYRO’s UVLS system is used to protect its 60kV distribution system and not the BPS, resulting in negligible impact to the BPS. No harm is known to have occurred from CYRO’s failure to perform quarterly tests of the UVLS batteries. | 4/1/2013 (thirty days after CYRO missed the battery tests) | 1/1/2014 (Mitigation Plan completion) | $17,000 (for WECC2014013601, WECC2014013347, WECC2013013093, WECC2014013567, and WECC2013013094) | Self-Report | To mitigate this violation, CYRO: 1) reviewed testing and maintenance records to ensure there were no additional deficiencies; 2) created an Outlook calendar with automatic alerts as a reminder for all battery maintenance and testing; 3) added a compliance component to the monthly safety meeting to forecast compliance work; and 4) scheduled and completed all deficient battery tests and inspections. | 1/1/2014 | 11/24/2014 | Agrees/Stipulates | WECC has not reviewed CYRO's internal compliance program (ICP). WECC considered CYRO's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Frederickson Power LP (FPWR) | NCR05164 | WECC2014013602 | Settlement Agreement | During an internal NERC Compliance Assessment of FPWR's Power Purchaser, NERC and FPWR's Power Purchaser determined that there was a concern with FPWR's Compliance with PRC-005-1 R2. FPWR's Power Purchaser notified FPWR there was a potential issue regarding PRC-005 R2. On February 11, 2014, FPWR submitted a Self-Certification stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. FPWR stated that it had an issue related to packaged electrical and electronic control compartment (PEECC) station battery maintenance and testing interval. In FPWR's generator Protection System maintenance and testing program, it states that FPWR will perform maintenance and load testing for the PEECC station batteries within the defined interval of five years. FPWR's PEECC station batteries were maintained and tested at an eight-year interval. WECC reviewed FPWR's maintenance and testing information and found that the station battery was last load tested on November 9, 2005; therefore the load test would have been due November 9, 2010, but FPWR failed to conduct the test within the allotted time. Further, WECC requested additional data on DC control circuitry testing from FPWR. WECC found that 100% of DC control circuit maintenance performed in 2009 was not completed. FPWR could not provide evidence that maintenance and testing was done in 2009. WECC found that FPWR failed to maintain and test one of three (33.3%) station batteries within the defined interval of FPWR's generator Protection System maintenance and testing program and failed to maintain and test 100% of its DC control circuitry. The root cause was both human error and inadequate documentation. FPWR overlooked performing the load test for one of three (33.3%) station batteries. There was an assumption made that it was performed when the other two batteries were tested. In the case of the DC control circuits, the root cause was due to inadequate documentation for the prior tests. | PRC-005-1 | R2, R2.1, R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to conduct maintenance and testing on Protection System devices within their specified interval could potentially result in the failure of the Protection System devices to operate in the expected fashion which could lead to a loss of up to 249 MW of generation. FPWR did implement good detective controls to reduce the loss of generation. Specifically, FPWR utilizes a supervisory control and data acquisition system which monitors the generators and interconnection quantities, and provides alarms to personnel that monitor the system on a continuous basis. FPWR also utilizes a roving operator that performs logging of unit and battery quantities at least twice a day. Further, for the battery system, FPWR performed quarterly and annual maintenance on the station battery. Also, FPWR has a battery charger for the battery that would carry the DC loads upon a loss of the battery. FPWR reviewed the results of the DC control circuitry test results, which indicated that the DC control circuitry performed as required in 2012. No harm is known to have occurred. | 1/1/2009 (when FPWR missed its testing for DC control circuits) | 11/1/2013 (when FPWR completed its maintenance and testing on the station battery) | $0 | Self-Certification | To mitigate this violation, FPWR: 1) completed the load testing on the station battery; 2) provided training to maintenance personnel on PRC-005 maintenance and testing program and the importance of meeting the defined intervals within its maintenance and testing program with zero slippage; 3) added the five year station battery load testing to its preventative maintenance program; 4) added all devices as listed in the NERC Glossary of Terms definition of Protection Systems (protective relays, associated communication systems, voltage and current sensing devices, station batteries, battery chargers and DC control circuitry) into its preventative maintenance program; 5) entered work orders that include the dates each Protection System device was last tested/maintained into the maintenance management system so that the work orders would be automatically printed and include the description of work to be completed and when device is due for maintenance and testing; 6) ensured that work orders will be completed as scheduled by having management be responsible for the work orders; and 7) completed testing on all DC control circuitry. | 12/20/2013 | 10/8/2014 | Agrees/Stipulates | WECC considered FPWR's compliance history and determined there were no relevant instances of noncompliance. WECC decided not to assess a financial penalty against FPWR. Instead, FPWR will submit to WECC by April 1, 2015, via WECC Compliance Enhanced File Transfer Server a narrative describing how FPWR plans to implement the following additional terms of settlement: 1) FPWR will complete WECC’s Internal Compliance Program Assessment (ICPA); 2) based on results or weaknesses identified by FPWR in its ICPA, develop, augment, or improve and implement its ICP; 3) FPWR will submit with its ICPA a narrative detailing the improvements or modifications it made to its ICP; and 4) enhance its PRC-005-1 R2 procedures to require duplicative review associated with PRC-005-1 R2 compliance. For example, develop peer review checklist and procedures for ensuring FPWR maintains applicable, timely, PRC-005-1 R2 reviews and documentation.