## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011513 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Transmission Operator (TOP), Balancing Authority (BA), and Generator Operator (GOP), it was in violation of PRC-001-1 R1. PGE failed to be familiar with the purpose and limitations of Protection System schemes applied in its area. PGE reported that it placed two Local Area Protection Schemes (LAPS) into service, but PGE did not identify them as Special Protection Schemes (SPS). As a result, PGE did not perform certain actions for the SPS as required by the NERC Reliability Standards, including PRC-001-1 R1. PGE placed the first LAPS, the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and since that time the LAPS operated successfully on two separate occasions. PGE placed the second LAPS, the Port Westward Generation Runback Scheme, in service on September 29, 2010, and this scheme has not operated since it was placed in service. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-001-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. If PGE's Grand Ronde SPS misoperated, the local 115 kV facilities could be exposed to low-voltage. Misoperation of the Port Westward SPS could result in a thermal overload to the remaining 230 kV line, which connects the Port Westward switchyard to PGE’s Bulk Electric System (BES) at Trojan. At Grand Ronde, a security misoperation would reduce system reliability by removing one element from service, increasing the exposure to load loss. At Port Westward, a security misoperation would have resulted in the unnecessary loss of generation with no impact to the BES. A dependability misoperation would have resulted in potential transmission line damage due to overload. The impact to the BPS would be mitigated by the transmission line relays at the remote end tripping in response to the damage. In this instance, PGE's personnel were not familiar with two protection schemes. The first LAPS was capable of tripping a breaker which could in certain circumstances result in shedding up to 40 MW of load, the other scheme could curtail generation up to 337 MW. However, despite not recognizing the LAPS as SPS, PGE was aware of the systems and continuously monitored the relays located on the SPS. PGE had real-time monitoring in place for this equipment and transmission operators would have been alarmed as to any system irregularities relating to these SPS. The one scheme is performed by transmission line relays, which is monitored by transmission operators and the other scheme is monitored through various equipment failure alarms at the plant and by transmission operators. Additionally, PGE performed regular maintenance and testing on the Protection System devices as part of PGE's Protection System Maintenance and Testing Program. Further, the first LAPS operated correctly on two separate occasions. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the TOPs, BA, and GOPs on the modification made at the Port Westward and the Grand Ronde schemes, training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained protection engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPSs and data for the Grand Ronde Remedial Action Scheme (RAS) to Remedial Action Scheme Reliability Subcommittee (RASRS) as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; 7) implemented the Grand Ronde test plan; 8) coordinated with neighboring TOPs and BA to insure full understanding of any potential impacts of the Grand Ronde SPS on their systems; and 9) revised procedures to address the notification of affected TOPs and BAs of each change in status of the Grand Ronde SPS. | 12/23/2013 | 2014-01-03 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011514 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Generator Operator (GOP) and Transmission Operator (TOP), it was in violation of PRC-001-1 R3. PGP failed to coordinate two new protective systems with its TOP and Host Balancing Authority (BA). PGE reported that it placed two Local Area Protection Schemes (LAPS) into service, but PGE did not identify them as Special Protection Schemes (SPS). As a result, PGE did not perform certain actions for the SPS as required by the NERC Reliability Standards, including PRC-001-1 R3. PGE placed the first LAPS, the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and since that time the LAPS operated successfully on two separate occasions. PGE placed the second LAPS, the Port Westward Generation Runback Scheme, in service on September 29, 2010, and this scheme has not operated since it was placed in service. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-001-1 | R3; R3.1; R3.2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE failed to coordinate two protective system changes with its TOP and Host BA. If PGE's Grand Ronde SPS misoperated, the local 115 kV facilities could be exposed to low-voltage. Misoperation of the Port Westward SPS could result in a thermal overload to the remaining 230 kV line, which connects the Port Westward switchyard to PGE’s Bulk Electric System (BES) at Trojan. At Grand Ronde, a security misoperation would reduce system reliability by removing one element from service, increasing the exposure to load loss. At Port Westward, a security misoperation would have resulted in the unnecessary loss of generation with no impact to the BES. A dependability misoperation would have resulted in potential transmission line damage due to overload. The impact to the BPS would be mitigated by the transmission line relays at the remote end tripping in response to the damage. However, PGE continuously monitored the relays on its SPS and routinely conducted maintenance and testing on the system devices as part of PGE's Protection System Maintenance and Testing Program. PGE had real-time monitoring in place for this equipment and transmission operators would have been alarmed as to any system irregularities relating to these SPS. The one scheme is performed by transmission line relays, which is monitored by transmission operators and the other scheme is monitored through various equipment failure alarms at the plant and by transmission operators. Had the devices been required to operate, PGE would have been aware and would have been able to notify its TOP and Host BA of any changes. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the TOPs, BA and GOPs on the modification made at the Port Westward and the Grand Ronde schemes, training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained protection engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPS and data for the Grand Ronde Remedial Action Scheme (RAS) to Remedial Action Scheme Reliability Subcommittee (RASRS) as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; 7) implemented the Grand Ronde test plan; 8) coordinated with neighboring TOPs and BA to insure full understanding of any potential impacts of the Grand Ronde SPS on their systems; and 9) revised procedures to address the notification of affected TOPs and BAs of each change in status of the Grand Ronde SPS. | 12/23/2013 | 2014-01-03 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011515 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Transmission Operator (TOP) and Balancing Authority (BA), it was in violation of PRC-001-1 R6. PGE placed two Local Area Protection Schemes (LAPS) into service, but PGE did not identify them as Special Protection Schemes (SPS). As a result, PGE did not perform certain actions for the SPS as required by the NERC Reliability Standards, including PRC-001-1 R6. PGE reported that it did not properly monitor these two SPS and failed to notify affected TOPs and BAs of the two status changes that occurred. The two SPS in scope included the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and the Port Westward Generation Runback Scheme, in service on September 29, 2010. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-001-1 | R6 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE did not identify two LAPS as SPS which caused PGE to improperly monitor the status of each SPS in its area and notify affected TOPs and BAs of each status change of its SPS. As a result, when PGE's SPS operated on at least two occasions, its surrounding utilities were not aware of the cause for generation curtailment on the line. If PGE's Grand Ronde SPS misoperated, the local 115 kV facilities could be exposed to low-voltage. Misoperation of the Port Westward SPS could result in a thermal overload to the remaining 230 kV line, which connects the Port Westward switchyard to PGE’s Bulk Electric System (BES) at Trojan. At Grand Ronde, a security misoperation would reduce system reliability by removing one element from service, increasing the exposure to load loss. At Port Westward, a security misoperation would have resulted in the unnecessary loss of generation with no impact to the BES. A dependability misoperation would have resulted in potential transmission line damage due to overload. The impact to the BPS would be mitigated by the transmission line relays at the remote end tripping in response to the damage. However, PGE continuously monitored the relays on the SPS and the system properly actuated on two occasions. PGE had real-time monitoring in place for this equipment and transmission operators would have been alarmed as to any system irregularities relating to these SPS. The one scheme is performed by transmission line relays, which is monitored by transmission operators and the other scheme is monitored through various equipment failure alarms at the plant and by transmission operators. PGE performed regular maintenance and testing on the Protection System devices as part of PGE's Protection System Maintenance and Testing Program. Further, the first LAPS operated correctly on two separate occasions. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the TOPs, BA and GOPs on the modification made at the Port Westward and the Grand Ronde schemes, training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained protection engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPS and data for the Grand Ronde Remedial Action Scheme (RAS) to Remedial Action Scheme Reliability Subcommittee (RASRS) as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; 7) implemented the Grand Ronde test plan; 8) coordinated with neighboring TOPs and BA to insure full understanding of any potential impacts of the Grand Ronde SPS on their systems; and 9) revised procedures to address the notification of affected TOPs and BAs of each change in status of the Grand Ronde SPS. | 12/23/2013 | 2014-01-03 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011510 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it was in violation of PRC-015-0 R1. PGE did not identify two Local Area Protection Schemes (LAPS) as Special Protection Schemes (SPS) when PGE implemented the schemes. The two SPS in scope included the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and the Port Westward Generation Runback Scheme, in service on September 29, 2010. As a result, PGE did not maintain a list of and provide dates for its existing and proposed SPS as specified in PRC-013-0 R1. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-015-0 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE did not maintain a list and provide data for existing and proposed SPS as specified in PRC-013-0 R1. This increased the potential for a situation where PGE's operators and neighboring utilities were unaware of the systems thereby increasing the possibility that they would not properly respond to operations that occurred. The potential risks were minimized due to PGE's compensating measures. PGE routinely performed maintenance and testing on the Protection System devices on each SPS as part of PGE's Protection System Maintenance and Testing Program. Additionally, real time monitoring was in place for the individual relays located on the SPS. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the Transmission Operators (TOPs), Balancing Authority (BA), and Generator Operators on the modification made at the Port Westward and the Grand Ronde schemes, training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained Protection Engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPS and data for the Grand Ronde Remedial Action Scheme (RAS) to RASRS as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; and 7) implemented the Grand Ronde test plan. | 12/23/2013 | 1/3/2014 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011511 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it was in violation of PRC-015-0 R2. PGE failed to have evidence that it reviewed two new or functionally modified Local Area Protection Schemes (LAPS) as Special Protection Systems (SPS) in accordance with the Regional Reliability Organization's procedures as defined in PRC-012-0 R1 prior to being placed in service. The two SPS in scope included the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and the Port Westward Generation Runback Scheme, in service on September 29, 2010. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-015-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE failed to review two new or functionally modified SPS in accordance with proper procedures as specified in PRC-012-0 R1. Specifically, PGE put in service two SPS, one of which was capable of tripping a breaker which could in certain circumstances result in shedding up to 40 MW of load while the other would curtail generation up to 337 MW. PGE's failure created a situation where its SPS could not be certified as properly designed to meet performance requirements. As a result, PGE had less certainty that the systems would operate correctly when required. Furthermore, because the SPS were not properly reviewed, the SPS could have reacted but under improper circumstances or by providing too much or too little curtailment. However, PGE did actively monitor the relays associated with the SPS and did conduct routine maintenance and testing on the associated Protection System equipment as part of PGE's Protection System Maintenance and Testing Program. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the Transmission Operators (TOPs), Balancing Authority (BA), and Generator Operators on the modification made at the Port Westward and the Grand Ronde schemes, training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained protection engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPS and data for the Grand Ronde Remedial Action Scheme (RAS) to Remedial Action Scheme Reliability Subcommittee (RASRS) as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; and 7) implemented the Grand Ronde test plan. | 2013-12-23 | 2014-01-03 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011512 | Settlement Agreement | On December 13, 2012, PGE submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it was in violation of PRC-017-0 R1. PGE did not have a maintenance and testing program in place for two Special Protection Systems (SPS). PGE failed to identify two of its Local Area Protection Schemes (LAPS) as SPS. The two SPS in scope included the Grand Ronde 115 kV Load Shedding Scheme, in service on December 9, 2008 and the Port Westward Generation Runback Scheme, in service on September 29, 2010. PGE determined that while the component testing required by PRC-017-0 has been completed as part of the PRC-005 maintenance program, the requirements for system testing in R1.3, R1.4, R1.5 and R1.6 have not been fully met. The root cause of this violation was lack of compliance understanding that led to PGE's failure to recognize that it had two LAPS that met the NERC definition of SPS. Specifically, PGE had insufficient administrative controls in place to identify these LAPS per the definition. | PRC-017-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE failed to document a maintenance and testing program specific to its SPS. PGE’s failure created a situation where the devices used in the system protection may not have received required maintenance and testing. The risks described above, however, were limited due to PGE’s compensating measures in place during the pendency of the violation. PGE performed system testing upon commissioning the SPS, and was performing maintenance and testing on the Protection System devices associated with the SPS according to PGE’s Protection System Maintenance and Testing Program. No harm is known to have occurred. | 12/9/2008 (when PGE placed the first LAPS in service) | 12/23/2013 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) trained the Transmission Operators (TOPs), Balancing Authority (BA), and Generator Operators on the modification made at the Port Westward and the Grand Ronde schemes; training also covered the requirement for TOPs and BAs to monitor the status of the Grand Ronde SPS and notify affected TOPs and BAs of each change in status; 2) trained Protection Engineers on the definition of SPS to ensure that future schemes are properly identified and that appropriate action is taken to achieve compliance with applicable Standards; 3) disabled the Port Westward SPS and implemented a manual curtailment plan; 4) created and submitted a list of SPS and data for the Grand Ronde Remedial Action Scheme (RAS) to Remedial Action Scheme Reliability Subcommittee (RASRS) as specified in Reliability Standard PRC-013 R1; 5) presented the Grand Ronde RAS scheme to the RASRS; 6) developed a test plan and schedule for Grand Ronde scheme; and 7) implemented the Grand Ronde test plan. | 12/23/2013 | 2014-01-03 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2014013653 | Settlement Agreement | During a Compliance Audit conducted from February 18, 2014 through February 28, 2014, WECC determined that PGE, as a Balancing Authority (BA) and Transmission Operator (TOP), was in violation of PER-005-1 R1. Specifically, PGE’s list of Bulk Electric System (BES) company-specific reliability-related tasks did not include tasks that meet PGE’s definition of reliability-related tasks. PGE worked with a consulting firm and an additional third party consultant to create its list of reliability-related tasks performed by its system operators. PGE used a consulting firm's generic task list as a starting point to develop a customized task list for the BA and TOP positions and designated this list as its BES company-specific reliability-related tasks list. PGE’s list covered almost exclusively emergency and abnormal operations and did not include reliability-related tasks associated with normal operations. As a result, PGE failed to create a list of BES company-specific reliability-related tasks performed by its System Operators. The root cause of this violation was lack of compliance understanding that led to a list of tasks that did not meet the requirements of the Standard. | PER-005-1 | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, PGE created a list of reliability-related tasks that did not include tasks that met PGE’s definition of a reliability-related task. PGE’s list consists almost exclusively of emergency actions; it excludes a significant number of tasks whose performance would prevent threats to the reliable operation of the BPS. Additionally, the non-performance or improper performance of many of the tasks that were not included in PGE’s list could lead to a possible violation of a NERC Reliability Standard. Although additional tasks meeting PGE’s definition of reliability-related tasks should have been included in PGE’s list, PGE’s list includes some tasks that are related to emergency preparedness and response. The risk is further reduced because PGE does provide training to system operators for some tasks that are excluded from the PGE’s list of reliability-related tasks, such as transferring operations to the Backup Control Center. No harm is known to have occurred. | 4/1/2013 (when the Standard became mandatory and enforceable) | 2/2/2015 (Mitigation Plan completion) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Compliance Audit | To mitigate this violation, PGE: 1) conducted a systematic analysis of the complete BA operator and transmission and distribution operator task lists; 2) reclassified additional tasks as "Reliability Related Tasks (RRT) to accurately reflect the spirit and intent of PGE's RRT definition and the NERC-defined concept of "adequate level of reliability;" 3) submitted PGE's newly revised RRT lists to a WECC-designated subject matter expert for acknowledgment that PGE's mitigation efforts are on track; and 4) revised Operations Training Program to formally establish the Continuing Training Program format, structure, and periodicity requirements for required RRT refresher training. | 2/2/2015 | TBD | Neither Admits nor Denies | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2014013851 | Settlement Agreement | On May 16, 2014, PGE submitted a Self-Report stating that, as a Generator Operator, it was in violation of VAR-002-2b R3. On April 30, 2014, PGE upgraded its Distributed Control System at Coyote Springs. During the upgrade, PGE’s plant and vendor personnel tested the functionality of new operator screens. PGE reported that during the testing at 10:09 a.m., PGE inadvertently disabled the power system stabilizer (PSS) on the Unit 2 Steam Generator. Audio and visual alarms should have notified the operator that the PSS did not activate when the unit reached the activation threshold. However, a configuration error prevented the alarm from functioning. The configuration likely occurred during the alarm’s original programming and testing in 2013. The error was compounded by problems associated with the Distributed Control System upgrade that resulted in a number of false alarms reporting in rapid succession. On April 30, 2014 at 9:05 PM, the operator coming on shift noticed the issue during routine checks of the operating screens. The operator immediately notified the Balancing Authority/Transmission Operator (TOP) and enabled the PSS. The root cause of this violation was a lack of oversight, monitoring, or properly-configured alarms to alert operators when the PSS was disabled. | VAR-002-2b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGE failed to notify its associated TOP within thirty minutes of changes in status of the Reactive Power resources, and the expected duration of the change in status. Failure to notify the TOP of a change in status could result in the generator not reacting to system conditions such as voltage fluctuations. This could lead to the generator tripping and the potential loss of 116 MW of generation. However, PGE implemented detective controls. Specifically, PGE implements a procedure to review controls screens during shift changes. During the review, PGE can detect a status change of the reactive power resources and implement corrections if needed. In this instance, Automatic Voltage Regulator (AVR) was running on the generating unit in scope when the PSS was disabled. The AVR would not be able to compensate for high magnitude voltage fluctuations or short disturbances as quickly as PSS, but AVR would stabilize the voltage fluctuation to a certain extent. PGE also implemented compensating controls. PGE was following the TOP's voltage schedule and there was no voltage fluctuation while the PSS was disabled. If needed, PGE's operators closely monitor the voltage on the system and could have manually controlled the voltage if needed. Specifically, AVR and PSS were running on the other generating unit. As a result, any voltage fluctuation or instability would have been minimized by the other reactive power resources. No harm is known to have occurred. | 4/30/2014 (when PGE's PSS was disabled) | 4/30/2014 (when PGE notified its Transmission Operator that the PSS was disabled) | $97,000 (for WECC2012011513, WECC2012011514, WECC2012011515, WECC2012011510, WECC2012011511, WECC2012011512, WECC2014013653, and WECC2014013851) | Self-Report | To mitigate this violation, PGE: 1) repaired the malfunctioning alarm; 2) tested the three existing alarms; 3) added additional alarms to each of the four units. This alarm will alert the operator anytime the PSS is disabled, regardless of whether or not the unit is running; 4) established an annual preventative maintenance and work order to test all PSS alarms for each Coyote Springs generator; 5) trained all Coyote Springs operations personnel on the incident and the changes made to the alarms; and 6) added an additional field to SharePoint entry the operator completes to differentiate between when the Reactive Power resource status change occurred and when the change was discovered; 7) conducted annual test of all PSS and AVR alarms; and 8) removed PSS disable capability from the Distributed Control System control screen. | 7/17/2014 | 10/31/2014 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that PGE’s ICP is documented; the ICP is disseminated throughout its operations staff; PGE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the chief executive officer and/or board of directors; PGE operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; PGE has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; PGE reviews and modifies its ICP regularly; PGE’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and PGE’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. WECC considered PGE's VAR-002 R3 compliance history to be an aggravating factor in the penalty determination.