## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | AES Redondo Beach LLC (AESR) | NCR05007 | WECC2014013817 | Settlement Agreement | During a Compliance Audit conducted from May 8, 2014 through May 9, 2014, WECC determined that AESR, as a Generator Owner, was in violation of PRC-005-1 R1. From June 18, 2007 to September 22, 2010, AESR’s maintenance and testing program failed to include all Protection Systems that affect the bulk power system (BPS). During this time, AESR’s program focused on relays and did not include batteries, instrument transformers, clear intervals, or the basis for the intervals. On September 22, 2010, AESR updated its maintenance and testing program to include intervals, basis, and a summary of all devices contained in the program. However, the updated program omitted station batteries. On March 1, 2012, AESR implemented a new program that included station batteries. AESR’s current maintenance and testing program includes intervals, their basis, and a summary for all items, including batteries and battery chargers. The root cause of the violation was that AESR did not assure procedures and documents were of adequate quality and up-to-date. | PRC-005-1 | R1 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. From 2008 to 2012, AESR did not have a complete Protection System maintenance and testing program. During this time, AESR’s various maintenance and testing programs did include some Protection System devices maintenance and testing intervals. AESR updated the maintenance and testing program regularly with each update containing more information. AESR’s current maintenance and testing program is complete. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on AESR) | 3/1/2012 (when AESR updated its maintenance and testing program) | $0 (for WECC2014013817 and WECC2014013818) | Compliance Audit | To mitigate this violation, AESR: 1) added a battery maintenance and testing program to its Protection System maintenance and testing program; and 2) implemented the battery maintenance and testing program. | 3/1/2012 | 2/17/2015 | Agrees/Stipulates | As a non-monetary penalty, AESR agreed to complete and submit a 2015 Internal Compliance Program Assessment (ICPA) to WECC in order to settle this violation. WECC considered AESR's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | AES Redondo Beach LLC (AESR) | NCR05007 | WECC2014013818 | Settlement Agreement | During a Compliance Audit conducted from May 8, 2014 through May 9, 2014, WECC determined that AESR, as a Generator Owner, was in violation of PRC-005-1 R2. During the Audit, AESR failed to provide documentation of its Protection System maintenance and testing program for certain devices. For other devices, the records provided were incomplete. Specifically, AESR did not provide records to demonstrate maintenance and testing for the Unit 5 and Unit 6 batteries. AESR also did not provide complete records for the Unit 5 and Unit 7 trip tests. However, AESR did provide complete records for over 90% of the Protection System devices. The root cause of this violation was less than adequate testing. | PRC-005-1 | R2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AESR was unable to provide evidence that the Unit 5 and Unit 6 batteries were maintained and tested within defined intervals. AESR also failed to provide complete records for the Unit 5 and Unit 7 trip tests. The failure to include evidence that all Protection System devices were maintained and tested within defined intervals could have resulted in AESR’s devices failing to properly detect or respond to service failures. However, the potential impact was lessened given the limited scope of the violation. In total, AESR failed to provide evidence for 9% of the total number of Protection System devices. For the remaining 91%, AESR provided evidence of maintenance and testing as prescribed under AESR’s maintenance and testing program. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on AESR) | present | $0 (for WECC2014013817 and WECC2014013818) | Compliance Audit | To mitigate this violation, AESR will: 1) create a detailed scope of work for the contractor performing the testing so there will be no question as to the equipment to be tested and the procedures. The detailed scope of work will include the procedures from the current Protection System Maintenance and Testing Program; 2) measure output of instrument transformers at each associated relay terminal on Unit 5; 3) measure output of instrument transformers at each associated relay terminal on Unit 6; 4) measure output of instrument transformers at each associated relay terminal on Unit 7; and 5) measure output of instrument transformers at each associated relay terminal on Unit 8. | 12/31/2015 (approved completion date) . | TBD | Agrees/Stipulates | As a non-monetary penalty, AESR agreed to complete and submit a 2015 Internal Compliance Program Assessment (ICPA) to WECC in order to settle this violation. WECC considered AESR's compliance history and determined there were no relevant instances of noncompliance.