## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2013013269 | Settlement Agreement | During a Compliance Audit conducted from December 10, 2013, to December 12, 2013, SPP RE determined that Westar, as a Transmission Operator, was in violation of TOP-002-2.1b R11. Specifically, SPP RE found that Westar’s planned outage and real-time contingency analysis (RTCA) studies did not accurately reflect post-contingency System Operating Limits (SOLs) for seven multi-breaker, i.e., double breaker, ring bus, and breaker-and-a-half transmission facilities. Thus, Westar had not updated its Bulk Electric System (BES) studies as necessary to reflect current system conditions. Westar subsequently reviewed the facility ratings for 103 multi-breaker facilities. No changes to its BES studies were required for 92 of the multi-breaker facilities. Eleven of the multi-breaker facilities were de-rated under contingency conditions, requiring changes to Westar’s planned outage and RTCA study processes. The root cause of the violation was lack of oversight by Westar employees in the construction of Westar's planning and RTCA models. | TOP-002-2.1b | R11 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Westar was performing the required seasonal, next-day, and current-day BES studies, the results of these studies were inaccurate in identifying the correct SOLs for contingencies involving 11 of Westar’s 103 multi-breaker facilities. Six of the 11 transmission lines that were subsequently de-rated by Westar operate at 345 kV. The facility ratings for five of the 345 kV transmission lines that were de-rated were reduced by more than ten percent. The ratings for two of the 345 kV transmission lines, i.e., Benton – Wolf Creek and Rose Hill – Wolf Creek, are relevant to studies involving the operation of the Wolf Creek Generating Station, the largest generating unit in the SPP RE footprint. The Benton – Wolf Creek transmission line was de-rated by 20% and the Rose Hill – Wolf Creek transmission line was de-rated 15% under contingency conditions. The remaining five transmission lines that were de-rated under contingency conditions operate between 115 and 138 kV. No actual harm resulted from this violation. | 6/18/2007 (when the Standard became mandatory and enforceable) | 5/16/2014 (Mitigation Plan completion) | $44,000 (for SPP2013013269 and SPP2013013270) | Compliance Audit | To mitigate this violation, Westar: 1) modified its Facility Rating Methodology so that equipment rating on the substation side of the terminal shall be rated based on one breaker being open for multi-breaker configurations, and if there is a difference between the equipment ratings of the terminal equipment including in the multi-breaker configuration, then the lower rating would be used to determine the overall Facility Rating; 2) updated the Facility Rating spreadsheets with the seven locations affected by the modified Facility Rating Methodology; 2) reviewed the equipment rating for its 103 multi-breaker installations; 3) identified 11 multi-breaker installations that required modification; and 4) changed the ratings for these multi-breaker installations in the appropriate Planning and Operational models. | 5/16/2014 | 6/4/2014 | Neither Admits nor Denies | SPP RE reviewed Westar's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In 2010, Westar Energy established a comprehensive ICP to ensure compliance with the NERC Reliability Standards. In ensuring a strong culture of compliance, Westar requires the active involvement of senior management in the development, implementation, and monitoring of its ICP. Overall management of Westar’s ICP is vested in a Steering Committee, which is responsible for monitoring the status of the ICP; annually reviewing the program for effectiveness; encouraging compliance; and providing sufficient funding and resources. Additionally, the Steering Committee provides oversight to ensure violations are reported timely and remediated completely. The Steering Committee is made up of four Westar officers who individually are responsible for compliance, legal, regulatory and transmission operations. The Chief Audit Executive (CAE) serves as the chair of the Steering Committee. Westar’s Regulatory Compliance Committee is made up of employees who are directly and indirectly responsible for compliance with NERC Reliability Standards. The Committee meets on a monthly basis with the Steering Committee to discuss the status of the compliance efforts and communicate compliance issues or concerns. Westar’s Regulatory Department is responsible for the interpretation and communication of regulatory requirements. The Regulatory Department monitors the development of new and revised operating protocols and guidelines, and in coordination with the impacted departments, works to ensure compliance with regulatory requirements. Regulatory also leads the preparation for compliance audits, and with the Legal Department, interfaces directly with regulatory agencies on issues pertaining to reliability standards and compliance enforcement. The Director of NERC Compliance is responsible for coordinating, administering, and supporting all aspects of the Westar’s NERC compliance efforts. Westar’s “Corporate Compliance and Internal Audit” is responsible for independently evaluating Westar’s compliance with the NERC Reliability Standards. Corporate Compliance and Internal Audit also works closely with assigned personnel to collect compliance evidence, identify compliance gaps, and maintain compliance documentation. Corporate Compliance and Internal Audit facilitates Westar’s self-assessments to measure compliance with the NERC Reliability Standards. A self-evaluation is performed annually to verify continued compliance. Within Westar, various operational areas are responsible for the day-to-day responsibility of operating reliably and ensuring compliance with the NERC Reliability Standards. These operational areas include: Transmission, Generation, Bulk Power Marketing, Substation Engineering and Maintenance, Distribution Power Delivery, Information Technology, Accounting, Finance, Human Resources, Customer and Community Relations, and Strategy and Support. Westar Energy has implemented training programs in support of its ICP. These training programs emphasize that compliance with regulatory requirements is mandatory and a priority and that Westar does not tolerate retaliation for good faith reports of any complaints or concerns regarding potential or actual compliance issues. Training requirements are monitored to ensure all employees receive necessary training. Employees that are part of the compliance effort meet regularly to review regulatory requirements. Westar has established a regulatory compliance database to document compliance with regulatory requirements. The database also includes the compliance program guidelines to ensure information is widely distributed. Access to the database and training are provided to ensure employees understand their responsibilities for compliance. Additionally, Westar has set up an integrity hotline to report complaints or concerns regarding compliance. An independent third party manages the hotline. Complaints and concerns can be made anonymously and are routed to Corporate Compliance and Internal Audit for review and investigation. Finally, compliance with regulatory requirements is incorporated into employee goals to ensure compliance is a top priority. A company-wide disciplinary policy (Human Resources Policy Manual – Policy to Effect Constructive Corrective Action) is followed to address violations. SPP RE considered Westar's compliance history and determined there were no relevant prior instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2013013270 | Settlement Agreement | During a Compliance Audit conducted from December 10, 2013, to December 12, 2013, SPP RE determined that Westar, as a Balancing Authority and Transmission Operator, was in violation of TOP-002-2.1b R10. Westar failed to plan to meet all System Operating Limits (SOLs). In its Supervisory Control and Data Acquisition (SCADA)/Energy Management System (EMS), Westar utilizes the Summer Emergency Rating of its non-power transformer transmission facilities as the High Alarm Limit set point. A value equal to 90 percent of the High Alarm Limit is utilized as the High Warning Limit set point. No other alarm set points are utilized by Westar in its SCADA/EMS for monitoring transmission line flow. In a sampling of 29 Westar transmission lines, SPP RE discovered that the SCADA/EMS High Warning Limit set point was above the Normal Rating for 7 transmission lines. Thus, these transmission lines could be operated for an indefinite period above their Normal Rating without the Westar SCADA/EMS generating an alarm. Because Westar could potentially operate these transmission lines above their Normal Rating before a SCADA/EMS alarm was generated, SPP RE found that Westar was not planning to meet all of its SOLs. Subsequent to the Audit, Westar examined the alarm set points for 361 transmission line sections. The High Warning Limit set points for 60 of the transmission line sections were found to be above the Normal Rating, requiring a change to 132 SCADA/EMS MVA and amp High Warning Limit set points. The root cause of the violation was lack of oversight by Westar employees in establishing the Westar SCADA/EMS alarm set points. | TOP-002-2.1b | R10 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Setting the SCADA/EMS MVA and amp High Warning set points for a transmission line above the transmission line’s Normal Rating could affect a system operator’s awareness of an impending transmission line overload. This potential delay in situational awareness could cause system operators to respond inappropriately or fail to respond to such a condition. The risk associated with this violation is mitigated by the High Warning Limit and High Alarm Limit set points in Westar’s SCADA/EMS. Furthermore, Westar’s Summer Emergency Rating, the set point for the High Alarm Limit, is a four-hour rating. Notwithstanding Westar’s failure to implement an alarm set point at or below the Normal Rating for 60 of its transmission line segments, Westar’s system operators would have received an alarm if the overload condition was greater than ninety percent of the Summer Emergency Rating. Depending upon system conditions, the affected transmission line segments could have operated for an indefinite period of time above the Normal Rating but below 90 percent of the Summer Emergency Rating. It is unlikely that a serious overload condition would have continued on the affected transmission line segments before an alarm was generated or other SCADA/EMS alarms made system operators aware of the overload condition. No actual harm resulted from this violation. | 9/6/2013 (the date Westar implemented the September 6, 2013 version of its Facility Rating Methodology) | 5/20/2014 (Mitigation plan completion) | $44,000 (for SPP2013013269 and SPP2013013270) | Compliance Audit | To mitigate this violation, Westar: 1) examined the alarm set points for 361 transmission line sections; 2) changed the Facility Rating Methodology to adapt the approach so that the EMS High Warning Limit will be set equal to the Normal Rating of Facilities. However, in those cases where the Emergency and Normal Ratings of a Facility are equal, the EMS High Warning Limit will be set to 90 percent of the EMS High Alarm Limit. In all cases the EMS High Alarm Limit is set equal to the Emergency Rating of the Facility; 3) changed 132 SCADA/EMS MVA and amp alarm set points; and 4) set the SCACA/EMS High Warning Limit equal to the Normal Rating of Facilities for those facilities with Normal Ratings below 90% of the High Alarm Limit. | 5/20/2014 | 5/28/2014 | Neither Admits nor Denies | SPP RE reviewed Westar's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In 2010, Westar Energy established a comprehensive ICP to ensure compliance with the NERC Reliability Standards. In ensuring a strong culture of compliance, Westar requires the active involvement of senior management in the development, implementation, and monitoring of its ICP. Overall management of Westar’s ICP is vested in a Steering Committee, which is responsible for monitoring the status of the ICP; annually reviewing the program for effectiveness; encouraging compliance; and providing sufficient funding and resources. Additionally, the Steering Committee provides oversight to ensure violations are reported timely and remediated completely. The Steering Committee is made up of four Westar officers who individually are responsible for compliance, legal, regulatory and transmission operations. The Chief Audit Executive (CAE) serves as the chair of the Steering Committee. Westar’s Regulatory Compliance Committee is made up of employees who are directly and indirectly responsible for compliance with NERC Reliability Standards. The Committee meets on a monthly basis with the Steering Committee to discuss the status of the compliance efforts and communicate compliance issues or concerns. Westar’s Regulatory Department is responsible for the interpretation and communication of regulatory requirements. The Regulatory Department monitors the development of new and revised operating protocols and guidelines, and in coordination with the impacted departments, works to ensure compliance with regulatory requirements. Regulatory also leads the preparation for compliance audits, and with the Legal Department, interfaces directly with regulatory agencies on issues pertaining to reliability standards and compliance enforcement. The Director of NERC Compliance is responsible for coordinating, administering, and supporting all aspects of the Westar’s NERC compliance efforts. Westar’s “Corporate Compliance and Internal Audit” is responsible for independently evaluating Westar’s compliance with the NERC Reliability Standards. Corporate Compliance and Internal Audit also works closely with assigned personnel to collect compliance evidence, identify compliance gaps, and maintain compliance documentation. Corporate Compliance and Internal Audit facilitates Westar’s self-assessments to measure compliance with the NERC Reliability Standards. A self-evaluation is performed annually to verify continued compliance. Within Westar, various operational areas are responsible for the day-to-day responsibility of operating reliably and ensuring compliance with the NERC Reliability Standards. These operational areas include: Transmission, Generation, Bulk Power Marketing, Substation Engineering and Maintenance, Distribution Power Delivery, Information Technology, Accounting, Finance, Human Resources, Customer and Community Relations, and Strategy and Support. Westar Energy has implemented training programs in support of its ICP. These training programs emphasize that compliance with regulatory requirements is mandatory and a priority and that Westar does not tolerate retaliation for good faith reports of any complaints or concerns regarding potential or actual compliance issues. Training requirements are monitored to ensure all employees receive necessary training. Employees that are part of the compliance effort meet regularly to review regulatory requirements. Westar has established a regulatory compliance database to document compliance with regulatory requirements. The database also includes the compliance program guidelines to ensure information is widely distributed. Access to the database and training are provided to ensure employees understand their responsibilities for compliance. Additionally, Westar has set up an integrity hotline to report complaints or concerns regarding compliance. An independent third party manages the hotline. Complaints and concerns can be made anonymously and are routed to Corporate Compliance and Internal Audit for review and investigation. Finally, compliance with regulatory requirements is incorporated into employee goals to ensure compliance is a top priority. A company-wide disciplinary policy (Human Resources Policy Manual – Policy to Effect Constructive Corrective Action) is followed to address violations. SPP RE considered Westar's compliance history and determined there were no relevant prior instances of noncompliance.