## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200800784 | Settlement Agreement | On April 9, 2008, NNSAL submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner (TO), it was in violation of PRC-005-1 R1. This violation was discovered on March 17, 2008 as a result of a self-evaluation performed by NNSAL. At the time of its Self-Report filing, NNSAL did not have a Protection System maintenance and testing program in place. Because NNSAL did not have a maintenance and testing program, it did not have maintenance and testing intervals and their basis or a summary of those procedures as required by the Standard. WECC reviewed NNSAL’s Self-Report and confirmed that NNSAL had a violation of PRC-005-1, because it did not have maintenance and testing program in place. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 8/10/2007 (when NNSAL was registered as a TO and the Standard became mandatory and enforceable on NNSAL) | 2/22/2010 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Report | To mitigate this violation, NNSAL: 1) checked inventory records against installed transmission and generation Protection System devices to ensure completeness; 2) performed review of transmission and generation Protection System devices and systems to ensure they are maintained and tested within defined intervals; 4) reviewed maintenance and testing methods to ensure all transmission and generation Protection System devices and systems are maintained and tested in accordance with manufacturers' instructions and internal procedures, developing or revising procedures as needed; 5) ensured retention of records showing Protection System devices are maintained and tested within defined intervals, the procedure will include record format and retention method; and 6) ensured the ability to provide Protection System device maintenance and testing records to WECC within 30 days of request. | 2010-02-22 | 2010-03-03 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200800887 | Settlement Agreement | On July 1, 2008, NNSAL submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of PER-002-0 R1. In the Self-Report, NNSAL reported that its NNSAL Power Dispatcher Training Plan would not result in adequately trained operating personnel in staffed positions. The Self-Report also indicated that NNSAL’s training plan did not contain any of the four defined training objectives specified in R3.1, R3.2, R3.3 and R3.4. Finally, the training plan called for less than two days per year of system emergency training, which does not meet the five-day standard required in R4. WECC confirmed that NNSAL had violations of PER-002, because it had failed to address the requirements of R1, R3, and R4 in either documentation or practice. | PER-002-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 3/27/2010 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Report | To mitigate this violation, NNSAL: 1) revised Power Dispatcher training program to include: (a) a set of defined training objectives based on NERC and WECC standards and NNSAL operating procedures; (b) Initial and continuing training addressing knowledge and competencies for reliable system operations; (c) Define training time to ensure operating proficiency; (d) Training staff identification and competencies in knowledge of system operations and instructional capabilities; and (e) Provide at least five days of training and drills using realistic simulations of system emergencies; 2) reviewed the training program; 3) approved the revised training program; and 4) secured NNSA's concurrence, implemented position description, and provided WECC evidence supporting compliance. | 2010-03-27 | 2011-04-08 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200800889 | Settlement Agreement | On July 1, 2008, NNSAL submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of PER-002-0 R1. In the Self-Report, NNSAL reported that its NNSAL Power Dispatcher Training Plan would not result in adequately trained operating personnel in staffed positions. The Self-Report also indicated that NNSAL’s training plan did not contain any of the four defined training objectives specified in R3.1, R3.2, R3.3 and R3.4. Finally, the training plan called for less than two days per year of system emergency training, which does not meet the five-day standard required in R4. WECC confirmed that NNSAL had violations of PER-002, because it had failed to address the requirements of R1, R3, and R4 in either documentation or practice. | PER-002-0 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 3/27/2010 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Report | To mitigate this violation, NNSAL: 1) revised Power Dispatcher training program to include: (a) a set of defined training objectives based on NERC and WECC standards and NNSAL operating procedures; (b) Initial and continuing training addressing knowledge and competencies for reliable system operations; (c) Define training time to ensure operating proficiency; (d) Training staff identification and competencies in knowledge of system operations and instructional capabilities; and (e) Provide at least five days of training and drills using realistic simulations of system emergencies; 2) reviewed the training program; 3) approved the revised training program; and 4) secured NNSA's concurrence, implemented position description, and provided WECC evidence supporting compliance. | 2010-03-27 | 2011-04-08 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200800890 | Settlement Agreement | On July 1, 2008, NNSAL submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of PER-002-0 R1. In the Self-Report, NNSAL reported that its NNSAL Power Dispatcher Training Plan would not result in adequately trained operating personnel in staffed positions. The Self-Report also indicated that NNSAL’s training plan did not contain any of the four defined training objectives specified in R3.1, R3.2, R3.3 and R3.4. Finally, the training plan called for less than two days per year of system emergency training, which does not meet the five-day standard required in R4. WECC confirmed that NNSAL had violations of PER-002, because it had failed to address the requirements of R1, R3, and R4 in either documentation or practice. | PER-002-0 | R4 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 3/27/2010 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Report | To mitigate this violation, NNSAL: 1) ensured its TOP operations will be staffed with adequately trained operating personnel; 2) developed a set of defined training objectives based on NERC and WECC Standards and NNSAL operating procedures; 3) defined training timelines, identified training staff and specified training dates for existing staff; 4) provided at least five days of training and drills using realistic simulations of system emergencies; 5) reviewed and approved revised training program; 6) implemented position descriptions and provided WECC with evidence supporting completion; 7) had transmission system operators transfer operations from primary control room to back up control room and operate from backup control room; and 8) completed the transmission simulation training. | 2010-03-27 | 2011-04-15 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200800891 | Settlement Agreement | On July 1, 2008, NNSAL submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of PER-003-0 R1. The violation was discovered as a result of an internal review following NNSAL’s May 14, 2008 registration as a TOP. In the Self-Report submission filing, NNSAL indicated that its NNSAL Power Dispatcher Training Plan did not contain the NERC System Operator Certification and continuing education requirements. Since the Standard requires all operating positions to have this training, NNSAL staff could not be NERC-certified. WECC confirmed that NNSAL had a violation of PER-003-0 R1, because it failed to require NERC-certified personnel for the positions addressed by this Standard. | PER-003-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 9/30/2010 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Report | To mitigate this violation, NNSAL: 1) placed system operation certification and TOP certification requirements and continuing education requirements in its training program; and 2) trained, tested, and certified operating personnel to be compliant with the Standard. | 2010-09-30 | 2011-04-06 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801160 | Settlement Agreement | On February 4, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-008-0 R1. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. At the time of the Self-Certification filing, NNSAL did not have a documented process to continue reliability operations if its control center is rendered inoperable. WECC confirmed that NNSAL had a violation of EOP-008-0 R1, because it did not have a plan to continue operations in the event of a loss of its control center. | EOP-008-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due to the lack of an appropriate plan for loss of control center functionality. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 9/4/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL: 1) interviewed dispatchers and linemen with regards to their knowledge of what to do in case the power dispatch control center is out of service; 2) gathered and reviewed all existing instructions and procedures that currently serve as instructions to dispatchers and linemen during emergency loss of power dispatch control center functionality; 3) wrote a contingency plan in accordance with the Standard utilizing applicable existing instructions, procedures, and practices; 4) issued contingency plan for review and approval and distributed it to dispatchers and linemen; and 5) scheduled an exercise of the contingency plan; 6) finalized plan with incorporated county of Los Alamos to continue reliable operations in the event NNSAL's control center becomes inoperative; 7) approved the revised procedure; and 8) secured NNSA's concurrence, implemented procedure, and provided WECC evidence of completion. | 2008-09-04 | 2008-09-29 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801229 | Settlement Agreement | On January 9, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-001-0 R3. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. NNSAL stated in its compliance Self-Certification documentation that it did not have the appropriate plans to mitigate operating emergencies, as required by the Standard. WECC confirmed that NNSAL had a violation of EOP-001 R3, because it had failed to develop, maintain, and implement the appropriate emergency plans as required by R3.1, R3.2, R3.3 & R3.4. | EOP-001-0 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due to the lack of an appropriate recovery plan. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 8/15/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL developed a comprehensive emergency operations plan for NNSAL operations. These documents give NNSAL staff specific instructions for mitigating operations, emergency load shedding, and system restoration. | 2008-08-15 | 2008-09-18 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801230 | Settlement Agreement | On January 9, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-001-0 R4. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. NNSAL stated in its compliance Self-Certification documentation that it did not have the appropriate emergency plans to be compliant with the Standard. WECC confirmed that NNSAL had a violation of EOP-001 R4, because it failed to have the appropriate emergency plans that will enable it to mitigate operating emergencies. | EOP-001-0 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due tp the lack of an appropriate recovery plan. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 8/15/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL developed a comprehensive emergency operations plan for NNSAL operations. These documents give NNSAL operating personnel specific instructions to follow during the loss of individual telecommunications facilities. | 2008-08-15 | 2008-09-18 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801231 | Settlement Agreement | On January 9, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-001-0 R5. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. NNSAL stated in its compliance Self-Certification documentation that it did not have the appropriate emergency plans to be compliant with the Standard. Because it did not have an emergency plan, the applicable elements could not be included in the plan as required by the Standard. WECC confirmed that NNSAL had a violation of EOP-001 R5, because it was unable to include the applicable elements in Attachment 1-EOP-001-0. | EOP-001-0 | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due to the lack of an appropriate recovery plan. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 8/15/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL developed a comprehensive emergency operations plan for NNSAL operations. These documents include each of the applicable elements in Attachment 1-EOP-001-0 within the emergency operations plan. | 2008-08-15 | 2008-09-18 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801232 | Settlement Agreement | On January 9, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-001-0 R6. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. NNSAL stated in its compliance Self-Certification documentation that it did not have the appropriate emergency plans to be compliant with the Standard. Because it did not have an emergency plan, it could not have conducted an annual review and update of its emergency plans, nor could it provide a copy of its updated plans to its neighboring entities as required by the Standard. WECC confirmed that NNSAL had a violation of EOP-001 R6, because NNSAL did not have the required emergency plans. Therefore, it could not review and update these emergency plans as required by the Standard or provide them to the appropriate entities. | EOP-001-0 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due to the lack of an appropriate recovery plan. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 8/15/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL developed a comprehensive emergency operations plan for NNSAL operations. These documents included a schedule for annual reviews and updates of the plan and a requirement to provide neighboring entities with a copy of the updated plans. | 2008-08-15 | 2008-09-18 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200801234 | Settlement Agreement | On January 9, 2008, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of EOP-001-0 R7. NNSAL responded to the Self-Certification request as a TOP even though it was not registered on the NERC Compliance Registry as a TOP at that time. WECC has determined that although NNSAL was not registered as a TOP when it self-certified this violation, this is an enforceable violation as of May 14, 2008 when NNSAL registered as a TOP. NNSAL stated in its compliance Self-Certification documentation that it did not have the appropriate emergency plans to be compliant with the Standard. Because it did not have an emergency plan, it could not have coordinated its emergency plans with other TOPs and Balancing Authorities (BAs) as required by the Standard. WECC confirmed that NNSAL had a violation of EOP-001 R7, because it failed to coordinate its emergency plans with other TOPs and BAs. | EOP-001-0 | R7 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Any unanticipated emergency could potentially isolate components of the NNSAL transmission system from the interconnection due to the lack of an appropriate recovery plan. However, NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 8/15/2008 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL developed a comprehensive emergency operations plan for NNSAL operations. These documents include processes for coordinating NNSAL’s emergency plans with other TOPs and BAs. | 2008-08-15 | 2008-09-18 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC200901268 | Settlement Agreement | On January 7, 2009, NNSAL submitted a Self-Certification stating that, as a Transmission Operator (TOP), it was in violation of VAR-001-1 R1. At the time of the Self-Certification, NNSAL was using its Balancing Authority (BA’s) guidelines for controlling voltage levels. NNSAL did not develop, maintain, and implement a formal policy for monitoring and controlling voltage levels and Mvar flows between its service area and its BA’s service area as required by the Standard. Since the Standard requires the operator to have its own policies and procedures for monitoring and controlling voltage levels and Mvar flows within its individual areas and with the areas of neighboring TOPs, NNSAL Self-Certified a possible violation of this Standard. WECC confirmed that NNSAL had a violation of VAR-001-1 R1, because it did not have the appropriate policies and procedures in place for monitoring and controlling voltage levels and Mvar flows to be compliant with this Standard. | VAR-001-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s connection to the BPS is limited to 115 kV, it is located in a remote part of New Mexico, and no harm is known to have occurred. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 1/6/2009 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL issued a standing order to provide its power dispatchers direction for monitoring and controlling voltage levels and Mvar flows within its service area. NNSAL provided a copy of the standing order to its Power Operations Personnel detailing the provisions of the order, as well as signatures from both the originators of the order as well as the recipients of the order. | 2009-01-06 | 2009-01-15 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC201102415 | Settlement Agreement | On February 18, 2011, NNSAL submitted a Self-Certification stating that, as a Generator Owner, Distribution Provider, and Transmission Owner (TO), it was in violation of PRC-005-1 R2. NNSAL’s Protection System Maintenance and Testing Program requires its battery banks to be inspected on a monthly basis. On March 14, 2011, NNSAL reported that 4 monthly battery tests were inadvertently cancelled for the month of September 2010. Originally, NNSAL had reported 2 battery cancellations, but upon further review of its program, NNSAL expanded the scope of the possible violation to include 2 additional batteries missed due to inadvertently cancelling the monthly maintenance and testing. On March 15, 2011, WECC reviewed NNSAL’s Self-Certification and determined that NNSAL reported a possible violation of PRC-005-1, R2 because it could not provide evidence of maintenance and testing within defined intervals for all of its Protection System devices. WECC reviewed NNSAL’s battery maintenance and testing documentation and determined that it was missing four battery inspections in September 2010 at four locations In addition to the batteries, NNSAL failed to include the 3 voltage and current sensing devices and 4 relays in its maintenance and testing program, therefore NNSAL could not provide evidence NNSAL maintained and tested these devices within defined intervals. WECC determined NNSAL’s failure to test and maintain 4 batteries, 4 relays, and 3 current sensing devices within defined intervals is a violation of PRC-005-1 R2, specifically R2.1. The cause was lack of compliance understanding and human error. The battery inspections were erroneously cancelled and NNSAL believed the bus bay protective systems was adequate protection for the bulk power system (BPS). | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. NNSAL’s system consists of a single 115 kV connection to the BPS in a remote part of New Mexico that has limited ability to disrupt the BPS. Although NNSAL missed four battery inspections in September 2010, NNSAL conducted its August 2010 and October 2010 inspections. Further, NNSAL confirmed the batteries were operating correctly in the October inspection. Finally, the missing testing and maintenance documentation relates to the same percentage of relays not included in the Program, 5.6%, and the percentage of voltage and current sensing devices not included in the Program, 6.9%. Therefore, the violation is limited to a small portion of NNSAL’s Protection System. | 8/10/2007 (when NNSAL registered as a TO and the Standard became mandatory and enforceable on NNSAL) | 4/28/2011 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL: 1) placed statement on all monthly and quarterly battery bank inspections generated from Passport Maintenance System stating that the tasks are required and not to postpone or cancel; 2) tested protective systems on the NNSAL generator; and 3) completed the NNSAL Static Var Compensator protective systems testing and maintenance. | 2011-04-28 | 2011-07-11 | Agrees/Stipulates | WECC considered NNSAL’s PRC-005-1 R2 compliance history in determining the disposition track. NNSAL’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID WECC200700190. WECC considered NNSAL’s PRC-005-1 R2 compliance history to be an aggravating factor in the disposition of the violation.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC201102421 | Settlement Agreement | On February 14, 2011, NNSAL submitted a Self-Certification stating that, as a Generator Operator and Transmission Operator (TOP), it was in violation of PRC-001-1 R2. Specifically, NNSAL failed to report two malfunctions of its Under Frequency Load Shedding (UFLS) program’s equipment to its Balancing Authority (BA), nor to its Reliability Coordinator (RC), as required by this Standard. The first event occurred on May 14, 2008, during the period from NNSAL’s registration until October 7, 2008, when the UFLS devices were repaired, tested, and functional after the completion of a PRC-008-0 violation mitigation plan. The second malfunction was discovered during an internal check of the UFLS program equipment on December 23, 2010. NNSAL notified the BA, on February 1, 2011, that the UFLS equipment was out of service. NNSAL repaired and placed its UFLS equipment back into service on February 3, 2011. WECC determined that NNSAL was in violation of PRC-001-1 R2.2 because it failed to timely notify its BA and RC of two instances when its UFLS was non-operational. NNSAL notes that after it discovered the December 2010 UFLS malfunction, NNSAL contacted WECC for clarification on reporting procedures with respect to UFLS equipment failures. In response, WECC referred NNSAL to Requirement 2 of PRC-001-1. Consequently, on February 1, 2011, NNSAL notified its BA and the RC of the two occasions in which NNSAL’s UFLS program equipment was non-operational. NNSAL had protective relay or equipment failures that reduced system reliability, and NNSAL failed to notify its affected BA and RC. Thus, WECC determined NNSAL had a violation of PRC-001-1 R2, specifically R2.2. | PRC-001-1 | R2 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL’s system consists of a single 115 kV connection to the BPS in a remote part of New Mexico with limited ability to disrupt the BPS. NNSAL’s UFLS program has six UFLS devices that monitor the frequency of the system with a Process Logic Controller (PLC). The PLC is assigned to signal the circuit breakers to be tripped should a frequency excursion occur. | 5/14/2008 (when NNSAL was registered as a TOP and the Standard became mandatory and enforceable on NNSAL) | 2/3/2011 (when NNSAL had notified the BA and repaired and placed its UFLS equipment back into service) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL: 1) notified the BA and RC that the UFLS equipment was out of service; and 2) repaired and placed its UFLS equipment back into service; and 3) submitted a standing order that requires notification of its protective systems failures affecting system reliability. | 2011-02-17 | 2011-04-05 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC201102801 | Settlement Agreement | On February 14, 2011, NNSAL submitted a Self-Certification stating that, as a Generator Owner, Distribution Provider, and Transmission Owner, it was in violation of PRC-005-1 R1. Specifically, an internal review of NNSAL’s Protection System Maintenance and Testing Program revealed that not all protection devices were included in NNSAL’s program. NNSAL failed to include its Static Var Compensator (SVC) and Generator protective systems in its PRC-005 Protection System Maintenance and Testing program. Specifically, NNSAL reported that it had failed to include its generator and SVC relays in the corrective actions of a previous mitigation plan completed in March 2010. When NNSAL was assessing the adequacy of its previous mitigation plan, NNSAL did not, at that time, include the protective relays associated with the 115 kV bus to which the SVC is connected or the protective devices associated with the generator. At the time, NNSAL stated it believed the bus and generator bay protective systems were adequate protection systems for the bulk electric system. NNSAL later discovered that it should have included the SVC and generator protective relays in its Protection System Maintenance and Testing program. On March 17, 2011, WECC determined that NNSAL’s Maintenance and Testing Program did not sufficiently summarize the maintenance and testing procedures for its SVC and Generator protective systems. Further, WECC determined that as a result of NNSAL not adequately summarizing its protection systems, four relays and three voltage and current sensing devices were not included in NNSAL’s Maintenance and Testing Program. WECC determined NNSAL’s failure to include the SVC and generator protective system for a 115 kV bus, four relay devices and three voltage and current sensing devices in its Protection System Maintenance and Testing Program is a violation of PRC-005-1 R1, including R1.1 and R1.2. The cause was lack of compliance understanding. NNSAL believed the bus bay protective systems was adequate protection for the bulk power system (BPS). | PRC-005-1 | R1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. NNSAL’s system consists of a single 115 kV connection to the BPS in a remote part of New Mexico that has limited ability to disrupt the BPS. By not including the SVC and Generator protection systems, NNSAL discovered that it had 4 relays and 3 current sensing devices not included in its Testing and Maintenance Program. The percentage of relays not included in the Program is 5.6 % and the percentage of Voltage and Current sensing devices not included in the Program is 6.9 %. Therefore, the violation is limited to a small portion of NNSAL’s Protection System. Further, since the discovery, one relay and two sensing devices for the generator have been maintained and tested. | 8/10/2007 (when NNSAL registered as a Transmission Owner and the Standard became mandatory and enforceable on NNSAL) | 4/29/2011 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Self-Certification | To mitigate this violation, NNSAL: 1) tested the protective systems on the NNSAL generator; 2) performed the NNSAL SVC protective systems testing and maintenance; and 3) placed the SVC and generator protective systems in the NNSAL maintenance program. | 2011-04-29 | 2011-07-11 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | National Nuclear Security Administration - Los Alamos National Laboratory (NNSAL) | NCR05515 | WECC2014013661 | Settlement Agreement | During a Compliance Audit conducted from March 3, 2014 through March 14, 2014, WECC determined that NNSAL, as a Transmission Operator (TOP), was in violation of EOP-008-1 R6. WECC determined that a single server in NNSAL’s Central Processing Unit (CPU) room supports NNSAL’s supervisory control and data acquisition (SCADA) system for both NNSAL’s Primary Control Center (PCC) and its Backup Control Center (BUCC). As such, if an event were to render the CPU nonfunctional, both the PCC and the BUCC would be rendered nonfunctional as well. WECC reviewed NNSAL’s “Loss of Primary Power Control Center Functionality,” which states that SCADA data are routed through the building housing the PCC. During the inspection, WECC confirmed that the CPU Room is in such proximity to the PCC that in a catastrophic event, if the building which houses the PCC was rendered nonfunctional, it would most likely also adversely affect the CPU Room, thereby affecting the BUCC. NNSAL currently uses a desktop application called the “Metering Program,” which is on a separate telecommunications Ethernet link and is independent from the PCC. While the “Metering Program” has a full spectrum of capabilities allowing for visibility of NNSAL’s system in the event SCADA is inoperative, NNSAL would still require sending personnel to up to five stations and would need to rely on voice communication to maintain system control. As such, the “Metering Program” does not fully function as a BUCC. WECC determined that NNSAL has a violation of EOP-008-1 R6 for failing to have primary and backup control centers that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | EOP-008-1 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NNSAL failed to have a fully redundant BUCC as required by EOP-008-1 R6. Not having fully redundant systems places risk on NNSAL’s adjacent TOP and Balancing Authority (BA). An unscheduled outage of NNSAL’s Static Var Compensator (SVC) (200 MW) has the potential of reducing the path rating of Path 48 in the event that the BA is unable to bring local generation online for Var support. The loss of SCADA at NNSAL’s BUCC could also inhibit NNSAL’s ability to respond to requests by the adjacent TOP to raise or lower the output of NNSAL’s SVC. NNSAL has only one source of SCADA for both its PCC and BUCC. However, if NNSAL loses the SCADA at its BUCC, whether caused by a failure of the CPU or through failure of the BUCC, NNSAL has additional procedures in place to ensure continued operations of its system. This includes staffing its five substations and relying on its “Metering Program” for system visibility and voice communication from NNSAL’s power dispatcher. | 7/1/2013 (when the Standard became effective) | 7/16/2015 (Mitigation Plan completion) | No penalty (for WECC200800784, WECC200800887, WECC200800889, WECC200800890, WECC200800891, WECC200801160, WECC200801229, WECC200801230, WECC200801231, WECC200801232, WECC200801234, WECC200901268, WECC201102415, WECC201102421, WECC201102801, and WECC2014013661) | Audit | To mitigate this violation, NNSAL: 1) determined the modification that will remove remote terminal unit (RTU) communication terminations from the PCC CPU and relocated them such that the terminations and cabling are removed from the building housing the PCC and routed to both the PCC and BUCC such that the loss of the PCC or BUCC will not render the other control center nonfunctional; 2) designed the solution and developed a bill of materials; 3) ordered material necessary to complete project installation; 4) received material and initiated field project installation; and 5) completed the project by programming CPUs to allow modifications to be functional, tested the modification, and turned it over to operations. | 2015-07-16 | 2015-11-20 | Agrees/Stipulates | WECC considered NNSAL compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | WECC2014014455 | Notice of Confirmed Violation | On November 17, 2014, VEA submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of EOP-008-1 R6. VEA failed to have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. On January 13, 2014, VEA had an event involving the complete loss of Bulk Electric System (BES) monitoring capabilities. The loss began at 10:26 am and concluded at 12:28 pm, a duration of two hours and two minutes. Following the event, VEA participated in the Event Analysis process and submitted a brief report to a WECC Events Analysis Team. WECC determined that when VEA introduced an Automatic Vehicle Location (AVL) system to the VEA corporate LAN, VEA had a complete loss of monitoring capability. VEA had a primary and backup functionality that depended on each other for the control center functionality required to maintain compliance with Reliability Standards. The network communications from the AVL system affected the corporate LAN switch infrastructure by disabling the Virtual Local Area Network (VLAN) configurations. This VLAN interruption affected the Supervisory Control and Data Acquisition (SCADA) system because the substation communications traffic was routed through the corporate network. The VLAN interruption caused a disconnect of the Virtual Private Network (VPN) between the substation communications firewall and the SCADA firewall. WECC determined VEA is in violation of EOP-008-1 R6 for failing to have a Primary Control Center (PCC) and Back Up Control Center (BUCC) that do not depend on each other for the control center functionality required to maintain compliance with the Standard. The root cause of the violation is VEA's lack of compliance understanding, leading to a less than adequate control center functionality. | EOP-008-1 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, VEA failed to have primary and backup control centers that did not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. VEA is a Transmission Owner (TO) and TOP of systems and facilities rated at 138 kV and above. VEA’s peak summer load in 2011 was 125 MW and winter peaks are nearly as high. Failing to have fully redundant systems places risk on VEA’s neighboring TOs and its Reliability Coordinators (RCs). Such burdens include but are not limited to requests for operational/visibility assistance from neighboring TOPs, coordination and communication with the RC, coordination and communication with the TOP’s Balancing Authority, and dependence on external entities for monitoring local System Operating Limit parameters. As compensating measures, VEA had procedures in place to manually monitor during the outage. Ability to monitor was coordinated with the California ISO and Peak Reliability. VEA substation personnel were deployed to VEA’s major substation (Pahrump) to monitor the BES and continued operation of its system. | 7/1/2013 (when the Standard became mandatory and enforceable on VEA) | 3/1/2014 (when the primary and backup systems were separated) | $0 (for WECC2014014455) | Self-Report | To mitigate this violation, VEA; 1) changed the network configuration to eliminate the traffic flow through the corporate network, routing SCADA traffic directly from the substation communications firewall to the SCADA firewall; and 2) updated the firewalls to ensure that if one firewall fails, the second firewall will automatically pick up the SCADA communications traffic. | 2014-03-01 | 2016-02-11 | Does Not Contest | WECC reviewed VEA's internal compliance program (ICP) and considered it to be a mitigating factor in determining the penalty. WECC determined that VEA's ICP documents and their active and enthusiastic staff participation in the audit process, as well as the compliance program review, demonstrated a compliance culture indicative of an evolving ICP with staff and resources committed to continued program development, program implementation, self-evaluation, and improvement. VEA did not receive mitigating credit for self-reporting the violation. However, WECC considered VEA's cooperation and participation in the voluntary event analysis process as mitigating factors, following the January 13, 2014 event. WECC considered VEA's compliance history and determined there were no relevant instances of noncompliance.