## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council (FRCC) | Tampa Electric Company (TEC) | NCR00074 | FRCC2015015352 | Settlement Agreement | On November 17, 2015, TEC submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-3 R2. TEC discovered the violation as part of its internal controls when it conducted a search of the power plant bus voltage database. This review identified that TEC did not maintain the bus voltage per the required schedule at Polk Power Station for a period of 7 hours and 30 minutes. On April 13, 2015, the bus voltage dropped approximately 1 kV, or 0.4%, under the required bus voltage lower-scheduled band of 238 kV (scheduled voltage limits (238-241.5 kV). TEC's operator failed to meet the conditions of notification for deviations from the voltage schedule provided by the Transmission Operator (TOP). On April 13, 2015 at 7:20 a.m., the Polk Power Station 230 kV bus dropped below the voltage schedule lower limit of the scheduled bus voltage of 238 kV, which initiated a low bus voltage alarm in the control room that was acknowledged by the station operator. However, at this stage of the start-up the station was exempt from maintaining the required voltage schedule since none of the station’s units were online at the time. The voltage subsequently recovered to 238.1 kV, but the alarm did not reset because the voltage was still below the 238.8 kV value required to reset the alarm. At 9:55 a.m., Polk Unit 4 combustion turbine (CT) was brought online with its automatic voltage regulator (AVR) in automatic, controlling voltage. At 10:45 a.m. Polk Unit 2 CT was brought online with its AVR in automatic, controlling voltage. At 11:05 a.m., the station bus voltage dropped to 237.6 kV and remained in the range of 237.4 - 237.9 kV until retuning to 238 kV at 6:35 p.m. that same day. The operator did not notice that the bus voltage was below the lower limit of the schedule because the alarm that would have brought it to his attention was obscured by more recent log entries for other events. TEC performed a root cause analysis for this noncompliance and determined the root cause was an ineffective detective control: the bus voltage alarm does not reset after startup. The bus voltage alarm, along with a host of other startup related alarms, commonly comes in during the startup phase, and had been acknowledged before the units were brought on line. The alarm did not recycle/reset after the units came on line because of the logic in the alarming does not take into account the unit's offline/online status. Therefore, the plant operator did not notice that the bus voltage was below the lower limit of the schedule. | VAR-002-3 | R2 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Risk posed to the BPS from this issue was mitigated by the following factors. On average, TEC’s generator voltage deficiency did not exceed 0.4% (1 kV) of the voltage schedule. In addition, the two generating units (Polk CT 2 & Polk CT 4) operated with its AVR in automatic mode during this period. The TEC transmission operators were monitoring the Bulk Electric System (BES) voltages, and TEC system voltage operated within voltage limits during the entire period. Although the TEC transmission operator had no system indicator to take action or request increased voltage from any of TEC generating units, in the event the TEC transmission operators required voltage response, the Polk Power Station still had reactive power capabilities. TEC examined the bus voltage records for all generation facilities and found no additional occurrences. Additionally, there were no Misoperations, System Operating Limit exceedances, or Interconnection Reliability Operating Limit exceedances. There were no impacts to real-time operations, the TEC BES was not stressed, and there were no operating emergencies or special operating procedure in effect during this time. Finally, TEC did not receive any notifications from its TOP during the time the voltage was outside of the voltage schedule to adjust generator voltage. No actual harm occurred. | 4/13/2015 (when the Polk Power Station 230 kV bus dropped below the voltage schedule while CT 4 was online, at 11:05 a.m.) | 4/13/2015 (when the Polk Power Station 230 kV bus returned to the voltage schedule at 6:35 p.m.) | $4,000 (for FRCC2015015352 and FRCC2015015379) | Self-Report | To mitigate this issue, TEC: 1) reviewed the records of all of TEC’s station's bus voltages and found no additional occurrences; 2) reconfigured the low bus voltage alarm at Polk Power Station to address the unit's online status. Additionally, the alarms are now "low-low" and "high-high" to alert the plant operators before they reach the limits of the bus schedule; 3) applied step 2 to Big Bend and Bayside plants; 4) revised the bus voltage schedule procedure for all three stations; and 5) re-trained plant operators on revised procedures. | 2016-02-20 | 2016-03-14 | Neither Admits nor Denies | FRCC reviewed TEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TEC has a documented ICP that has been reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP. FRCC considered TEC’s compliance history and determined there were no relevant instances of noncompliance. In working with TEC regarding previous violation disposed in NP16-11-000, TEC improved its root cause analysis process, and uncovered these additional violations. However, due to time constraints, FRCC could not wait to settle all of them at the same time.
Florida Reliability Coordinating Council (FRCC) | Tampa Electric Company (TEC) | NCR00074 | FRCC2015015379 | Settlement Agreement | On November 19, 2015 TEC submitted a Self-Report stating that, as a Transmission Owner (TO), it was in violation of FAC-008-3 R8, R8.1. On two separate instances, May 10, 2015 and again on May 14, 2015, circuits tripped within TEC's system affecting several facility ratings. These issues occurred due to a transmission line not being re-rated when the relays operated and opened one of the two circuit breakers that were feeding the circuit. FAC-008-3 R8, R8.1 requires an entity to provide the re-ratings of facilities to an associated group of requesting entities. TEC failed to provide information of all of its re-ratings to its associated group of requested entities. This issue occurred because TEC's transmission operators failed to properly execute the process of de-rating values for all of the affected circuits into the energy management system (EMS). Specifically, they failed to hit “enter” after inputting the last circuit re-rating, and as such the value did not actually get accepted or entered into the EMS; which is the means by which TEC provides information required in FAC-008-3 R8. Instance #1 On Sunday, May 10, 2015, a 230 kV static wire fell across the West 230 kV Bus and across a 69 kV circuit, subsequently initiating several relay trippings. TEC failed to notify the Reliability Coordinator (RC) and other applicable entities of the de-rated circuit 230009 that changed as a result of the trippings. Instance #2 On Thursday, May 14, 2015, a fault occurred on 230008 (Big Bend to Castle, tie-line between TEC and a neighboring entity) and the circuit tripped. TEC failed to notify the RC and other applicable entities of the de-rated circuit 230018’s short-term emergency rating that changed as a result of the trippings. TEC performed a root cause analysis for this noncompliance and determined that the root cause was: the failure to verify and ensure that the EMS had been properly updated, which was due to task saturation from a large number of alarms and phone calls that TEC transmission operators encounter during instances of disturbances. | FAC-008-3 | R8; R8.1; R8.1.1 | Medium | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The maximum flows on the lines over the past two calendar years were 641 MVA for 230009, (93% of the de-rated continuous rating, and 80% of the de-rated short term emergency rating), and 476 MVA for 230018, (69% of the de-rated continuous and 59% the de-rated short term emergency rating). Therefore, the failure to de-rate the lines would not have likely resulted in overloads in these instances. No System Operating Limits were exceeded, no Interconnection Reliability Operating Limits were exceeded, and no energy emergencies were requested during this period. In the first instance, the actual flow on the circuit 230009 was 143 MVA, (21% of the de-rated continuous facility rating). In the second instance, the actual flow on circuit 2300018 was 111 MVA, (12% of the continuous facility rating). TEC reviewed all 2015 unplanned outages to confirm that facilities that required re-rates were done correctly. There was only one facility re-rate required other than these two events and it was done correctly. Additionally, TEC performed testing to ensure the identified root cause was not the result of an underlying software issue with the EMS system. No actual harm occurred. | 5/10/2015 (the first instance where circuit 230009 was de-rated without properly communicating the change in rating) | 5/14/2015 (the final instance where circuit 230018 was de-rated without properly communicating the change in rating) | $4,000 (for FRCC2015015352 and FRCC2015015379) | Self-Report | To mitigate this issue, TEC: 1) updated procedures to have another system operator in the room verify that all re-rates have been implemented and communicated to the FRCC RC via Inter-Control Center Communications Protocol data link; and 2) provided updated training on circuit re-rates including the additional step to have another system operator in the room verify that all re-rates have been implemented correctly. | 12/2/2015 | 2016-02-08 | Neither Admits nor Denies | FRCC reviewed TEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TEC has a documented ICP that has been reviewed by FRCC to verify the program included corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP. FRCC considered TEC’s FAC-008-3 R8 compliance history in determining the penalty. TEC's relevant prior noncompliance with FAC-008 R8 includes NERC Violation ID FRCC2014014460. FRCC considered TEC's FAC-008 R8 be an aggravating factor in the penalty determination. This violation evaluated individually was minimal risk. However, there was a trend identified through repeat violations that increased the risk to reliability that resulted in additional focus through SNOP and Settlement. In working with TEC regarding previous violation disposed in NP16-11-000, TEC improved its root cause analysis process, and uncovered these additional violations. However, due to time constraints, FRCC could not wait to settle all of them at the same time.
ReliabilityFirst Corporation (ReliabilityFirst) | Calpine Corporation (Calpine) | NCR00006 | RFC2015015261 | Settlement Agreement | During a Compliance Audit conducted from September 14, 2015 through September 23, 2015, ReliabilityFirst determined that Calpine, as a Generator Operator, was in a violation of EOP-005-2 R14. For 10 of 16 sampled Blackstart Resources, Calpine did not have documented procedures for starting each Blackstart Resource and energizing a bus to be implemented during system restoration. Calpine provided some procedures for testing the Blackstart Resources, but not for starting the Blackstart Resources as required by EOP-005-2 R14. Since the Compliance Audit, Calpine has retired eight of the units and PJM Interconnection LLC (PJM) elected to discontinue its blackstart service from five of Calpine’s units due to the small size of the units. Calpine determined that the root cause of the issue was an oversight when Calpine acquired the facilities in 2010 and conducted its routine protocol for ensuring regulatory compliance for newly acquired facilities, that led to Calpine overlooking the procedures. Additionally, a contributing factor was lack of effective verification controls surrounding the acquisition of new generating units to confirm that the proper procedures were in place with respect to those units. | EOP-005-2 | R14 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk of not having procedures in place for starting a Blackstart Resource or energizing a bus is that if a blackout or partial blackout occurred, and Calpine was called on to start the Blackstart Resources per the Transmission Operator’s System Restoration Plan, Calpine may not have started the Blackstart Resources and energized a bus as required, or may not have been able to do so in a timely manner. In this case, this risk was partially reduced because the evidence showed that the operators were familiar with the Blackstart Resources, were able to run and test them during normal system conditions, and that many of the operators participated in PJM’s and local utility’s restoration drills, thus increasing the likelihood that the operators would have been able to take the required actions to start the units during a blackout. However, these facts do not eliminate the risk of the units not starting, because during a restoration event, system conditions such as frequency and voltage may be in flux and thus a defined procedure to follow would assist in timely and effective start-up of the unit. Calpine does a complete compliance assessment for newly acquired units. Calpine's fleet wide procedures already require Calpine to ensure that its newly acquired blackstart unit procedures have the required information. The violation occurred only with respect to units acquired in 2010, and those units had test procedures, but not the specific procedures required by EOP-005-2 R14. During the audit, ReliabilityFirst confirmed that Calpine's newer units had correct procedures. Thus, the risk posed to the BPS was moderate. No harm is known to have occurred. | 7/1/2013 (when the Standard became mandatory and enforceable) | 10/13/2015 (Mitigation Plan completion) | $20,000 (for RFC2015015261 and RFC2015015262) | Compliance Audit | To mitigate this violation, Calpine: 1) reviewed current fleet-wide and plant-specific blackstart procedures for all active Calpine Blackstart Resources and updated them as necessary; and 2) revised its fleet-wide and plant-specific blackstart procedures to incorporate the ReliabilityFirst audit team’s recommendations, including: (a) modifying existing procedures to detail the steps for startup and energizing a bus during a system restoration event; and (b) adding revision histories, approval signature(s) and approval date(s) to the fleet-wide and plant-specific blackstart procedures. | 2015-10-13 | 2016-01-05 | Admits | Because of the duration of the violations, and the fundamental nature of the violations and criticality of Blackstart Resources, ReliabilityFirst has determined that a monetary penalty of $20,000 is warranted. ReliabilityFirst reviewed Calpine's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Although Calpine did not identify these violations prior to the audit, Calpine's immediate and thorough response to the findings is an indicator of the quality of Calpine's compliance program. Calpine’s compliance program has the active support and participation of senior management. The NERC Compliance Team operates independently of Calpine’s operations functions and reports to Calpine’s chief compliance officer/senior vice president internal audit. In turn, the chief compliance officer/senior vice president internal audit reports directly to the chief legal officer and independently to the chairman of the Audit Committee of the Board of Directors. Calpine also has a documented open door policy that encourages reporting of any questions or concerns related to compliance to any member of management or to any executive officer. Additionally, ReliabilityFirst also considered that Calpine was extremely cooperative through the enforcement process. Calpine was proactive in providing ReliabilityFirst with information relating to the violations and quickly responded to additional requests for information. Also, Calpine provided ReliabilityFirst with draft Mitigation Plans even before the audit was complete and committed to an aggressive timeline for completing its comprehensive mitigation. ReliabilityFirst considered Calpine's compliance history and determined there were no relevant instances of noncompliance.
ReliabilityFirst Corporation (ReliabilityFirst) | Calpine Corporation (Calpine) | NCR00006 | RFC2015015262 | Settlement Agreement | During a Compliance Audit conducted from September 14, 2015 through September 23, 2015, ReliabilityFirst determined that Calpine, as a Generator Operator, was in violation of EOP-005-2 R17, R17.1 and R17.2. For the nine individual operators sampled, Calpine did not submit evidence that it provided a minimum of two hours of training on its system restoration plan every two calendar years for operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. Additionally, because Calpine also violated EOP-005-2 R14 by not having documented procedures for starting each Blackstart Resource, it could not provide training on those procedures as required by EOP-005-2 R17.2. Calpine determined that the root cause of the issue was poor administrative controls relating to training records. | EOP-005-2 | R17; R17.1; R17.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk of not providing the required training to operating personnel responsible for Blackstart Resources or energizing a bus is that if a blackout or partial blackout occurred, and Calpine was called on to start the Blackstart Resources per the Transmission Operator’s System Restoration Plan, Calpine may not have started the Blackstart Resources and energized a bus as required, or may not have been able to do so in a timely manner. In this case, this risk was partially reduced because the evidence showed that the operators were familiar with the Blackstart Resources, were able to run and test them during normal system conditions, and that many of the operators participated in PJM Interconnection LLC's and local utility’s restoration drills, thus increasing the likelihood that the operators would have been able to take the required actions to start the units during a blackout. However, these facts do not eliminate the risk of the units not starting because during a restoration event, system conditions such as frequency and voltage may be in flux and thus and tailored training would assist in timely and effective start-up of the unit. Thus, the risk posed to the BPS was moderate. No harm is known to have occurred. | 7/1/2015 (when Calpine was required to provide the training under the Standard) | 10/29/2015 (Mitigation Plan completion) | $20,000 (for RFC2015015261 and RFC2015015262) | Compliance Audit | To mitigate this violation, Calpine: 1) disseminated the revised fleet-wide and plant-specific Blackstart procedures to each Blackstart facility plant manager; 2) sent each Blackstart facility plant manager revised training sign-up sheets to be executed by each individual upon completion of training, and an attestation to be executed by the Blackstart facility plant manager verifying that training was conducted; 3) (a) discussed the required training sessions on both the revised fleet-wide and plant-specific Blackstart procedures for all Blackstart facility personnel; and (b) reviewed Calpine’s obligation to maintain proper evidence of training of Blackstart facility personnel on the revised procedures, during a regularly scheduled monthly compliance conference call with plant managers; 4) plant managers conducted requisite two-hour training on Blackstart restoration at each Blackstart facility; and 5) reviewed evidence of training for each Blackstart facility and created an electronic record of such training. | 2015-10-29 | 2016-02-05 | Admits | Because of the duration of the violations, and the fundamental nature of the violations and criticality of Blackstart Resources, ReliabilityFirst has determined that a monetary penalty of $20,000 is warranted. ReliabilityFirst reviewed Calpine's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Although Calpine did not identify these violations prior to the audit, Calpine's immediate and thorough response to the findings is an indicator of the quality of Calpine's compliance program. Calpine’s compliance program has the active support and participation of senior management. The NERC Compliance Team operates independently of Calpine’s operations functions and reports to Calpine’s chief compliance officer/senior vice president internal audit. In turn, the chief compliance officer/senior vice president internal audit reports directly to the chief legal officer and independently to the chairman of the Audit Committee of the Board of Directors. Calpine also has a documented open door policy that encourages reporting of any questions or concerns related to compliance to any member of management or to any executive officer. Additionally, ReliabilityFirst also considered that Calpine was extremely cooperative through the enforcement process. Calpine was proactive in providing ReliabilityFirst with information relating to the violations and quickly responded to additional requests for information. Also, Calpine provided ReliabilityFirst with draft Mitigation Plans even before the audit was complete and committed to an aggressive timeline for completing its comprehensive mitigation. ReliabilityFirst considered Calpine's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Colorado Springs Utilities (CSU) | NCR05106 | WECC2014014528 | Settlement Agreement | On December 19, 2014, CSU submitted a Self-Report stating that, as a Transmission Owner, Distribution Provider and Generator Owner, it was in violation of PRC-005-1 R2. Specifically, following recommendations from a July 2014 peer review by the North American Transmission Forum, CSU management conducted a thorough review to physically confirm all relay settings documented in its electronic database. On October 30, 2014, CSU identified that six electro-mechanical relays were inadvertently omitted from its work management system and had not been tested since 2004. WECC reviewed the details of this Self-Report during an on-site Compliance Audit conducted from April 27 to May 8, 2015. During the audit, WECC determined that maintenance records provided for two additional relays and for DC control circuitry at two stations were insufficient to demonstrate compliance, and expanded the scope of the Self-Report to include this discovery. During a quarterly review conducted in January 2016, CSU discovered incomplete documentation for maintenance performed on three battery banks in November 2015. CSU informed WECC of the discovery and expanded its mitigating activities to include the battery banks. WECC determined that CSU failed to maintain and test 8 of CSU’s 948 relays (0.84%), 2 of CSU’s 175 DC Control Circuitry (1.14%), and 3 of CSU's batteries. The root cause of this violation was inadvertent omission of devices during CSU's transition to an electronic database system from its manual index-card based record-keeping system. CSU also explained that while most maintenance records were accessible in the current database, a small sub-set of devices were maintained using ProTesT and the detailed records were stored in a database that is no longer in use. | PRC-005-1 | R2; R2.1; R2.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CSU failed to fully implement its Protection System Maintenance and Testing Program (PSMP) by: 1) missing testing intervals for six electro-mechanical relays; and 2) providing incomplete and/or insufficient documentation for testing of two additional relays, three battery banks, and DC control circuitry at two stations. Such failure could potentially result in inconsistent testing and maintenance activity and/or documentation thereof, which could limit CSU’s awareness of the working order of its Protection System devices. However, CSU’s small size and limited connection to other entities limits its ability to have an adverse impact beyond its own system. Additionally, the devices addressed within the scope of this violation included less than one percent of relays (8 of 948 relays), (2 of 175 DC control circuitry), and battery banks in CSU’s PSMP. Further, all devices included in the scope of this violation have since been maintained and tested. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on CSU) | 1/15/2016 ( Mitigation Plan completion date) | 0 | Self-Report | To mitigate this violation, CSU: 1) completed testing and maintenance on all devices included in the scope of this violation; 2) verified the six electro-mechanical relays listed in the original Self-Report are now included in its work management system; 3) reviewed and updated its PSMP to incorporate new requirements; 4) consolidated management of PSMP under a single point of responsibility; | 1/15/2016 | 2016-02-23 | Neither Admits nor Denies | WECC considered the fact that CSU self-reported this violation a mitigating factor. In addition to required mitigation efforts, WECC considered “above and beyond” actions and investments made by CSU to prevent recurrence of this violation as mitigating factors. At the time of the initial discovery, CSU was investing in and transitioning to a work management system and electronic database to improve its maintenance and testing program. As part of the effort to ensure consistency between paper and digital records through this transition, CSU conducted a thorough review to physically confirm all relay settings documented in its electronic database system, leading to the identification of the six devices included in the original Self-Report. CSU developed and implemented new processes for utilizing its work management system to automate scheduling and other maintenance tasks and improve documentation consistency and quality. The implementation of this system cost CSU approximately $191,000. WECC treated these activities as a credit in the determination of the $0 penalty. WECC considered CSU’s PRC-005-1 R2 compliance history to be an aggravating factor in the disposition determination. CSU’s relevant prior noncompliance with PRC-005-1 R2 includes NERC Violation IDs: WECC200801034 and WECC201102445.
Western Electricity Coordinating Council (WECC) | Columbia River People’s Utility District (CRPD) | NCR05109 | WECC2014013475 | Settlement Agreement | On February 28, 2014, CRPD submitted a Self-Certification stating that, as a Distribution Provider, it was in violation of PRC-005-1 R2. As part of CRPD’s self-certification process, CRPD reviewed its maintenance and testing program and determined it was not compliant with its annual battery testing and maintenance schedule. A WECC subject matter expert reviewed CRPD’s Self-Certification, and determined that for 35 out of 39 (89.74%) Protection System devices, (excluding the battery chargers), CRPD failed to perform maintenance and testing in accordance with its maintenance and testing program. Specifically, CRPD failed to maintain and test 10 out of a total 10 protective relays; 13 out of 13 instrument transformers; 8 out of 12 battery systems; and 4 out of 4 control systems. WECC determined that CRPD had a violation of PRC-005-1 R2, for its failure to provide sufficient documentation that CRPD implemented its maintenance and testing program for CRPD’s Protection Systems for 35 Protection System devices except for CRPD’s battery chargers. Therefore, WECC determined that CRPD failed to have evidence that it maintained and tested its Protection System devices within defined intervals, resulting in a violation of PRC-005-1 R2 (R2.1). The root cause of this issue was CRPD’s lack of compliance understanding, leading to its failure to record maintenance and testing results, to provide evidence that its Protection System devices were maintained and tested within the defined intervals. (WECC notes that mitigation of an earlier occurrence of this violation was verified complete on 9/30/2008. Then, at a WECC offsite audit in 2009, the audit team "reviewed the maintenance records for these protection systems and found them to be current with CRPD’s maintenance and testing program.” For these reasons, CRPD relied on WECC's guidance, and considered itself compliant with this Standard from 2009 forward.) | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to provide sufficient documentation of the implementation of CRPD’s maintenance and testing program might expose the 35 Protection System equipment devices associated with this violation to a higher risk of failure as the devices would not be tested for their operation. CRPD implemented good detective controls to detect the potential loss of 104 MW of load. Specifically, CRPD implemented a supervisory control and data acquisition (SCADA) system which provides visibility of its substation status and configuration to its system operators. About 50% of CRPD’s system relays utilize self-monitoring capabilities and provide alarms in the case of relay trouble and/or failure. This notifies the system operators in real time if there are any issues with the substation. Further, CRPD’s batteries are located in distribution substations, connected to 115 kV transmission lines owned by Bonneville Power Administration (BPA). These transmission lines are not critical to BPA’s transmission system. No harm is known to have occurred. | 5/31/2008 (when CRPD first missed its maintenance and testing interval, except for the battery chargers) | 4/6/2015 (Mitigation Plan completion) | 0 | Self-Certification | To mitigate this violation, CRPD: 1) added a section to the data sheet to include Voltage levels when CRPD tests the power supply voltage; 2) added a spot to record results of the wiring and connection inspection during visual inspection and provided updated documents showing the maintenance mentioned in the new sections was performed; 3) added a section to inspection forms to include a section to record battery system ambient temperature; and 4) added the sections to record visual inspection for protective relays, including a spot to record inspection for proper condition of test switches, lockout relays, and controls switches and provided updated documents showing the maintenance was performed. In addition to the above mitigation, CRPD agreed to the following additional terms. On March 20, 2015, CRPD's Engineering and Operations Manager submitted confirmation to WECC that it had fulfilled the following deliverables agreed to by the Parties in the Settlement, below. 1) initiated an assessment, engaging with applicable WECC registration personnel, with respect to Bulk Electric System (BES) definitional exclusions or exemptions to determine any CRPD elements that may be deemed non-BES; 2) developed and updated CRPD's PRC-005 Maintenance and Testing Program in preparation for PRC-005 Version 2 implementation; 3) submitted a narrative to WECC describing CRPD’s plan to assess its BES elements for possible exemptions or exclusion and any possible registration ramifications BES by March 16, 2015; and 4) submitted a narrative to WECC via the WECC Compliance Enhanced File Transfer Server (EFT Server) describing the steps CRPD it would take to prepare for PRC-005-1 Version 2 by March 16, 2015. | 4/6/2015 | 3/25/2016 | Agrees/Stipulates | WECC considered CRPD’s PRC-005 R2 compliance history in determining the disposition track. CRPD’s relevant prior noncompliance with PRC-005 R2 includes NERC Violation ID WECC200700468. WECC verified completion on 9/03/2008. The root cause of the earlier violation was CRPD's lack of a NERC-compliant process when the Standard came into effect. The first violation for PRC-005-1 R2, was filed under FERC Docket NP10-2-000 on October 14, 2009. The present violation began on 5/31/2008, (overlapping the first occurrence), and WECC determined that CRPD’s compliance history should not serve as a basis for aggravating the disposition track. WECC conducted an off-site audit of CRPD in 2009 wherein it found CRPD’s maintenance records for its protection systems to be current with CRPD’s maintenance and testing program. For these reasons, CRPD relied on WECC's guidance, and considered itself compliant with this Standard from 2009 forward. When CRPD self-certified in 2014 that it had missed a single testing interval, WECC discovered that CRPD had additional issues with its PSMP and testing. WECC is assessing a zero-dollar penalty for this violation based in part on the prior history of compliance monitoring. In 2014, a WECC SME, to verify the completed mitigation plan review, conducted a thorough review of CRPD's compliance with the Standard, including multiple data requests for information, procedures, and maintenance and testing records. WECC notes that CRPD fully cooperated with WECC on this additional review.
Western Electricity Coordinating Council (WECC) | Equilon Enterprises, LLC (f/k/a March Point Cogeneration Company) (MPCC) | NCR05232 | WECC2014014104 | Settlement Agreement | During a Compliance Audit conducted from June 23, 2014 through June 24, 2014, WECC determined that MPCC, as a Generator Operator (GOP) and Generator Owner (GO), was in violation of PRC-005-1 R2. The entity failed to fully implement the Protection System Maintenance and Testing Program including documentation that all the Protection System devices were maintained and tested within the defined intervals. MPCC failed to document that it maintained and tested 217 out of 659 (33%) Protection System devices within the defined intervals. WECC determined that there were two primary causes of the missing data. MPCC was acquired by Equilon Enterprises, LLC in February 2010 and many of the documents that predate this transaction are missing or unavailable. Additionally, a scheduling error in 2012 resulted in a "major" maintenance scope being conducted resulting in missed maintenance on the Steam Turbine Generator (STG) and some of its common equipment. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MPCC's failure to test and maintain its Protection System devices according to its defined intervals could lead to a misoperation. However, MPCC connects to the BPS at a single point of interconnection. MPCC has less than 7% of its Balancing Authority's total available generation. Further each battery set has redundant chargers, and the chargers alarms into MPCC control system in the event of a malfunction. Also, MPCC conducted annual and quarterly maintenance concurrently on batteries. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 9/30/2015 (Mitigation Plan completion date) | 15000 | Compliance Audit | To mitigate this violation, MPCC has: 1) conducted electrical maintenance on Gas Turbine Generator (GTG) 201 during a planned outage in June 2015; 2) conducted electrical maintenance work for the STG during a planned outage in June 2015; 3) entered the major maintenance events into the 5-year shutdown schedule, including GTG 101 in 2016 and GTG 301 in 2017; and 4) created maintenance plans in GSAP, the work planning system. Work plans include the entire work scope, task list, and the text of the plan including the following statement: “This work is mandatory/regulatory preventative maintenance to satisfy the WECC compliance plan. An MOC is required to change content or interval.” | 2015-09-30 | TBD | Does Not Contest | WECC considered MPCC's compliance history and determined there were no relevant instances of noncompliance