## Public Non-CIP SNOP Posting
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
SERC Reliability Corporation (SERC) | Associated Electric Cooperative, Inc. (AECI) | NCR01177 | SERC2015015266 | Settlement Agreement | On October 1, 2015, AECI submitted a self-log stating that, as a Transmission Operator (TOP), it was in violation of TOP-004-2 R6.2. Specifically, AECI failed to implement its formal policies and procedures that addressed the execution and coordination of switching transmission elements. On January 5, 2016, AECI submitted self-logs of two additional violations of TOP-004-2 R6.2. Because the three instances all involved failure to implement the same procedure required by TOP-004-2 R6.2, SERC consolidated all three instances into a single violation. Because AECI had several self-logged issues of TOP-004-2 R6.2, SERC determined the issues posed a moderate risk and should not receive Compliance Exception treatment. AECI is registered as a TOP on behalf of Northeast Missouri Electric Power Cooperative (Northeast) and KAMO Electric Power Cooperative (KAMO) per JRO00088. July 21, 2015 Incident On July 20, 2015, AECI system operations received notification from the Northeast dispatch center that the Palmyra 345/161 kV transformer had lost a portion of its cooling system and had to be derated. Northeast notified AECI system operations that Northeast planned to switch the failed transformer unit out with the onsite spare transformer unit on July 21, 2015. On July 20, 2015, at 3:55 p.m., AECI notified the Reliability Coordinator (RC) at Tennessee Valley Authority (TVA) of the new operating limits and maintenance plan. At 4:18 p.m. on July 20, 2015, due to loading concerns, AECI, Northeast, and TVA coordinated with MISO/Ameren to open the Spencer Creek 345 kV line to help reduce load on the Palmyra transformer. At 1:20 a.m. on July 21, 2015, Northeast removed the Palmyra transformer from service to prevent potential damage to it. Up to this point, AECI had followed the required procedural notifications, i.e. proper notifications and coordination with the TOP, RC, and surrounding TOPs and the use of three-part communication to convey the situation as the day went on. On July 21, 2015, Northeast dispatch notified AECI that its maintenance crew would be going to the Palmyra substation that day to perform the switching procedure required to energize the onsite spare transformer. After completing the work, Northeast returned the Palmyra transformer to service at 10:24 a.m. but did not notify AECI until 10:27 a.m. Northeast did not notify AECI system operations prior to switching to energize the spare transformer as required by its procedure. On July 21, 2015, AECI identified the noncompliance when its Energy Management System (EMS) showed the transformer was back in service but AECI dispatch had not received communication from Northeast prior to the switching. October 28, 2015 Incident On October 28, 2015, Thomas Hill Unit #2 was taken offline by operating generator circuit breakers, in accordance with AECI’s switching procedure. Subsequently, Thomas Hill plant personnel operated the unit disconnect switch without a switching order, as required by the AECI switching procedure. An AECI system operator identified the violation when responding to alarms and EMS system status point changes issued by the AECI EMS system. November 9, 2015 Incident On November 9, 2015, KAMO removed a 138 kV line from service in accordance with the AECI switching procedure. While switching the line out of service, KAMO inadvertently deviated from the switching order and opened the incorrect circuit breaker. Once KAMO realized that it had opened the wrong circuit breaker, it closed the circuit breaker and then resumed implementing the switching order by opening the correct circuit breaker. The KAMO regional dispatch office notified the AECI system operator that KAMO had deviated from the switching order. The root cause of all three instances was human error. Specifically, AECI operators (plant personnel) failed to adhere to established and documented procedures. AECI and its member cooperatives had not completed the training activity associated with the mitigation activities for the October 1, 2015, self-logged issue by the time of the two additional occurrences. | TOP-004-2 | R6; R6.2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AECI’s system operator controlled bringing generation online or offline and the AECI regional dispatch did not have control capability to do so. A regional dispatch center failing to implement the AECI switching procedure correctly when operating a radial 161/138 kV line could potentially cause a loss of load. Because the AECI system operator failed to implement the AECI switching procedure correctly, there could have been a loss of both generation and load. Nevertheless, AECI monitored BPS conditions such that a single planned or unplanned operation would not cause a facility to overload. AECI operated to N-1 conditions and studied, via real-time N-1 contingency analysis, any single intentional or unintentional operation. In addition, the AECI EMS provided alarming to system operations staff. When changes of state occurred, real-time breaker status alarms reported to AECI system operations staff. For the July 21, 2015 instance, AECI returned the Palmyra 345/161 transformer to service, therefore improving reliability. No harm is known to have occurred. | 7/21/2015 (when AECI first executed switching transmission elements without prior notification) | 4/29/2016 (Mitigation Plan completion) | $0 | Self-Report | To mitigate this violation, AECI: 1) updated its switching procedure to address the second and third instances; 2) provided training on the revised AECI switching order procedure and jurisdictional control agreement to each of the generation and transmission regional dispatch center’s staff; 3) scheduled for generation and transmission regional dispatch personnel to receive the training once every six months; and 4) scheduled for applicable AECI power production personnel to receive the training once every six months. | 4/29/2016 | 2016-06-07 | Admits | SERC reviewed AECI’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. AECI has a documented ICP specific to NERC and SERC compliance. AECI reviews the ICP once every year and posts it where all AECI employees can access it. AECI’s manager of reliability compliance (MRC) oversees the ICP and reports to the senior manager reliability compliance and audit services (SMRCAS), who reports to the chief executive officer (CEO). AECI’s SMRCAS has direct access to the CEO and board of directors and has independence from operations responsible for compliance. AECI trains all employees on the ICP once per year and also makes employees aware of enforcement actions. The ICP provides for an annual self-audit. The ICP allows for discipline of employees for failing to abide by the ICP. In determining the penalty amount, SERC considered that this violation was AECI's first violation of TOP-004 R6 and was reported to SERC via the self-logging program. SERC provided additional risk-assessment training to AECI on May 25, 2016 to ensure AECI self-logs only minimal risk noncompliance going forward. SERC considered AECI's compliance history and determined there were no relevant instances of noncompliance.