## Public Non-CIP SNOP Posting
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Avangrid Renewables (PPME) | NCR10259 | WECC2014013988 | Settlement Agreement | During a Compliance Audit conducted from June 5, 2014 through June 6, 2014, WECC determined that PPME, as a Generator Owner, was in violation of PRC-005-1 R1. WECC determined that PPME's Protection System Maintenance and Testing Program (PSMP) at its Klamath facility contained the following deficiencies: 1) station batteries and chargers lacked a summary of maintenance and testing procedures; 2) protective relays lacked an interval and its basis; 3) DC circuits lacked an interval and its basis, and a summary of maintenance and testing procedures; 4) instrument transformers lacked an interval and its basis, and a summary of maintenance and testing procedures; and 5) associated communications lacked an interval and its basis. PPME’s failure to have a complete PSMP for Klamath is a violation of PRC-005-1 R1. PPME asserted that all high-side equipment located within the ring bus/switchyard at Klamath is owned, operated, and maintained by another entity and that PPME is only responsible for equipment that falls below the point of interconnection to the Bulk Electric System. PPME further asserted that the equipment below the point of interconnection does not fall under PRC-005 and therefore does not require a PSMP. However, after several data requests it was determined that Klamath does not have its own PSMP and PPME would not be submitting a PSMP specific to Klamath. The root cause of the violation was a lack of compliance understanding, in that PPME was unaware that the Klamath Facility was required to be covered in its PSMP. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PPME failed to have a complete PSMP for its Klamath Co-generation Facility. Failure to implement a documented maintenance and testing program could result in sporadic or incomplete maintenance and testing on Protection System devices. Failure to regularly maintain and test could lead to Protection System misoperations, potentially resulting in the loss of the Protection Systems associated with the Klamath Co-generation Facility. As a compensating measure, PPME’s lack of a PSMP only applied to Klamath. All other PPME facilities operate under PPME’s corporate wide PSMP, which was not found to contain deficiencies. Further, equipment at the Klamath Co-generation facility is continually monitored, visually inspected and periodically tested on a regular basis. Finally, no harm is known to have occurred. | 10/8/2007 (when the Standard became mandatory and enforceable on PPME) | 3/19/2015 (Mitigation Plan completion) | $20,000 (for WECC2014013988 and WECC2014013989) | Compliance Audit | To mitigate this violation, PPME: 1) created a Klamath specific PSMP that adheres to PRC-005 2 standard; and 2) appointed a PRC-005 subject matter expert for the Klamath Co-generation facility that has knowledge of the facility, equipment, and strong comprehension of the requirements for the PRC-005 Standard. | 2015-03-19 | 2015-09-28 | Agrees/Stipulates | WECC reviewed PPME’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: PPME has a high-level general program; PPME’s ICP identifies and lists applicable NERC Reliability Standards and includes a process for updating this list; PPME has identified and assigned responsibility and accountability to a compliance officer; PPME has one position fully dedicated to FERC/NERC compliance; PPME’s compliance official has independent access to the chief executive officer (CEO) or equivalent; PPME’s ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; PPME has dedicated adequate resources to support its ICP; PPME’s ICP has the support and participation of senior management; PPME’s ICP requires general compliance training for all staff and specific training for SMEs; PPME has distributed the ICP to all employees, contractors and vendors; PPME has fully implemented its program; PPME’s ICP includes procedures for disciplinary action for employees involved in willful violations of the Reliability Standards; PPME’s ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards; PPME reviews its ICP at least annually; and, PPME participates in outreach compliance program activities. WECC considered PPME’s compliance history and determined there were no relevant instances of noncompliance. In addition to the agreed upon payment terms, PPME agreed to engage in Reliability Enhancement Measures to further reliability of the BPS. PPME agreed to undergo the following Reliability Enhancement Measures: A) Further strengthen internal controls related to Protection System maintenance and testing; i) Standardize program documentation specific to PRC-005-2; ii) Develop or enhance training with respect to implementing the V2 program; iii) Ensure PPME provides enhanced training with respect to PRC-005 V2 to all applicable personnel; and B) Provided a narrative to WECC explaining how PPME implemented the above items, including descriptions of new or enhanced internal controls.
Western Electricity Coordinating Council (WECC) | Avangrid Renewables (PPME) | NCR10259 | WECC2014013989 | Settlement Agreement | During a Compliance Audit conducted from June 5, 2014 through June 6, 2014, WECC determined that PPME, as a Generator Owner, was in violation of PRC-005-1 R2. WECC determined after reviewing a sample of Protection System devices that PPME could not provide maintenance and testing records for thirteen relays, representing 8% of its relays, and 9 instrument transformers, representing 5% of PPME's instrument transformers. In addition, PPME could not provide documentation of maintenance and testing for 100% of its DC Circuitry at Klamath, 100% of its Potential Transformer (PT) and Current Transformers (CT) at Klamath, one of nine (11.1%) CTs at Pebble Springs, and one of ten (10%) relays at Pebble Springs. WECC determined that PPME's failure to provide documentation evidencing maintenance and testing of all Protection System devices is a violation of PRC-005-1 R2. WECC further determined that PPME failed to provide documentation of the Klamath PSMP within 30 calendar days of WECC’s request. The root cause of the violation was a lack of compliance understanding, in that PPME was unaware that the Klamath Facility was required to be covered in its Protection System Maintenance and Testing Program (PSMP). | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PPME failed to test and maintain all Protection System devices in accordance with its program. Also, PPME failed to have a complete PSMP for Klamath. PPME failed to provide evidence that the Protection System devices at that facility were tested and maintained within defined intervals. Failure to maintain and test Protection System devices prevents PPME from determining whether the devices are reliable to limit the effects of disturbances in a system network. Failure to maintain and test Protection System devices could also potentially result in loss or degradation of one or more Protection Systems. Finally, PPME failed to provide requested documentation to WECC within 30 days of request. Because of this failure, PPME cannot ensure it is regularly maintaining and testing its Protection System devices. However, equipment at the Klamath Co-gen facility is continually monitored, visually inspected and periodically tested on a regular basis. Finally, no harm is known to have occurred. | 10/8/2007 (when the Standard became mandatory and enforceable on PPME as a Generator Owner) | 5/27/2016 (Mitigation Plan completion) | $20,000 (for WECC2014013988 and WECC2014013989) | Compliance Audit | To mitigate this violation, PPME: 1) appointed a PRC-005 subject matter expert for the Klamath Co-generation facility that has knowledge of the facility, equipment, and strong comprehension of the requirements for the PRC-005 standard in order to identify all applicable equipment at the Klamath facility; 2) created the PSMP for the Klamath Co-generation facility; 3) worked to ensure the equipment is tested in accordance with the PSMP and all equipment is tested entirety; and 4) selected a third-party testing company to schedule the maintenance and testing of all identified equipment. | 2016-05-27 | 2016-08-09 | Agrees/Stipulates | WECC reviewed PPME’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that: PPME has a high-level general program; PPME’s ICP identifies and lists applicable NERC Reliability Standards and includes a process for updating this list; PPME has identified and assigned responsibility and accountability to a compliance officer; PPME has one position fully dedicated to FERC/NERC compliance; PPME’s compliance official has independent access to the chief executive officer (CEO) or equivalent; PPME’s ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards; PPME has dedicated adequate resources to support its ICP; PPME’s ICP has the support and participation of senior management; PPME’s ICP requires general compliance training for all staff and specific training for SMEs; PPME has distributed the ICP to all employees, contractors and vendors; PPME has fully implemented its program; PPME’s ICP includes procedures for disciplinary action for employees involved in willful violations of the Reliability Standards; PPME’s ICP includes formal, internal self-auditing for compliance with all applicable NERC Reliability Standards; PPME reviews its ICP at least annually; and, PPME participates in outreach compliance program activities. WECC considered PPME’s compliance history and determined there were no relevant instances of noncompliance. In addition to the agreed upon payment terms, PPME agreed to engage in Reliability Enhancement Measures to further reliability of the BPS. PPME agreed to undergo the following Reliability Enhancement Measures: A) Further strengthen internal controls related to protection system maintenance and testing; i) Standardize program documentation specific to PRC-005 Version 2; ii) Develop or enhance training with respect to implementing the V2 program; iii) Ensure PPME provides enhanced training with respect to PRC-005 V2 to all applicable personnel; and B) Provided a narrative to WECC explaining how PPME implemented the above items, including descriptions of new or enhanced internal controls.
Western Electricity Coordinating Council (WECC) | USACE - Seattle District (UNWS) | NCR05539 | WECC2013012293 | Settlement Agreement | During a Compliance Audit conducted from April 15, 2013 through April 19, 2013, WECC determined that UNWS, as a Generator Owner (GO), was in violation of PRC-005-1 R1. WECC determined that 14 of 111 (12%) instrument transformers were not included in the UNWS maintenance and testing plan, including maintenance and testing intervals, their basis, and a summary of maintenance and testing procedures. The instrument transformers that were not included were Transformer Bushing Potential Devices (BPDs) at Chief Joseph Dam. This occurred because the BPDs were originally only used for metering and synchronizing. The original electro-mechanical protective relays were replaced with electronic multifunction relays. Beginning at this time, the new relays used signals from the BPDs for transformer protection. UNWS personnel did not add the BPDs to the maintenance and testing program when their function changed. As a result of its examination, WECC determined that UNWS was in violation of PRC-005-1 R1. UNWS was missing the maintenance and testing interval and their basis for 12% of their instrument transformers. They were also missing the summary of maintenance and testing procedures for those devices. The cause was that UNWS personnel did not add the BPDs to the maintenance and testing program when their function changed. | PRC-005-1 | R1; R1.1; R1.2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, UNWS failed to include 14 of 111 (12%) instrument transformers in their Protection System Maintenance and Testing Plan. This included maintenance and testing intervals and their basis, as well as a summary of maintenance and testing procedures for the instrument transformers. The information was missing from the maintenance and testing plan from August 10, 2007 until August 22, 2013. Testing these Protection Systems help to determine if the devices are reliable to limit the effects of disturbances in a system network. If the devices are not tested per the program defined by the entity, the devices cannot be certified to interrupt disturbances that may damage the transmission system and/or generation plants. UNWS did have compensating measures in place. Though not specified in the Plan, UNWS performs various inspections and parallel monitoring of Protection Systems elements and the associated facilities. The Chief Joseph facility is a collection of 27 generating units each rated at 92-100 MW. The failure of instrument transformers leading to the loss of single unit is significant; however, that potential loss is only a fraction of the facilities total output. The entity is in the process of upgrading all relays in the near term and as part of that effort the instrument transformers are scheduled to be tested by mid-year 2013. However, this testing alone may not have led to future testing had UNWS not added the devices to its maintenance and testing plan. | 8/10/2007 (when the BPDs' function changed to include transformer protection) | 8/22/2013 (Mitigation Plan completion) | No penalty (for WECC2013012293 and WECC2013012294) | Compliance Audit | To mitigate this violation, UNWS: 1) added 14 Chief Joseph Dam Transformer Bushing Potential Devices to the maintenance and testing program; and 2) provided training to its operation personnel concerning the noncompliance. | 2013-08-22 | 2013-10-23 | Agrees/Stipulates | WECC considered UNWS’s PRC-005 R1 compliance history. UNWS’s relevant prior noncompliance with PRC-005 R1 includes: NERC Violation ID WECC200801413. WECC considered UNWS’s PRC-005 R1 compliance history to be an aggravating factor in the disposition determination.
Western Electricity Coordinating Council (WECC) | USACE - Seattle District (UNWS) | NCR05539 | WECC2013012294 | Settlement Agreement | During a Compliance Audit conducted from April 15, 2013 through April 19, 2013, WECC determined that UNWS, as a Generator Owner (GO), was in violation of PRC-005-1 R2. The Audit Team issued a request for the maintenance and testing records of 29 Protection System devices. UNWS did not provide records for Libby Dam Unit 1, Current Transformers (CTs). In their response, UNWS stated that it did not have the maintenance documentation for that device. Their maintenance database listed that the maintenance had been completed; however, after review of the underlying record, UNWS determined that the device had not been tested as they did not have maintenance documentation showing that maintenance was performed. The Audit Team requested that UNWS determine if there were any other devices with missing maintenance and testing records. UNWS then determined that there are 16 devices at Libby Dam where the maintenance and testing records cannot be located. In addition, there are 14 Bushing Potential Devices and CTs for the Transformers at Chief Joseph Dam that were not previously included in the maintenance and testing program. This means that UNWS has no records of last and prior date tested for 30 of 111 (27%) sets of instrument transformers owned by UNWS. As a result of its examination, conversations with UNWS personnel, and subsequent data requests WECC determined that UNWS is in violation of PRC-005-1 R2.1 for failing to have evidence of the maintenance and testing program for 30 of 111 (27%) Protection System devices. UNWS was missing documentation for the maintenance and testing of 30 of 111 (27%) of its Protection System devices. The cause was that UNWS personnel did not add the BPDs to the maintenance and testing program when their function changed. The cause for the CT was that the configuration was changed but the maintenance personnel failed to recognize the change. Some of the testing for CTs were deferred due to scheduling reasons and were incorrectly marked as complete in the Protection System Maintenance and Testing Software. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. UNWS failed to have evidence that Protection System devices were maintained and tested within the defined intervals as required by PRC-005-1 R2.1. Specifically, UNWS had no records of last and prior date tested for 30 of 111 (27%) sets of instrument transformers. Testing of the Protection Systems help determine if the devices are reliable to limit the effects of disturbances in a system network. If there is no evidence that the devices were tested according to the program defined by the entity, the devices cannot be entrusted to interrupt disturbances that may damage the transmission system and/or generation plants. UNWS did have compensating measures in place. These include sufficient maintenance and testing practices, as well as the performance of various inspections and the parallel monitoring of Protection Systems elements and the associated facilities. UNWS was also able to provide and attest to the last test date for 12 of the 30 devices based on instrument transformer testing performed as part of upgrades of the associated relays, for which dates are known. It also upgraded all relays and the instrument transformers and the testing was completed by September 20, 2013. However, this testing alone may not have led to future testing had UNWS not added the devices to its maintenance and testing plan. In addition, the Chief Joseph facility is a collection of 27 generating units each rated at 92-100 MW. While the failure of instrument transformers leading to the loss of a single unit is not insignificant, the potential loss of a single unit is only a fraction of the facilities output. However, UNWS failed to have evidence that Protection System devices were maintained and tested within the defined intervals for a significant percentage (27%) of devices at its facility. | 8/10/2007 (when the BPDs' function changed to include Protection) | 9/20/2013 (Mitigation Plan completion) | No penalty (for WECC2013012293 and WECC2013012294) | Compliance Audit | To mitigate this violation, UNWS: 1) scheduled, tested, and documented testing for all 30 Protection System devices; and 2) provided training to its operation personnel concerning the noncompliance. | 2013-09-20 | 2014-06-11 | Agrees/Stipulates | WECC considered UNWS’s PRC-005 R2 compliance history. UNWS’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID WECC200801414. WECC considered UNWS’s PRC-005 R2 compliance history to be an aggravating factor in the disposition determination.
Western Electricity Coordinating Council (WECC) | USACE - Portland District (UNWP) | NCR05538 | WECC201102822 | Settlement Agreement | On May 19, 2011, UNWP submitted a Self-Report stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R2. An internal audit revealed that UNWP had failed to maintain documentation of testing for the following generation Protection System devices: 2 of 517 protective relays, 236 of 900 voltage and current sensing devices, 16 of 982 DC control circuits, and 7 of 21 station batteries. At four Willamette Valley plants, battery maintenance could not be verified because UNWP did not retain the test documentation. At the John Day Dam, while summary job plans exist for battery maintenance, no signed and dated records of this maintenance could be found prior to 2010. Data documenting this maintenance was lost when the computer system storing the data was damaged. WECC reviewed the Self-Report, the Subject Matter Expert's (SME) findings and requested additional information from UNWP. Based on this review, WECC determined that UNWP failed to maintain evidence its Protection System devices were maintained and tested within the defined intervals, and did not maintain the date each Protection System device was last tested and maintained for 2 of 517 protective relays (.4%), 236 of 900 voltage and current sensing devices (26.2%), 16 of 982 DC control circuits (1.6%), and 7 of 21 station batteries (33.3%). For these reasons, WECC determined UNWP had a violation of PRC-005-1 R2. The primary causes for this are the lack of proper test equipment, test procedures, and understanding of the priority associated with the completion of these tasks. The person in charge did not understand the requirements. A new compliance person who is more technically competent has been put in charge. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, the purpose of this Standard is to ensure all transmission and generation Protection Systems affecting the reliability of the BPS are maintained and tested. UNWP is a large GO with 29 generation plants with a maximum generating capacity of 15,569 MW. Although UNWP missed testing and maintenance for approximately 10% of its total Protection System devices, it missed 33% of its scheduled battery maintenance. As compensating measures, UNWP has job plans for maintenance and testing, and UNWP’s SMEs affirm that certain maintenance and testing checks were completed during bi-annual scheduled line outages. These measures, however, do not provide evidence that UNWP has implemented its maintenance and testing program in compliance with the Standard. No harm is known to have occurred. | 8/10/2007 (when the Standard became mandatory and enforceable on UNWP) | 1/8/2014 (Mitigation Plan completion) | No penalty | Self-Report | To mitigate this violation, UNWP: 1) identified and described the maintenance requirements of applicable components, including the generation of monthly preventative maintenance (PMs) and added the information to the maintenance management program; 2) designed and created job plans to ensure that all applicable components are tested regularly per the PRC-005 Standard; 3) conducted training to relate the importance of documenting and archiving all test data and data sheets to verify that the maintenance was completed; and 4) acquired and installed software for the purpose of satisying the PRC-005 audit record retetion. | 2014-01-08 | 2014-02-20 | Agrees/Stipulates | WECC considered UNWP’s PRC-005-1 R2 compliance history in determining the disposition track. UNWP’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID WECC200801007 and WECC200801718. WECC considered UNWP’s PRC-005-1 R2 compliance history to be an aggravating factor in the disposition track determination.
Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC200800976 | Settlement Agreement | On July 10, 2008, UNWW submitted a Self-Certification stating that, as a Generator Owner (GO), it was in violation of PRC-005-1 R1. This noncompliance was discovered as a result of an internal review that was conducted to complete a compliance Self-Certification for WECC. UNWW reported the implementation of a new maintenance database had delayed it from generating and standardizing Preventative Maintenance (PM) across UNWW facilities. As a result of the delays, UNWW had not developed a Protection System maintenance and testing program sufficient to be compliant for audit purposes. WECC conducted an Off-Site Audit (Audit) of UNWW for GO and Generator Operator (GOP) functions. During the Compliance Audit, WECC reviewed UNWW’s “Facility Equipment Maintenance (FEM) & Testing Matrix,” and determined it failed to include maintenance and testing intervals and their basis, as well as a summary of maintenance and testing procedures as required by R1.1 and R1.2 respectively. WECC reviewed the Self-Certification, Compliance Audit results, and Mitigation Plan, and determined UNWW had a violation of the Standard, because UNWW’s Protection System maintenance and testing program failed to include maintenance and testing intervals and their basis, as well as a summary of maintenance and testing procedures as required by the Standard. The cause was a lack of compliance understanding. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). UNWW failed to have a Protection System maintenance and testing program for its facility operations that included all elements required by the Standard. Nevertheless, despite the lack of detail and standardization in its processes, UNWW stated that basic maintenance and testing was being performed under its facility-specific processes. The preventative maintenance was being performed as specified within the maintenance schedule, but lacked standardization across the District projects. This was confirmed in an interview with the reliability compliance program manager. | 8/10/2007 (when the Standard became mandatory and enforceable on UNWW) | 12/19/2008 (Mitigation Plan completion) | No penalty (for WECC200800976, WECC200801418, and WECC2014014151) | Self-Certification | To mitigate this violation, UNWW: 1) identified and developed critical PM, which included testing intervals along with the basis for its intervals and summary of maintenance and testing procedures, for protective relays, associated communication systems, voltage and current sensing devices, station batteries, and DC Control Circuitry; and 2) analyzed and standardized its practices to develop a standardized and detailed Maintenance and Testing program for UNWW facilities. | 2008-12-19 | 2009-07-02 | Agrees/Stipulates | WECC considered UNWW's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC200801418 | Settlement Agreement | During a Compliance Audit conducted on July 28, 2008, WECC determined that UNWW, as a Generator Owner (GO), was in violation of PRC-005-1 R2. UNWW did not provide documentation of its Protection System maintenance and testing program for more than 60 days following a request from its Regional Reliability Organization. During the audit, UNWW failed to provide the WECC Audit Team a comprehensive list of maintenance and testing records for UNWW facilities. UNWW provided a random sample of Protection System maintenance and testing; however, the WECC Audit Team determined these were not sufficient in detail. UNWW had previously submitted a Self-Certification on July 10, 2008, reporting that it was in compliance with the Standard. UNWW stated at the time of audit that it was unable to assemble the volume of testing records by the close of the audit. WECC determined that UNWW’s inability to provide sufficient evidence to demonstrate it has performed the maintenance and testing of its Protection System devices was a violation of the Standard. WECC determined UNWW had a violation of the Standard, because UNWW failed to demonstrate it conducted maintenance and testing of its Protection System devices as required by the Standard. UNWW did not provide documentation of its Protection System maintenance and testing program for more than 60 days following a request from its Regional Reliability Organization. The cause was a lack of compliance understanding on the importance and need of maintaining accurate, complete, and accessible records. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the audit, UNWW affirmed that it was performing basic maintenance and testing on its Protection System devices; however, it was unable to provide specific evidence for the majority of devices. Based on a conversation with UNWW’s reliability compliance program manager, WECC believed UNWW was conducting basic maintenance and testing of its Protection System devices, but was unable to provide evidence of testing as required by the Standard. The preventative maintenance was being performed as specified within the maintenance schedule, but lacked standardization across the District projects. | 8/10/2007 (when the Standard became mandatory and enforceable on UNWW) | 10/30/2009 (Mitigation Plan completion) | No penalty (for WECC200800976, WECC200801418, and WECC2014014151) | Compliance Audit | To mitigate this violation, UNWW: 1) implemented maintenance and testing within the intervals of the program previously described in the Mitigation Plan for PRC-005-1 R1; 2) created new and revised job plans that detail the various component steps that would require administrative time to implement in Facility Equipment Maintenance (FEM) database as maintenance crew time is dependent on available manpower and skill set at each project; and 3) validated preventative maintenance data tracking information using the state-of-the-art equipment maintenance database which was deployed at the district's operations center. | 2009-10-30 | 2010-01-04 | Agrees/Stipulates | WECC considered UNWW's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC2014014151 | Settlement Agreement | During a Compliance Audit conducted from July 21, 2014 through July 22, 2014, WECC determined that UNWW, as a Generator Owner (GO), was in violation of PRC-005-1 R2. The Audit Team determined that UNWW failed to provide documentation that it maintained and tested its Protection System devices within the defined intervals and to provide the date last tested and maintained because UNWW was unable to provide bookend dates to 44 applicable devices. Specifically, UNWW was unable to provide bookend dates for 24 of 276 relays (approximately 8.70%) and 20 of 83 Current Transformers (CTs) (approximately 24.1%). As a result of its examination, the Audit Team determined that UNWW was in violation of PRC-005-1 R2. Based on this review, WECC determined that UNWW was in violation of PRC-005-1 R2. WECC determined that UNWW failed to include documentation in its maintenance and testing program that all the Protection System devices were maintained and tested within the defined intervals and to provide the date last tested and maintained for all Protection System devices. As a result, WECC determined that UNWW was in violation of PRC-005-1 R2. UNWW failed to have evidence that Protection System devices were maintained and tested within the defined intervals for more than 15% of the applicable devices. The root cause is a misunderstanding regarding which protection system devices were in scope of PRC-005-1. UNWW added the devices in anticipation of PRC-005-2, which was thought to include exciter relays. UNWW now believes this was a misinterpretation that led to confusion. Under PRC-005-2 the applicability includes relays that protect the exciter transformer; the relays UNWW included protect the exciter but not the transformer. The relay CTs are on the load side of the transformer, thus it is protecting the integral components of the exciter. Fuses protect the exciter transformer. Since these devices were newly added to UNWW's PRC-005 Maintenance Program they believed they had a maintenance cycle to achieve the first maintenance since it was not possible to meet standards before they are defined. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, UNWW failed to provide documentation that all the Protection System devices were maintained and tested within the defined intervals and to provide the date last tested and maintained for all Protection System devices. This included maintenance and testing intervals and their basis, as well as a summary of maintenance and testing procedures for the instrument transformers. Testing of the Protection Systems help determine if the devices are reliable to limit the effects of disturbances in a system network. If there is no evidence that the devices were tested according to the program defined by the entity, the devices cannot be entrusted to interrupt disturbances that may damage the transmission system and/or generation plants. The affected devices were limited to approximately 8.70% of relays and approximately 24.1% of CTs. UNWW owns and operates six hydroelectric plants on the Columbia and Snake River System. These six plants have a peak generation of approximately 3,854 MW. The Protection System devices that were missing maintenance and testing dates did not have redundant controls in place. Further, UNWW stated it implemented its Protection System Maintenance and Testing Program for the majority of its devices | 8/10/2007 (when the Standard became mandatory and enforceable on UNWW) | 3/23/2015 (Mitigation Plan completion) | No penalty (for WECC200800976, WECC200801418, and WECC2014014151) | Compliance Audit | To mitigate this violation, UNWW: 1) included and tested the relays and CTs in its program as part of its preparation for version 2 of PRC-005; and 2) tested CTs with the unit on line to show they are within acceptable tolerances with continuity to the relays and tested the relays according to UNWW's PRC-005 procedure. | 2015-03-23 | 2015-06-10 | Agrees/Stipulates | WECC considered UNWW’s PRC-005 R2 compliance history in determining the disposition track. UNWW’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID WECC200801418. WECC considered UNWW’s PRC-005 R2 compliance history to be an aggravating factor.