## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Upper Great Plains Region (WAUW) | NCR05467 | WECC200901727 | Settlement Agreement | On October 29, 2009, WAUW submitted a Self-Report stating that as a Transmission Owner it was in violation of PRC-005-1 R2. Specifically, WAUW reported that during the transition to a new document management system, it discovered that records for monthly battery maintenance were missing at ten substations, and 13 of its Protection System devices had not been maintained/tested per the intervals of its maintenance and testing program. The root cause of this violation was inadequate work scheduling and record retention procedures. | PRC-005-1 | R2; R2.1; R2.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WAUW failed to maintain documentation of monthly battery maintenance at several substations, and failed to maintain/test 13 of its Protection System devices within the intervals of its maintenance and testing program. However, WAUW monitors all of its battery chargers and battery voltages via its Supervisory Control and Data Acquisition (SCADA) system. Due to the monitoring and alarm systems, most abnormalities in the batteries would trigger an alarm, immediately alerting WAUW of a problem. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WAUW) | 10/28/2009 (Mitigation Plan completion) | No penalty | Self-Report | To mitigate this violation, WAUW: 1) performed required battery maintenance and testing at all of its substations; 2) required all personnel responsible for tasks related to this Standard to attend a two-day compliance workshop sponsored by MRO to emphasize the importance of proper record keeping and work scheduling and WAUW's commitment to compliance; and 3) completed its transition to a computerized scheduling and document management system. | 2009-10-28 | 2010-03-05 | Agrees/Stipulates | WECC considered WAUW's internal compliance program (ICP) a to be a neutral factor in determining the disposition track. WECC considered WAUW's compliance history and determined there were no relevant instances of noncompliance.