## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2013012974 | Settlement Agreement | On September 20, 2013, TVA submitted a Self-Report stating that, as a Generator Operator, it was in violation of VAR-002-1.1b R3. TVA failed to notify its Transmission Operator (TOP) within 30 minutes of a status or capability change on each automatic voltage regulator (AVR). In preparation for its October 2013 Self-Certification submittal, TVA conducted a review of VAR-002 performance data from May 18, 2012 through August 26, 2013 for all generation facilities. During the review, TVA identified five instances in which it could not provide documentation that it notified the TOP within 30 minutes of an AVR status change at Brown’s Ferry Station Unit 3 (BFN3). The status changes involved changes between automatic and manual control and, in all instances, the AVR remained on-line. The five instances occurred on May 26, 2012 and May 27, 2012 when BFN3 was returning on-line after an outage for replacement of the AVR. In each instance, the operator was switching from automatic to manual or from manual to automatic to test operation of the AVR. The first four instances occurred on May 26, 2012, after a TVA operator toggled the AVR to manual and back to automatic. The TVA operator then toggled the AVR from manual to automatic without notifying the TOP of the changes in AVR status within 30 minutes as required by VAR-002-1.1b R3. The TVA operator’s actions occurred over a period of less than 2 minutes. The last instance occurred on May 27, 2012, when TVA changed the AVR from automatic to manual and back to automatic. TVA made proper notification to the TOP for the change from automatic to manual but failed to notify the TOP within 30 minutes of when TVA changed the AVR back to automatic approximately 79 minutes later as required by VAR-002-1.1b R3. The root cause of this violation was training and TVA staff’s failure to follow established procedures, which required notification to the TOP within 30 minutes of a change in the status of an AVR. | VAR-002-1.1b | R3; R3.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to notify its TOP within 30 minutes of changing BFN3’s AVR back to automatic voltage control mode could result in the TOP expecting BFN3’s AVR to be in a mode of operation that it was not. However, the AVR at BFN3 remained on-line in each instance, and TVA switched the AVR from automatic to manual and back to automatic within a few minutes, reducing the time that the TOP was unaware of the correct AVR status. When TVA failed to properly notify the TOP within 30 minutes, TVA was returning the AVR to automatic, the desired mode of operation. The TOP was aware that BFN3 was returning to service and was not at full output. During the issue, BFN3 had a generation output of between 120 and 295 MW, while BFN units 1 and 2 both had a generation output of more than 1,130 MW and AVRs operating in automatic voltage control mode. Therefore, there was a significant amount of generation at the site with the AVR in automatic voltage mode. No harm is known to have occurred. | 5/26/2012 (the first instance in which TVA failed to notify the TOP of a change in AVR status as required) | 5/27/2012 (the last instance in which TVA failed to notify the TOP of a change in AVR status as required) | No penalty (for SERC2013012974, SERC2013013260, SERC2015014921, SERC2016015698, and SERC2016015699) | Self-Report | To mitigate this violation, TVA: 1) performed a review of all TVA nuclear power group (NPG) operating instructions related to VAR-002 compliance and forwarded notated copies of applicable procedures to each site; 2) issued operations standing orders or other guidance as an interim measure to provide direction to NPG operators regarding VAR-002 compliance; 3) created a training presentation for NERC compliance awareness for NPG operations that explained employees' responsibilities and obligations to maintain NERC compliance and described lessons learned within the nuclear industry of confirmed violations of the NERC Reliability Standards; 4) reviewed and revised site procedures as necessary to ensure each treatment of generation resource status reinforced the notification content and timeframes that are consistent with VAR-002 requirements and TOP directions, and also document specific retention requirements for readings sheets for consistency across all three NPG sites; 5) revised its computer-based training module to ensure generating unit operators understand how to properly notify the TOP of both planned and unplanned AVR status changes; and 6) ensured all generating unit operator personnel had completed the revised training module. | 2016-08-31 | TBD | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the determination of the disposition track. TVA has a documented ICP, which it created in July 2008 in order to establish the structure of TVA's ICP. TVA annually conducts a review of its ICP and modifies it as necessary. TVA revised its ICP in April 2011 and October 2014. TVA maintains the ICP in a “Procedure Center” that is accessible to all employees. TVA’s documented ICP establishes the structure of its ICP, including the Reliability Standards Oversight Group (RSOG), the Reliability Standards Working Group (RSWG), and the Transmission Programs & Regulatory Compliance (TP&RC) group, and the relationships between those groups and the responsibilities of each group. The RSOG is composed of executives from TVA business units and provides guidance and oversight of TVA’s compliance program. The RSWG is composed of subject matter experts from TVA business units, and provides organization-specific direction and executes activities as directed by the RSOG. The TP&RC group is an internal, independent NERC compliance oversight organization within TVA that is separate from the business units responsible for the day-to-day execution activities and compliance with applicable Reliability Standards. TVA’s general manager of TP&RC is responsible for overseeing the ICP within TVA. The general manager of TP&RC reports directly to the senior vice president of transmission at TVA, who in turn has independent access to the TVA chief operating officer (COO) and the chief executive officer (CEO). TVA’s RSOG meets quarterly and provides oversight and subject matter expert resources needed for TVA to achieve and sustain its compliance with all applicable Reliability Standards. TVA’s RSWG meets monthly to review any emerging issues associated with compliance with applicable Reliability Standards, the status of any Reliability Standards in the development process, and the status of Reliability Standards applicable to TVA. The RSOG and RSWG meetings include discussions of training topics and issues. TVA’s TP&RC group conducts general training regarding compliance activities and specific training for subject matter experts occurs within the affected business units. TVA’s ICP does not address disciplinary actions against employees involved in violations of Reliability Standards, but TVA would handle such actions through its separate employee discipline policy. TVA’s ICP includes self-assessments to prevent recurrence of violations. Different business units use different methods to achieve this goal, including the use of independent staff for monitoring, second-party verification, and third-party vendors to provide performance assessments and reviews. The RSOG provides additional oversight and guidance to this process, and serves as forum to discuss the most effective practices to prevent recurrence of violations. TVA did not receive mitigating credit for self-reporting because the Self-Report was submitted during the self-certification period. SERC considered TVA’s VAR-002 R3 compliance history in determining the disposition track. TVA’s relevant prior noncompliance with VAR-002 R3 includes: NERC Violation IDs and SERC201000517 and SERC2011006541. SERC determined that TVA’s compliance history should not serve as a basis for aggravating the disposition track. Regarding NERC Violation ID SERC201000517, the failure occurred at a single plant and lasted for approximately one month, ending in January 2010. Regarding NERC Violation ID SERC2011006541, the failure occurred at a single plant and involved two AVRs tripping from automatic to manual and lasted approximately one and one-half hours in March 2011. In the current violation, the failure resulted from testing a single unit’s AVR during startup of a unit in May 2012 that was not involved in the prior noncompliances. The AVRs were not in automatic voltage control mode for a matter of minutes at a time in which the TOP was aware that the unit was returning to service and not operating at full output. The prior mitigating activities would not have prevented the instant violation.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2013013260 | Settlement Agreement | On December 13, 2013, TVA submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-003-1 R1.2. TVA failed to provide correct outage information daily to affected Balancing Authorities (BAs) and TOPs for scheduled generator outages and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) violation or a regional operating area limitation. From Friday, September 27, 2013 at 7:59 a.m., until Monday, September 30, 2013 at 10:00 a.m., TVA sent information to the NERC System Data Exchange (SDX), but the generator outage information was transmitted as null sets showing no generation outages. TVA transmitted all other information as expected. Entities that obtain TVA generation data from SDX, including Reliability Coordinators (RCs), BAs, TOPs, and market entities, thus received inaccurate outage information for TVA generators during this time. TVA BA and TOP system operators have access to outages through TVA’s consolidated outage portal application and various spreadsheets utilized in next-day planning. However, neighboring BAs and TOPs only had access to the incorrect future generation outage information through SDX. TVA had five generator units go into scheduled outages on September 27, 2013, the first day of the violation. These units included two fossil units totaling 1,325 MW that entered a three-month outage and three combustion turbine units totaling 255 MW that entered a two-week outage. Neighboring BAs and TOPs had received information regarding these five scheduled outages, including the planned start and stop dates of the outages, on the last successful transmittal of correct generator outage information on September 26, 2013. TVA provided daily outage information to affected BAs and TOPs showing null sets for all TVA generators during the violation. No other units entered or returned from an outage during the violation. TVA determined that this violation occurred because it made a change to a system upon which SDX depended without adequate testing. A bug in the new database resulted in a null set of data being returned by the query and passed to SDX. Once TVA discovered the issue on September 30, 2013, it repointed the process to the old database until the bug could be fixed in the new database, thereby ensuring that neighboring BAs and TOPs received outage information daily. | TOP-003-1 | R1; R1.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to provide correct scheduled outage information on a daily basis could have led TVA or a neighboring BA or TOP to approve transmission or generator outages based on the belief that certain generators within TVA’s TOP area were available when, in reality, that generation was unavailable. The system could then encounter heavy loading, outages, or other stressors, potentially leading to SOL or IROL violations. Further, by having a null set of generation outages during the violation, TVA or a neighboring BA or TOP could have relied on inaccurate data to sell transmission service across its lines, potentially selling more or less transmission service than was actually available. Nevertheless, the affected BAs and TOPs received notice of the scheduled outages of the five units on September 26, 2013, the day before those units went into outage, and had previously received notice of all other scheduled generator outages. TVA’s failure to provide daily scheduled outage information lasted for three days and took place over a weekend, during which time it would be unusual for TVA to review and approve longer-term outages, thus reducing the risk of an SOL or IROL violation. In addition, the TVA RC and neighboring RCs have options at their disposal to minimize both pre-contingency and post-contingency overloads on the system, including re-dispatch, reconfiguration, and the Transmission Loading Relief process. Affected BAs and TOPs had access to real-time information and visibility into real-time issues. In addition, operators routinely study outages using real-time data before taking equipment out of service. TVA’s BA and TOP system operators had ready access to accurate outage information through TVA’s consolidated outage portal application and various spreadsheets utilized in next-day planning. TVA did not approve any outages based on models with missing information. No harm is known to have occurred. | 9/27/2013 (when TVA failed to provide correct generation outage information daily to affected BAs and TOPs) | 9/30/2013 (when TVA resumed providing correct generation outage information daily to affected BAs and TOPs) | No penalty (for SERC2013012974, SERC2013013260, SERC2015014921, SERC2016015698, and SERC2016015699) | Self-Report | To mitigate this violation, TVA: 1) reappointed the process to the old database until the bug could be fixed in the new process; 2) remedied the bug by replacing a hard-coded value in a query within the database; 3) identified and implemented data quality alarms for the generation and transmission outage data that is passed to SDX, which will allow future errors of this nature to be caught and addressed in a timely manner; 4) developed a list of all data flows and applications whose availability have compliance implications, which will be reviewed with all application development staff and will be used to heighten sensitivity to application modifications; 5) identified applications and data flows which require an additional peer check prior to production modifications; and 6) integrated peer-checking into its existing change management process for certain mission critical applications, which will ensure that the proper system subject-matter experts are engaged in changes that have the potential to have reliability or regulatory impact. | 2014-03-05 | 2014-06-01 | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the determination of the disposition track. TVA has a documented ICP, which it created in July 2008 in order to establish the structure of TVA's ICP. TVA annually conducts a review of its ICP and modifies it as necessary. TVA revised its ICP in April 2011 and October 2014. TVA maintains the ICP in a “Procedure Center” that is accessible to all employees. TVA’s documented ICP establishes the structure of its ICP, including the Reliability Standards Oversight Group (RSOG), the Reliability Standards Working Group (RSWG), and the Transmission Programs & Regulatory Compliance (TP&RC) group, and the relationships between those groups and the responsibilities of each group. The RSOG is composed of executives from TVA business units and provides guidance and oversight of TVA’s compliance program. The RSWG is composed of subject matter experts from TVA business units, and provides organization-specific direction and executes activities as directed by the RSOG. The TP&RC group is an internal, independent NERC compliance oversight organization within TVA that is separate from the business units responsible for the day-to-day execution activities and compliance with applicable Reliability Standards. TVA’s general manager of TP&RC is responsible for overseeing the ICP within TVA. The general manager of TP&RC reports directly to the senior vice president of transmission at TVA, who in turn has independent access to the TVA chief operating officer (COO) and the chief executive officer (CEO). TVA’s RSOG meets quarterly and provides oversight and subject matter expert resources needed for TVA to achieve and sustain its compliance with all applicable Reliability Standards. TVA’s RSWG meets monthly to review any emerging issues associated with compliance with applicable Reliability Standards, the status of any Reliability Standards in the development process, and the status of Reliability Standards applicable to TVA. The RSOG and RSWG meetings include discussions of training topics and issues. TVA’s TP&RC group conducts general training regarding compliance activities and specific training for subject matter experts occurs within the affected business units. TVA’s ICP does not address disciplinary actions against employees involved in violations of Reliability Standards, but TVA would handle such actions through its separate employee discipline policy. TVA’s ICP includes self-assessments to prevent recurrence of violations. Different business units use different methods to achieve this goal, including the use of independent staff for monitoring, second-party verification, and third-party vendors to provide performance assessments and reviews. The RSOG provides additional oversight and guidance to this process, and serves as forum to discuss the most effective practices to prevent recurrence of violations. SERC considered TVA's compliance history and determined there were no relevant instances of noncompliance.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2015014921 | Settlement Agreement | On February 10, 2015, SERC sent TVA an audit detail letter notifying it of a Compliance Audit scheduled for May 11, 2015 through May 29, 2015. On May 11, 2015, TVA submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1.1b R3. TVA failed to notify the Transmission Operator (TOP) of changes in automatic voltage regulator (AVR) status within 30 minutes. In response to a SERC data request prior to the May 2015 Compliance Audit, TVA performed a review of AVR status changes for its coal, gas, and hydro generating plants and identified two instances of noncompliance. TVA’s Power Operations (non-nuclear) group does not have a formal process to periodically review AVR status compliance, which resulted in TVA not identifying the instances of noncompliance until it responded to the data request for the Compliance Audit. The violation occurred at Colbert Fossil Plant (COF) Unit 3. In this instance, generator operator log entries on January 31, 2013 indicated that TVA removed the AVR from service at approximately 11:00 a.m. to allow maintenance on the AVR and returned the AVR to service at approximately 2:00 p.m. Pursuant to VAR-002-1.1b R3, TVA should have notified the TOP within 30 minutes of returning the AVR to service. However, TVA had no log entries documenting the required TOP notifications. TVA routinely removes the AVRs from service for preventative maintenance and testing. TVA’s procedure for removing and returning the AVR to service contained instructions to perform TOP notification but did not include signoffs. The primary cause of this issue is human performance error for failure to follow the procedural steps. | VAR-002-1.1b | R3; R3.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to notify its TOP within 30 minutes of changing the COF Unit 3 AVR back to automatic voltage control mode could result in the TOP expecting COF Unit 3 to be in a mode of operation that it was not. However, TVA maintained its voltage schedule in this instance. In addition, the TVA TOP operating desks have alarm points for system voltage that would have prompted it to control system voltage if COF Unit 3 were causing voltage problems due to the AVR being off during the violation. COF Unit 3 is 209 MW and operates on the TVA system of approximately 34,000 MW, limiting the impact the unit could have during the occasion when its AVR was in the off position without proper notification to the TOP. No harm is known to have occurred. | 1/31/2013 (the first instance in which TVA failed to notify the TOP as a change in AVR status as required) | 1/31/2013 (when TVA notified the TOP of the change in AVR status) | No penalty (for SERC2013012974, SERC2013013260, SERC2015014921, SERC2016015698, and SERC2016015699) | Self-Report | To mitigate this violation, TVA: 1) revised the COF system operating procedure regarding removing and returning the voltage regulator to service to include signoff placeholders to document proper response to unplanned removal of the AVR from service and the notification requirement to the TOP; 2) revised the COF system operating procedure regarding unit operation with the voltage regulator in hand to include signoff placeholders to document proper response to unplanned removal of the AVR from service and the notification requirement to the TOP; 3) revised the COF annunciator response instruction to include signoff placeholders to document proper response for the notification to the TOP for general voltage regulator trip annunciation; 4) revised its operational communication and coordination standard process procedure for its power operations personnel; 5) revised its computer-based training module to ensure generating unit operators understand how to properly notify the TOP of both planned and unplanned AVR status changes; 6) reviewed and revised other Power Operations (non-nuclear) generating site-specific procedures for documenting actions taken for an AVR status change event; 7) ensured all generating unit operators have completed the revised training module; and 8) created a Problem Evaluation Report to document and track corrective actions to prevent recurrence. | 2016-08-31 | 2016-09-19 | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the determination of the disposition track. TVA has a documented ICP, which it created in July 2008 in order to establish the structure of TVA's ICP. TVA annually conducts a review of its ICP and modifies it as necessary. TVA revised its ICP in April 2011 and October 2014. TVA maintains the ICP in a “Procedure Center” that is accessible to all employees. TVA’s documented ICP establishes the structure of its ICP, including the Reliability Standards Oversight Group (RSOG), the Reliability Standards Working Group (RSWG), and the Transmission Programs & Regulatory Compliance (TP&RC) group, and the relationships between those groups and the responsibilities of each group. The RSOG is composed of executives from TVA business units and provides guidance and oversight of TVA’s compliance program. The RSWG is composed of subject matter experts from TVA business units, and provides organization-specific direction and executes activities as directed by the RSOG. The TP&RC group is an internal, independent NERC compliance oversight organization within TVA that is separate from the business units responsible for the day-to-day execution activities and compliance with applicable Reliability Standards. TVA’s general manager of TP&RC is responsible for overseeing the ICP within TVA. The general manager of TP&RC reports directly to the senior vice president of transmission at TVA, who in turn has independent access to the TVA chief operating officer (COO) and the chief executive officer (CEO). TVA’s RSOG meets quarterly and provides oversight and subject matter expert resources needed for TVA to achieve and sustain its compliance with all applicable Reliability Standards. TVA’s RSWG meets monthly to review any emerging issues associated with compliance with applicable Reliability Standards, the status of any Reliability Standards in the development process, and the status of Reliability Standards applicable to TVA. The RSOG and RSWG meetings include discussions of training topics and issues. TVA’s TP&RC group conducts general training regarding compliance activities and specific training for subject matter experts occurs within the affected business units. TVA’s ICP does not address disciplinary actions against employees involved in violations of Reliability Standards, but TVA would handle such actions through its separate employee discipline policy. TVA’s ICP includes self-assessments to prevent recurrence of violations. Different business units use different methods to achieve this goal, including the use of independent staff for monitoring, second-party verification, and third-party vendors to provide performance assessments and reviews. The RSOG provides additional oversight and guidance to this process, and serves as forum to discuss the most effective practices to prevent recurrence of violations. TVA did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered TVA’s VAR-002 R3 compliance history in determining the disposition track. TVA’s relevant prior noncompliance with VAR-002 R3 includes: NERC Violation IDs SERC201000517 and SERC2011006541. SERC determined that TVA’s compliance history should not serve as a basis for aggravating the disposition track. Regarding NERC Violation IDs SERC201000517, the failure occurred at a single plant and lasted for approximately one month, ending in January 2010. Regarding NERC Violation ID SERC2011006541, the failure occurred at a single plant and involved two AVRs tripping from automatic to manual and lasted approximately one and one-half hours in March 2011. In the current violation, the failure resulted from human error in following procedures that occurred approximately one and one-half years and 3 three years after TVA mitigated the most recent prior noncompliance. The prior mitigating activities would not have prevented the instant violation.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2016015698 | Settlement Agreement | On September 20, 2013, TVA submitted a Self-Report stating that, as a Generator Operator, it was in violation of VAR-002-1.1b R3 (NERC Violation ID SERC2013012974). During its review, SERC determined that the facts also represented a violation of VAR-002-1.1b R1 because TVA failed to operate each generator connected to the interconnected transmission system automatic voltage control regulator (AVR) in the automatic voltage control mode without notifying the Transmission Operator. In preparation for its October 2013 Self-Certification submittal, TVA conducted a review of VAR-002 performance data from May 18, 2012 through August 26, 2013 for all generation facilities. During the review, TVA identified three instances in which it could not provide documentation that it notified the TOP within 30 minutes of an AVR status change at Brown’s Ferry Station Unit 3 (BFN3). The status changes involved changes between automatic and manual control and, in all instances, the AVR remained on-line. It was determined that TVA had three reportable instances of R1 at BFN3. The three instances occurred on May 26, 2012 and May 27, 2012 when BFN3 was returning on-line after an outage for replacement of the AVR. In each instance, the operator was switching from automatic to manual or from manual to automatic to test operation of the AVR. The first two instances occurred on May 26, 2012, after a TVA operator twice toggled the AVR to manual and back to automatic. Pursuant to VAR-002-1.1b R1, TVA should have notified the TOP prior to changing the AVR status from automatic voltage control mode to manual each time. The TVA operator’s actions occurred over a period of less than 2 minutes. The third and last instance occurred on May 27, 2012, when TVA changed the AVR from automatic to manual and back to automatic. The root cause of this violation was TVA staff’s failure to follow established procedures, which required notification to the TOP prior to changing an AVR from automatic voltage control mode to a different mode. | VAR-002-1.1b | R1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to notify its TOP prior to changing BFN3’s AVR from automatic voltage control mode to manual could result in the TOP expecting BFN3’s AVR to be in a mode of operation that it was not. However, the AVR at BFN3 remained on-line in each instance, and TVA switched the AVR from automatic to manual and back to automatic within a few minutes, reducing the time that the TOP was unaware of the correct AVR status. The TOP was aware that BFN3 was returning to service and was not at full output. During the issue, BFN3 had a generation output of between 120 and 295 MW, while BFN units 1 and 2 both had a generation output of more than 1,130 MW and AVRs operating in automatic voltage control mode. Therefore, there was a significant amount of generation at the site with the AVR in automatic voltage mode. No harm is known to have occurred. | 5/26/2012 (the first instance in which TVA failed to notify the TOP of a change in AVR status as required) | 5/27/2012 (the last instance in which TVA failed to notify the TOP of a change in AVR status as required) | No penalty (for SERC2013012974, SERC2013013260, SERC2015014921, SERC2016015698, and SERC2016015699) | Self-Report | To mitigate this violation, TVA revised its computer-based training module for VAR-002 compliance to address R1 through R4. To prevent future occurrence of this violation, TVA will: 1) deploy incremental training on application of prior notifications and operator discretion for AVR status changes to all generating fleet operations departments; 2) complete incremental training discussions across the generating fleets in stand-down, pre-shift briefing, or similar meetings for all operators in each crew at each operating unit; and 3) review and revise TVA’s Business Unit, and site-specific procedures and instructions as necessary to address proper notifications under VAR-002 R1 | 6/5/2017 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the determination of the disposition track. TVA has a documented ICP, which it created in July 2008 in order to establish the structure of TVA's ICP. TVA annually conducts a review of its ICP and modifies it as necessary. TVA revised its ICP in April 2011 and October 2014. TVA maintains the ICP in a “Procedure Center” that is accessible to all employees. TVA’s documented ICP establishes the structure of its ICP, including the Reliability Standards Oversight Group (RSOG), the Reliability Standards Working Group (RSWG), and the Transmission Programs & Regulatory Compliance (TP&RC) group, and the relationships between those groups and the responsibilities of each group. The RSOG is composed of executives from TVA business units and provides guidance and oversight of TVA’s compliance program. The RSWG is composed of subject matter experts from TVA business units, and provides organization-specific direction and executes activities as directed by the RSOG. The TP&RC group is an internal, independent NERC compliance oversight organization within TVA that is separate from the business units responsible for the day-to-day execution activities and compliance with applicable Reliability Standards. TVA’s general manager of TP&RC is responsible for overseeing the ICP within TVA. The general manager of TP&RC reports directly to the senior vice president of transmission at TVA, who in turn has independent access to the TVA chief operating officer (COO) and the chief executive officer (CEO). TVA’s RSOG meets quarterly and provides oversight and subject matter expert resources needed for TVA to achieve and sustain its compliance with all applicable Reliability Standards. TVA’s RSWG meets monthly to review any emerging issues associated with compliance with applicable Reliability Standards, the status of any Reliability Standards in the development process, and the status of Reliability Standards applicable to TVA. The RSOG and RSWG meetings include discussions of training topics and issues. TVA’s TP&RC group conducts general training regarding compliance activities and specific training for subject matter experts occurs within the affected business units. TVA’s ICP does not address disciplinary actions against employees involved in violations of Reliability Standards, but TVA would handle such actions through its separate employee discipline policy. TVA’s ICP includes self-assessments to prevent recurrence of violations. Different business units use different methods to achieve this goal, including the use of independent staff for monitoring, second-party verification, and third-party vendors to provide performance assessments and reviews. The RSOG provides additional oversight and guidance to this process, and serves as forum to discuss the most effective practices to prevent recurrence of violations. SERC considered TVA’s VAR-002 R1 compliance history in determining the disposition track. TVA’s relevant prior noncompliance with VAR-002 R1 includes: NERC Violation ID SERC201000516. SERC determined that TVA’s compliance history should not serve as a basis for aggravating the disposition track. Regarding NERC Violation ID SERC201000516, the failure occurred at a single plant and lasted for approximately one month, ending in January 2010. In the current violation, the failure resulted from testing a single unit’s AVR during startup of a unit in May 2012 that was not involved in the prior noncompliances. The AVRs were not in automatic voltage control mode for a matter of minutes at a time in which the TOP was aware that the unit was returning to service and not operating at full output. The prior mitigating activities would not have prevented the instant violation.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2016015699 | Settlement Agreement | On February 10, 2015, SERC sent TVA an audit detail letter notifying it of a Compliance Audit scheduled for May 11, 2015 through May 29, 2015. On May 11, 2015, TVA submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1.1b R3 (NERC Violation ID SERC2015014921). During its review, SERC determined that the facts also represented a violation of VAR-002-1.1b R1 because TVA failed to operate each generator connected to the interconnected transmission system in the automatic voltage control mode without notifying the Transmission Operator. In response to a SERC data request prior to the May 2015 Compliance Audit, TVA performed a review of AVR status changes for its coal, gas, and hydro generating plants and identified two instances of noncompliance. TVA’s Power Operations (non-nuclear) group does not have a formal process to periodically review AVR status compliance, which resulted in TVA not identifying the instances of noncompliance until it responded to the data request for the Compliance Audit. The first instance occurred at Colbert Fossil Plant (COF) Unit 3. In this instance, generator operator log entries on January 31, 2013 indicated that TVA removed the AVR from service at approximately 11:00 a.m. to allow maintenance on the AVR and returned the AVR to service at approximately 2:00 p.m. Pursuant to VAR-002-1.1b R1, TVA should have notified the TOP prior to removing the AVR from service. The second instance occurred at COF Unit 1. In this instance, a generator operator log entry at 7:54 a.m. on November 20, 2014 indicated that TVA placed the AVR in the off position to allow maintenance on the AVR. TVA documented the TOP notification at 9:37 a.m. Pursuant to VAR-002-3 R1, TVA should have notified the TOP prior to placing the AVR in the off position. TVA returned the AVR to automatic at 10:34 a.m. following maintenance and notified the TOP of the change in AVR status at 10:43 a.m. (within 30 minutes as required by VAR-002-3 R3). At 6:40 p.m., TVA again placed the AVR in the off position without prior notification to the TOP, as required by VAR-002-3 R1. At 12:24 p.m. the following day, TVA notified the TOP that the AVR was in manual. The AVR remained in manual until shut down on December 12, 2014. TVA repaired the AVR during the outage. TVA routinely removes the AVRs from service for preventative maintenance and testing. TVA’s procedure for removing and returning the AVR to service contained instructions to perform TOP notification but did not include signoffs. The primary cause of this issue is human performance error for failure to follow the procedural steps. | VAR-002-1.1b | R1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to notify its TOP prior to changing COF Units 1 and 3 AVRs from automatic voltage control mode to manual could result in the TOP expecting COF Units 1 and 3 to be in a mode of operation that they were not. However, TVA maintained its voltage schedule in both instances. In addition, the TVA TOP operating desks have alarm points for system voltage that would have prompted it to control system voltage if COF Units 1 or 3 were causing voltage problems due to the AVRs being off during the violation. COF Unit 1 is 200 MW and COF Unit 3 is 209 MW, and both operate on the TVA system of approximately 34,000 MW, limiting the impact either unit could have during the separate occasions in which their AVRs were in the off position without proper notification to the TOP. No harm is known to have occurred. | 1/31/2013 (the first instance in which TVA failed to notify the TOP as a change in AVR status as required) and 11/20/2014 (the last instance in which TVA failed to notify the TOP of a change in AVR status as required) | 1/31/2013 (when TVA notified the TOP of the change in AVR status) and 11/21/2014 (when TVA notified the TOP of the change in AVR status) | No penalty (for SERC2013012974, SERC2013013260, SERC2015014921, SERC2016015698, and SERC2016015699) | Self-Report | To mitigate this violation, TVA: 1) retired all units at the COF site from service and no further revisions to site-level procedures for COF will be issued; and 2) revised its computer-based training module for VAR-002 compliance to address R1 through R4. To prevent future occurrence of this violation, TVA will: 1) deploy incremental training on application of prior notifications and operator discretion for AVR status changes to all generating fleet operations departments; 2) complete incremental training discussions across the generating fleets in stand-down, pre-shift briefing, or similar meetings for all operators in each crew at each operating unit; and 3) review and revise TVA’s Business Unit, and site-specific procedures and instructions as necessary to address proper notifications under VAR-002 R1 | 6/5/2017 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed TVA's internal compliance program (ICP) and considered it to be a mitigating factor in the determination of the disposition track. TVA has a documented internal compliance program (ICP), which it created in July 2008 in order to establish the structure of TVA's ICP. TVA annually conducts a review of its ICP and modifies it as necessary. TVA revised its ICP in April 2011 and October 2014. TVA maintains the ICP in a “Procedure Center” that is accessible to all employees. TVA’s documented ICP establishes the structure of its ICP, including the Reliability Standards Oversight Group (RSOG), the Reliability Standards Working Group (RSWG), and the Transmission Programs & Regulatory Compliance (TP&RC) group, and the relationships between those groups and the responsibilities of each group. The RSOG is composed of executives from TVA business units and provides guidance and oversight of TVA’s compliance program. The RSWG is composed of subject matter experts from TVA business units, and provides organization-specific direction and executes activities as directed by the RSOG. The TP&RC group is an internal, independent NERC compliance oversight organization within TVA that is separate from the business units responsible for the day-to-day execution activities and compliance with applicable Reliability Standards. TVA’s general manager of TP&RC is responsible for overseeing the ICP within TVA. The general manager of TP&RC reports directly to the senior vice president of transmission at TVA, who in turn has independent access to the TVA chief operating officer (COO) and the chief executive officer (CEO). TVA’s RSOG meets quarterly and provides oversight and subject matter expert resources needed for TVA to achieve and sustain its compliance with all applicable Reliability Standards. TVA’s RSWG meets monthly to review any emerging issues associated with compliance with applicable Reliability Standards, the status of any Reliability Standards in the development process, and the status of Reliability Standards applicable to TVA. The RSOG and RSWG meetings include discussions of training topics and issues. TVA’s TP&RC group conducts general training regarding compliance activities and specific training for subject matter experts occurs within the affected business units. TVA’s ICP does not address disciplinary actions against employees involved in violations of Reliability Standards, but TVA would handle such actions through its separate employee discipline policy. TVA’s ICP includes self-assessments to prevent recurrence of violations. Different business units use different methods to achieve this goal, including the use of independent staff for monitoring, second-party verification, and third-party vendors to provide performance assessments and reviews. The RSOG provides additional oversight and guidance to this process, and serves as forum to discuss the most effective practices to prevent recurrence of violations. TVA did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered TVA’s VAR-002 R1 compliance history in determining the disposition track. TVA’s relevant prior noncompliance with VAR-002 R1 includes: NERC Violation IDs SERC201000516. SERC determined that TVA’s compliance history should not serve as a basis for aggravating the disposition track. Regarding NERC Violation ID SERC201000516, the failure occurred at a single plant and lasted for approximately one month, ending in January 2010. In the current violation, the failure resulted from human error in following procedures that occurred approximately three years after TVA mitigated the most recent prior noncompliance. The prior mitigating activities would not have prevented the instant violation.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Desert Southwest Region (WALC) | NCR05461 | WECC200801291 | Settlement Agreement | During a Compliance Audit conducted from October 20, 2008 through October 24, 2008, WECC determined that WALC, as a Transmission Operator (TOP), was in violation of VAR-001-1 R4. Specifically, WALC failed to provide evidence that it directed its Generator Operators (GOPs) to operate in automatic voltage control mode (with the automatic voltage regulator (AVR) in service and controlling the voltage). Although WALC provided its GOPs with a voltage schedule and required all generators not exempt from the voltage schedule to operate with AVRs in service, WALC could not produce evidence that it specifically directed its GOPs to operate in automatic voltage control mode. The root cause of this violation was a lack of compliance processes. | VAR-001-1 | R4 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WALC failed to provide evidence of directing its GOPs to operate in automatic voltage control mode, WALC had: 1) specified a voltage schedule; 2) provided the voltage schedule to its GOPs; and 3) required its GOPs to operate generators with AVR in service. Additionally, WALC provided emails from four of the five GOPs confirming that they operated in automatic voltage control mode without the directive. Further, WALC could monitor all generator voltages and could have directed corrective action if necessary. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WALC) | 10/23/2008 (when WALC correctly directed its GOPs) | No penalty (for WECC200801291, WECC200801292, and WECC200810406) | Compliance Audit | To mitigate this violation, WALC: 1) directed its GOPs to operate in automatic voltage control mode; 2) updated its standard operating procedures to direct its GOPs to operate in automatic voltage control mode; and 3) distributed the updated operating procedures to all its GOPs. | 2009-05-08 | 2009-08-04 | Agrees/Stipulates | WECC reviewed WALC's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WALC's ICP is well documented; WALC has named and staffed an ICP oversight position; the ICP oversight position is supervised at a high level; the ICP oversight position has independent access to the chief executive officer or board of directors; WALC has dedicated sufficient staff and an adequate budget to the ICP; the ICP has the support and participation of senior management; the ICP includes appropriate and sufficient training for all staff; the ICP includes disciplinary action for employees involved in violations of the Reliability Standards if appropriate; the ICP has internal controls including self-assessment and self-enforcement to prevent recurrence of Reliability Standard violations. WECC considered WALC's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Desert Southwest Region (WALC) | NCR05461 | WECC200801292 | Settlement Agreement | During a Compliance Audit conducted from October 20, 2008 through October 24, 2008, WECC determined that WALC, as a Transmission Operator (TOP), was in violation of VAR-001-1 R6. Specifically, on June 5, 2008, a Generator Operator (GOP) notified WALC that a generating unit's automatic voltage regulator (AVR) failed. At that time, WALC did not direct the GOP to maintain or change either its voltage schedule or Reactive Power Schedule. Instead, WALC simply confirmed the GOP's statement that, until further notice, it would continue to operate with voltage control in "manual." The root cause of this violation was lack of organizational processes. | VAR-001-1 | R6; R6.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WALC did not provide a specific directive, at the time of the incident WALC was aware of the unit's status, could monitor the system’s voltage status in real time, and was cognizant of the system voltage requirements during an AVR failure. Under these circumstances, WALC could give the GOP directives as needed to maintain system voltage. No harm was known to have occurred. | 6/5/2008 (when WALC failed to appropriately direct the GOP) | 10/23/2008 (Mitigation Plan completion) | No penalty (for WECC200801291, WECC200801292, and WECC200810406) | Compliance Audit | To mitigate this violation, WALC: 1) informed its system operators of the requirement to appropriately direct GOPs; 2) revised its standard operating procedures to ensure that, when notified of an AVR failure, system operators appropriately direct GOPs to either maintain or change voltage; and 3) distributed this information to all system operators, along with a memo outlining the specific requirements. | 2009-05-08 | 2009-08-04 | Agrees/Stipulates | WECC reviewed WALC's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WALC's ICP is well documented; WALC has named and staffed an ICP oversight position; the ICP oversight position is supervised at a high level; the ICP oversight position has independent access to the chief executive officer or board of directors; WALC has dedicated sufficient staff and an adequate budget to the ICP; the ICP has the support and participation of senior management; the ICP includes appropriate and sufficient training for all staff; the ICP includes disciplinary action for employees involved in violations of the Reliability Standards if appropriate; the ICP has internal controls including self-assessment and self-enforcement to prevent recurrence of Reliability Standard violations. WECC considered WALC's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Desert Southwest Region (WALC) | NCR05461 | WECC200810406 | Settlement Agreement | On October 17, 2008, WALC submitted a Self-Report stating that, as a Planning Authority and Transmission Planner, it was in violation of TPL-004-0 R1. Specifically, WALC had not performed a valid annual Entity Planning Authority assessment between 2007 and 2008. WALC lacked a valid assessment because it failed to conduct near-term studies based on system configurations extending five years into the future. Additionally, WALC failed to evaluate the risks and consequences of the Category D contingencies. The root cause of this violation was WALC's incorrect interpretation of the requirement. | TPL-004-0 | R1; R1.2; R1.4 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Reliability Coordinator performed real-time studies, and WALC performed coordinated seasonal studies with a neighboring entity during the duration of the violation. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WALC) | 7/13/2009 (Mitigation Plan completion) | No penalty (for WECC200801291, WECC200801292, and WECC200810406) | Self-Report | To mitigate this violation, WALC: 1) completed its 2009 assessment in accordance with the requirement; 2) documented the assessment as required; 3) reported the assessment to WECC; and 4) contracted execution of the three-phase study plan for the development of a ten-year library of studies for each of the ten years for TPL-001 through TPL-004, so as to better baseline its assessments in the future. | 2009-07-13 | 2009-09-02 | Agrees/Stipulates | WECC reviewed WALC's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WALC's ICP is well documented; WALC has named and staffed an ICP oversight position; the ICP oversight position is supervised at a high level; the ICP oversight position has independent access to the chief executive officer or board of directors; WALC has dedicated sufficient staff and an adequate budget to the ICP; the ICP has the support and participation of senior management; the ICP includes appropriate and sufficient training for all staff; the ICP includes disciplinary action for employees involved in violations of the Reliability Standards if appropriate; the ICP has internal controls including self-assessment and self-enforcement to prevent recurrence of Reliability Standard violations. WACM did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of its upcoming Compliance Audit. WECC considered WALC's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC200901714 | Settlement Agreement | During a Compliance Audit conducted from September 28, 2009 through October 2, 2009, WECC determined that WACM, as a Planning Authority and a Transmission Planner, was in violation of TPL-001-0 R1. WACM's 2007 assessment lacked comprehensive heavy and light load studies on the near-term planning horizon, and did not include sufficient studies to determine system performance in the long-term planning horizon for light load conditions. The cause of this violation was a lack of compliance understanding. | TPL-001-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WACM failed to demonstrate that system performance met Category A conditions at all demand levels over the range of forecast demands. Such failure could have limited WACM's awareness of unanticipated impacts to its system from light load conditions. However, WACM's 2007 assessment did include 1) heavy summer operating studies to ensure reliability in the upcoming operating season, and 2) longer-term planning studies for the most critical load condition (heavy summer). Additionally, WACM's 2008 assessment met the requirement. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WACM) | 10/6/2008 (Mitigation Plan completion) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Compliance Audit | To mitigate this violation, WACM completed its 2008 assessment in accordance with the requirement. | 2008-10-06 | 2009-12-18 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC200901715 | Settlement Agreement | During a Compliance Audit conducted from September 28, 2009 through October 2, 2009, WECC determined that WACM, as a Planning Authority and a Transmission Planner, was in violation of TPL-002-0 R1. WACM's 2007 assessment lacked comprehensive heavy and light load studies on the near-term planning horizon, and did not include sufficient studies to determine system performance in the long-term planning horizon for light load conditions. The cause of this violation was a lack of compliance understanding. | TPL-002-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WACM failed to demonstrate that system performance met Category B conditions at all demand levels over the range of forecast demands. Such failure could have limited WACM's awareness of unanticipated impacts to its system from light load conditions. However, WACM's 2007 assessment did include 1) heavy summer operating studies to ensure reliability in the upcoming operating season, and 2) longer-term planning studies for the most critical load condition (heavy summer). Additionally, WACM's 2008 assessment met the requirement. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WACM) | 10/6/2008 (Mitigation Plan completion) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Compliance Audit | To mitigate this violation, WACM completed its 2008 assessment in accordance with the requirement. | 2008-10-06 | 2009-12-18 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC200901716 | Settlement Agreement | During a Compliance Audit conducted from September 28, 2009 through October 2, 2009, WECC determined that WACM, as a Planning Authority and a Transmission Planner, was in violation of TPL-003-0 R1. WACM’s 2007 and 2008 assessment did not include sufficient studies to determine system performance in the near-term and long-term planning horizon for light load conditions. Additionally, WACM's 2007 assessment lacked comprehensive heavy and light load studies on the near-term planning horizon. The cause of this violation was a lack of compliance understanding. | TPL-003-0 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WACM failed to demonstrate that system performance met Category C conditions at all demand levels over the range of forecast demands. Such failure could have limited WACM's awareness of unanticipated impacts to its system from light load conditions. However, WACM's 2007 and 2008 assessments did include 1) heavy summer operating studies to ensure reliability in the upcoming operating season, and 2) longer-term planning studies for the most critical load condition (heavy summer). Additionally, WACM's 2009 assessment met the requirement. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WACM) | 11/17/2009 (Mitigation Plan completion) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Compliance Audit | To mitigate this violation, WACM completed its 2009 assessment in accordance with the requirement. | 2009-11-17 | 2009-12-18 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC201002855 | Settlement Agreement | During a Spot Check conducted on April 18, 2010, WECC determined that WACM, as a Planning Authority and a Transmission Planner, was in violation of TPL-003-0 R2. During the Spot Check, WECC determined that WACM did not develop operating procedures necessary to meet the performance requirements of Category C until planned system upgrades could be placed in service, and therefore did not provide a written summary of its plans to achieve the required system performance throughout the planning horizon. The cause of this violation was less than adequate procedures prior to system upgrades. | TPL-003-0 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WACM failed to provide a written summary of its plans to achieve the required system performance, which could lead to operators taking inappropriate actions. However, this issue mainly concerned inadequate documentation. Although WACM did not have written operating procedures, WACM had distributed a transmission study which identified the need to shed load to its operators, and provided evidence that its operators were aware of the need to shed load under the conditions of the event. During an October 2009 event, WACM operators responded appropriately and prevented greater loss of load or cascading outages.When icing conditions created faults in WACM's system, WACM had to manually shed load in order to maintain acceptable voltage levels and system integrity. This action is expected in this condition and is supported as good utility practice, in part, by PER-001 R1, which requires Balancing Authorities and Transmission Operators to authorize operating personnel to implement real-time actions to maintain a stable and reliable BPS. | 6/18/2007 (when the Standard became mandatory and enforceable on WACM) | 10/7/2010 (when WACM placed planned system upgrades in service) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Spot Check | To mitigate this violation, WACM: 1) established a formal process to update procedures for system operators with information and procedures for all events identified in WACM's TPL studies; and 2) energized a 230 kV substation, thereby implementing the corrective action plan to achieve system performance. | 2010-10-07 | 2012-06-21 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC201102719 | Settlement Agreement | On February 16, 2011, WACM submitted a Self-Certification stating that, as Transmission Owner, it was in violation of PRC-005-1 R2. WECC reviewed the Self-Certification and determined that WACM failed to maintain and test batteries associated with a mobile capacitor bank within the intervals prescribed by WACM's maintenance and testing program. The scope of this violation included one battery bank of 111 battery banks - 0.9% of WACM's battery banks. This violation was caused by inadvertant omission of the mobile capacitor bank in WACM's Protection System Maintenance Plan. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WACM failed to maintain/test one battery bank housing four batteries within the interval defined in its maintenance and testing program. However, the battery chargers are alarmed for loss of AC power. Additionally, although the battery bank provides backup power to a protection scheme on a mobile capacitor bank, the protection scheme can, and does, function independently of the battery supply because the capacitor bank is also served from the station supply. Had the battery bank failed, the protection scheme could still have functioned properly. Had both the battery bank and service to the station failed, a transfer breaker protection would have operated to clear a fault. No harm was known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on WACM) | 2/25/2011 (Mitigation Plan completion) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Self-Certification | To mitigate this violation, WACM: 1) reviewed its maintenance plan and completion records for inclusion of all mobile Protection System devices; 2) replaced and tested the batteries on the mobile capacitor bank; and 3) included the one battery bank in its maintenance and testing program's scheduled maintenance plan. | 2011-02-25 | 2011-07-27 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WECC considered WACM’s PRC-005-1 R2 compliance history an aggravating factor in determining the disposition track. WACM’s relevant prior noncompliance with PRC-005-1 R2 included: NERC Violation ID: WECC200810343.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC2012011346 | Settlement Agreement | On October 31, 2012, WACM submitted a Self-Report stating that, as a Transmission Operator, it was in violation of TOP-007-WECC-1 R2. Specifically, WACM reported that on October 24, 2012, the Net Scheduled Interchange was overscheduled and exceeded a line's System Operating Limit (SOL) by two MW for roughly nine minutes. WECC reviewed the Self-Report and discussed concerns with WACM. WECC determined that WACM allowed the Net Scheduled Interchange to exceed the line's SOL when the Transmission Operator implemented its real-time schedule for the next hour on seven separate occassions. The issue was caused by WACM's failure to verify Net Scheduled Interchanges prior to implementation of realtime schedules. | TOP-007-WECC-1 | R2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk the reliability of the bulk power system. During the instances in scope, WACM failed to ensure that the Net Scheduled Interchange for power flow on a major transfer path did not exceed the line's SOL. Such failure could result in voltage stability issues and possible damage to equipment. However, WACM implemented compensating measures to decrease risk. Specifically, in each instance an alarm notified the operator of the exceedance, and the exceedance was resolved within nine minutes. Additionally, in each instance the actual flows on the path were well below the scheduled interchange and no overloading or voltage stability issues occurred before the exceedance was resolved. No harm was known to have occurred. | 6/17/2012 (the date of the first occurrence of the violation) | 10/30/2012 (the last occurrence of the violation) | No penalty (for WECC200901714, WECC200901715, WECC200901716, WECC201002855, WECC201102719, and WECC2012011346) | Self Report | To mitigate this violation, WACM: 1) updated its Energy Management System alarms to include audible and visible alarm notifying personnel of condition when next hour schedules exceed current operating limit, and requiring manual action to silence; and 2) upgraded its scheduling tool to display all path information for past, current, and next hour schedules on the main operating screen. | 2013-02-15 | 2013-04-11 | Agrees/Stipulates | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a mitigating factor in determining disposition track. WACM's ICP incorporates a number of best practices, promotes a culture of compliance, and indicates that WACM is committed to helping ensure the reliability of the BPS. WACM’s relevant prior noncompliance with TOP-007-WECC-1 R2 included NERC Violation ID: WECC2012009730, WECC considered WACM’s compliance history to be an aggravating factor in determining disposition track.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Sierra Nevada Region (WASN) | NCR05465 | WECC200801213 | Settlement Agreement | On November 4, 2008, WASN submitted a Self-Report stating that as a Planning Authority and Transmission Planner it was in violation of TPL-003-0 R1. Specifically, WASN reported it had not performed planning studies for each year of near-term and long-term planning horizons as required by TPL-003-0 R1.2. The cause of this issue was a lack of compliance understanding. | TPL-003-0 | R1; R1.2 | High | Not Specified | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WASN failed to conduct studies for the near and long-term planning horizons. Nevertheless, WASN periodically performed planning studies to ensure the development of reliable systems that meet specified performance requirements. In its Self-Reports for these violations, WASN stated that it performs transmission planning studies in response to system configuration changes to its system or in response to customers requesting interconnection or transmission services. WASN also stated that it performs transmission planning studies whenever operating conditions change due to generation expansion or load growth on the interconnected system that affect WASN’s system. WASN violated this Standard because these studies did not adequately address the near- and long-term planning horizons. For these reasons, and because no harm was known to have occurred, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable on WASN) | 2/1/2009 (when WASN's 2008 assessment was approved) | No penalty (for WECC200801213, WECC200801214, and WECC200801215) | Self-Report | To mitigate this violation, WASN completed its 2008 assessment, which included all required studies and demonstrated that WASN's system met performance requirements of Category C. | 2009-02-01 | 2009-02-24 | Agrees/Stipulates | WECC reviewed WASN's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. Upon undertaking the actions outlined in the Mitigation Plan, WASN took voluntary corrective action to remediate this violation. WECC considered WASN's compliance history and determined there were no relevant instances of noncompliance. .
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Sierra Nevada Region (WASN) | NCR05465 | WECC200801214 | Settlement Agreement | On November 4, 2008, WASN submitted a Self-Report stating that as a Planning Authority and Transmission Planner it was in violation of with TPL-002-0 R1. Specifically, WASN reported it had not performed planning studies for each year of near-term and long-term planning horizons as required by R1.2 of TPL-002-0. The cause of this issue was a lack of compliance understanding. | TPL-002-0 | R1; R1.2 | High | Not Specified | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WASN failed to conduct studies for the near and long-term planning horizons. Nevertheless, WASN periodically performed planning studies to ensure the development of reliable systems that meet specified performance requirements. In its Self-Reports for these violations, WASN stated that it performs transmission planning studies in response to system configuration changes to its system or in response to customers requesting interconnection or transmission services. WASN also stated that it performs transmission planning studies whenever operating conditions change due to generation expansion or load growth on the interconnected system that impact WASN’s system. WASN violated this Standard because these studies did not adequately address the near and long-term planning horizons. For these reasons, and because no harm was known to have occurred, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable on WASN) | 2/1/2009 (when WASN's 2008 assessment was approved) | No penalty (for WECC200801213, WECC200801214, and WECC200801216) | Self-Report | To mitigate this violation, WASN completed its 2008 assessment, which included all required studies and demonstrated that WASN's system met performance requirements of Category B. | 2009-02-01 | 2009-02-24 | Agrees/Stipulates | WECC reviewed WASN's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. Upon undertaking the actions outlined in the Mitigation Plan, WASN took voluntary corrective action to remediate this violation. WECC considered WASN's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Sierra Nevada Region (WASN) | NCR05465 | WECC200801215 | Settlement Agreement | On November 4, 2008, WASN submitted a Self-Report stating that as a Planning Authority and Transmission Planner it was in violation of with TPL-001-0 R1. Specifically, WASN reported it had not performed planning studies for each year of near-term and long-term planning horizons as required by R1.2 of TPL-001-0. The cause of this issue was a lack of compliance understanding. | TPL-001-0 | R1; R1.2 | High | Not Specified | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WASN failed to conduct studies for the near and long-term planning horizons. Nevertheless, WASN periodically performed planning studies to ensure the development of reliable systems that meet specified performance requirements. In its Self-Reports for these violations, WASN stated that it performs transmission planning studies in response to system configuration changes to its system or in response to customers requesting interconnection or transmission services. WASN also stated that it performs transmission planning studies whenever operating conditions change due to generation expansion or load growth on the interconnected system that impact WASN’s system. WASN violated this Standard because these studies did not adequately address the near and long-term planning horizons. For these reasons, and because no harm was known to have occurred, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable on WASN) | 2/1/2009 (when WASN's 2008 assessment was approved) | No penalty (for WECC200801213, WECC200801214, and WECC200801217) | Self-Report | To mitigate this violation, WASN completed its 2008 assessment, which included all required studies and demonstrated that WASN's system met performance requirements of Category A. | 2009-02-01 | 2009-02-23 | Agrees/Stipulates | WECC reviewed WASN's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. Upon undertaking the actions outlined in the Mitigation Plan, WASN took voluntary corrective action to remediate this violation. WECC considered WASN's compliance history and determined there were no relevant instances of noncompliance.