## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | US Bureau of Reclamation (USBR) | NCR05441 | WECC2015014589 | Settlement Agreement | On January 26, 2015, USBR submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-023-1 R1. Specifically, USBR reported that during an internal review it discovered that settings for 12 relays on 5 transmission lines did not incorporate line loadability fault tolerance margins as required by R1.1. Upon further review and discussion between USBR and WECC, the actual scope of this violation concerned only 7 relays on 5 transmission lines. The root cause of this issue was lack of internal controls regarding evaluation of relay loadability. This violation began July 1, 2010, when the Standard became mandatory and enforceable on USBR, and ended October 6, 2015, when USBR changed the last relay setting in accordance with R1.1. | PRC-023-1 | R1; R1.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, USBR failed to set seven applicable relays in accordance with R1.1 of the Reliability Standard. Such failure increased the risk of inadvertent tripping of the associated breakers, leading to potential loss of the lines. One of the relays in scope was associated with a Major WECC Transfer Path with a System Operating Limit (SOL) transfer limit of 4,250 MW. Nevertheless, the scope of this violation was limited to 7 out of 81 relays, or approximately only 9% of USBR’s applicable relays. No misoperations occurred on the lines during the period in question, and no harm is known to have occurred. | 7/1/2010 (when the Standard became mandatory and enforceable on USBR) | 10/6/2015 (when USBR changed the last relay setting in accordance with R1.1) | No penalty | Self-Report | To mitigate this violation, USBR: 1) established “relay setting package” whereby relays applicable to this Reliability Standard will meet sub-requirement criteria by default; 2) evaluated the relays in scope; 3) coordinated relay replacement and scheduled outages with the neighboring entity; and 4) completed relay replacement and associated commissioning. | 7/28/2016 | 2016-11-07 | Agrees/Stipulates | WECC did not review USBR's internal compliance program when determining disposition method. USBR did not receive mitigating credit for self-reporting because the Self-Report was submitted during the Self-Certification period. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the NERC and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. USBR is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for the this violation. WECC considered USBR's PRC-023-1 R1 compliance history in determining the disposition track. USBR's relevant prior noncompliance with PRC-023-1 R1 includes: NERC Violation ID WECC2012011525. WECC considered USBR's PRC-023-1 R1 compliance history to be an aggravating factor in the disposition determination.