## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2014013589 | Settlement Agreement | On January 18, 2014, PGE submitted a Self-Certification stating that as a Transmission Owner, Distribution Provider, and Generator Owner, it was in violation of PRC-005-1 R2. WECC reviewed the Self-Certification, discussed details of the issue with PGE, and requested additional evidence. PGE provided documentation for its Protection System Maintenance and Testing Program (PSMP), including an “Attachment G Supplement” summarizing relevant maintenance and testing activity. PGE failed to provide documentation that all Protection System devices were maintained and tested within the defined intervals. Upon review of this documentation, and as a result of subsequent data requests and multiple discussions, WECC determined that the scope of this issue included the following locations and devices: Bethel-Market: Missed maximum interval for transfer-trip module testing (three circuits) Orenco-Reedville: Missed maximum interval for transfer-trip module testing Murrayhill-St. Mary's: Missed maximum interval for transfer-trip module testing Beaver Plant: Missed maximum interval for one battery Port Westward: Incomplete test records for one battery and associated charger Port Westward: Incomplete test records for ten instrument transformers Pelton Unit #2: Missed maximum interval for one instrument transformer Tucannon River: Missed maximum interval for one battery and associated charger Boardman Plant: Missed maximum interval for one battery Coyote Springs: Missed maximum interval for one protective relay Glendoveer: Missed maximum interval for three CT/PT devices Gresham: Incomplete test records for three CT/ PT devices Gresham: Missed maximum interval for one battery Shute: Incomplete test records for two CT/PT devices Shute: Missed maximum interval for two batteries Alder: Missed maximum interval for one battery Orenco: Missed maximum interval for one segment of control circuitry The scope of this issue involved approximately one percent of PGE's applicable Protection System devices. Given the disparate locations, devices, and causes identified over the course of WECC’s evaluation of this violation, WECC determined the root cause was a systemic issue concerning consistent implementation of PGE’s PSMP. | PRC-005-1 | R2; R2.1; R2.2 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PGE failed to perform maintenance and testing of all applicable devices in accordance with its PSMP. Such failure could result in undetected degradation and/or malfunction of the devices. The scope of this issue involved 34 out of 3,632 devices, which represented roughly one percent of PGE’s applicable devices. None of the devices in scope failed over the course of the violation duration, and none of the devices were overdue for testing by more than one maximum interval. PGE consistently and continuously remediated this issue by testing each device as it was discovered. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on PGE) | 6/15/2016 (Mitigation Plan completion) | 26000 | Self-Certification | To mitigate this violation, PGE: 1) tested all of the devices in scope; 2) performed a thorough review of applicable devices to confirm test records were consistent and complete; 3) revised documented methodology to ensure proper classification of generation plant batteries; 4) entered corrections in its work management system for previously miscategorized devices, ensuring timely, automatic generation of future work orders; 5) revised work orders to require engineering review of test results, promoting consistent retention of documentation; 6) revised PSMP and associated procedures to establish documentation practices, specifically proper retention, and storage of maintenance records; 7) eliminated duplicative lists of devices to ensure future maintenance/testing activity is scheduled as determined by a single source (PGE’s work management system); and 8) conducted formal training to ensure documentation practices are understood by requisite staff. | 2016-06-15 | 2016-10-15 | Agrees/Stipulates | WECC reviewed PGE's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. PGE self-reported the violation, however, WECC did not apply mitigating credit because the Self-Report was submitted during the Self-Certification period. WECC considered PGE’s PRC-005 R2 compliance history to be an aggravating factor in the penalty determination. PGE had two previous violations of this Standard and Requirement, given Violation IDs: WECC200800858 and WECC201102539. WECC considered PGE's lack of detective controls an aggravating factor. The violation duration was 3,285 days, and PGE did not have any detective controls in place that could have helped identify the issues sooner.