## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Shiloh Wind Project 2, LLC (SWPII) | NCR10292 | WECC2016015506 | Settlement Agreement | On February 1, 2016, SWPII submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1a R2. Specifically, SWPII reported that during an internal gap analysis with a third party, it discovered it had failed to consistently monitor voltage, maintain generator voltage or Reactive Power, or make notifications to the Transmission Operator (TOP) when the generator voltage has traveled outside of the voltage schedule. Although SWPII has been monitoring its voltage more regularly since it discovered this violation, WECC considers the issue to be ongoing until SWPII installs the appropriate monitoring and alarming equipment. The root cause of this violation was a lack of internal controls regarding system studies under low or no-load conditions that caused high voltage. | VAR-002-1a | R2; R2.1 | Medium | Moderate | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SWPII failed to consistently monitor voltage, and therefore did not maintain or make notifications to the TOP when the generator voltage traveled outside of the voltage schedule. During the time SWPII was not monitoring voltages, the interconnecting TOP made requests to control voltage and SWPII responded accordingly. As a compensating control, SWPII conducted an internal investigation after the TOP called SWPII, asking if it could adjust its voltage inside the voltage schedule. As a detective control, SWPII’s TOP was monitoring voltage at the interconnection point and would notify SWPII when it was not within its voltage schedule. No harm is known to have occurred. | 1/9/2009 (when SWPII registered as a GOP) | present | 54000 | Self-Report | To mitigate this violation, SWPII will: 1) reconfigure capacitor bank systems to operate in accordance with the voltage set point at SWPII; 2) implement controls and telemetry so that the operations control center (OCC) can operate SWPII appropriately; 3) transmit voltage data from SWPII to the OCC; 4) monitor voltage and alarm on voltage deviations 24/7 at the OCC on the Monarch Energy Management System; 5) establish protocols for operations and switching; and 6) refresh training on communication of VAR-002-4 R2 with OCC staff. | 4/21/2017 (approved completion date) | TBD | Admits | WECC reviewed SWPII's compliance history and determined there were no relevant instances of noncompliance. As of the issue date of SWPII’s notice of expedited settlement agreement, the violation duration was at least 2,933 days, and is ongoing. SWPII did not have any detective controls in place that could have helped identify this violation sooner to lessen the violation duration and thereby lessen the risk. WECC applied an aggravating factor and escalated the disposition treatment to an expedited settlement with a penalty.
Western Electricity Coordinating Council (WECC) | Shiloh III Wind Project, LLC. (SIIIW) | NCR11232 | WECC2016015507 | Settlement Agreement | On February 1, 2016, SIIIW submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-1.1b R2. Specifically, SIIIW reported that during an internal gap analysis with a third party, it discovered it had failed to consistently monitor voltage, maintain generator voltage or Reactive Power, or make notifications to the Transmission Operator (TOP) when the generator voltage has traveled outside of the voltage schedule. Although SIIIW has been monitoring its voltage more regularly since it discovered this violation, WECC considers the issue to be ongoing until SIIIW installs the appropriate monitoring and alarming equipment. The root cause of this violation was a lack of internal controls regarding system studies under low or no-load conditions that caused high voltage. | VAR-002-1.1b | R2; R2.1 | Medium | Moderate | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SIIIW failed to consistently monitor voltage, and therefore did not maintain or make notifications to the TOP when the generator voltage traveled outside of the voltage schedule. During the time SIIIW was not monitoring voltages, the interconnecting TOP made requests to control voltage and SIIIW responded accordingly. As a compensating control, SIIIW conducted an internal investigation after the TOP called SIIIW, asking if it could adjust its voltage inside the voltage schedule. As a detective control, SIIIW’s TOP was monitoring voltage at the interconnection point and would notify SIIIW when it was not within its voltage schedule. No harm is known to have occurred. | 5/18/2012 (when SIIIW registered as a GOP) | present | 54000 | Self-Report | To mitigate this violation, SIIIW will: 1) reconfigure capacitor bank systems to operate in accordance with the voltage set point at SIIIW; 2) implement controls and telemetry so that the Operations Control Center (OCC) can operate SIIIW appropriately; 3) Transmit voltage data from SIIIW to the OCC; 4) monitor voltage and alarm on voltage deviations continuously at the OCC on the Monarch Energy Management System; 5) establish protocols for operations and switching; and 6) refresh training on communication of VAR-002-4 R2 with OCC staff. | 4/21/2017 (approved completion date) | TBD | Admits | WECC reviewed SIIIW's compliance history and determined there were no relevant instances of noncompliance. As of the issue date of SIIIW’s notice of expedited settlement agreement, the violation duration was at least 1,708 days, and is ongoing. SIIIW did not have any detective controls in place that could have helped identify this violation sooner to lessen the violation duration and thereby lessen the risk. WECC applied an aggravating factor and escalated the disposition treatment to an expedited settlement with a penalty.