## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2013012135 | Settlement Agreement | On March 20, 2013, BPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1 R2. Specifically, BPA identified and reported that seven of its relays were incorrectly categorized in its work management system and had been tested beyond the intervals prescribed by BPA’s Protection System Maintenance and Testing Program (PSMP). On December 3, 2014, BPA identified and reported an additional issue with this Standard and Requirement. Specifically, BPA reported that during its annual Self-Certification review, BPA discovered that it failed to perform one or more monthly battery inspections at 11 of its substations between May 2014 and September 2014. BPA expanded the scope of its mitigating activities for this violation to include this discovery. This issue involved 65 out of 376 batteries and 7 out of 7,856 relays, which comprised less than 5% of BPA’s applicable devices. The root cause of this violation was less than adequate controls to ensure 1) applicable devices were entered correctly in the work management system, and 2) inspection frequency was communicated to, and understood by, field personnel. | PRC-005-1 | R2; R2.1 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BPA failed to maintain and test Protection System devices within the intervals prescribed in its PSMP. Such failure could have limited BPA’s awareness of the working order of its Protection System devices. However, all devices included in scope of this issue were tested regularly, if not within the specified intervals, and have since been maintained and tested. No harm is known to have occurred. | 11/30/2008 (the earliest date in which relays in scope were overdue for testing) | 8/14/2015 (Mitigation Plan completion) | No penalty (for WECC2013012135, WECC2014014021, WECC2015014760, WECC2015015392, and WECC2016015455) | Self-Report | To mitigate this violation, BPA: 1) performed overdue maintenance and testing on the relays; 2) performed internal review to verify extent of condition and validate accuracy of assigned intervals; 3) validated relay manufacturer and model data in the work management system; 4) re-categorized the relays in scope in its work management system to ensure future testing is performed per the appropriate interval; 5) modified and implemented its process and procedures for entering relay groups into the work management system to ensure timely and accurate designation of categories; 6) verified that the intervals were set correctly; 7) developed a report to improve visibility of pending battery inspections; and 8) implemented revised process and battery inspection report, and communicated revisions with personnel responsible for battery inspections. | 2015-08-14 | 2015-11-02 | Does Not Contest | WECC reviewed BPA's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA's ICP features measureable compliance performance targets, which contribute to BPA's practice of consistent self-reporting. BPA had two previous violations of this Standard and Requirement, given Violation IDs: WECC201103045 and WECC2013013091. WECC considered BPA's compliance history to be an aggravating factor. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for these violations.
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2014014021 | Settlement Agreement | On June 25, 2014, BPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of FAC-501-WECC-1 R3. BPA reported that during a quality check of internal documentation concerning this requirement, it discovered that the “Oil Quality Test” for a transformer associated with a WECC Major Transfer Path was not completed prior to closing a work order, as required by its Transmission Maintenance and Inspection Plan (TMIP). Following discovery of this issue, BPA conducted an internal review and identified additional instances in which maintenance tasks prescribed in its TMIP were either not completed, or not completed within the required interval. The scope of this violation eventually included 31 transformers and 3 circuit breakers. This violation reflected a systemic failure to fully and timely implement tasks prescribed in BPA’s TMIP and involved multiple root causes, including: human error; insufficient training; and less than adequate controls to ensure accurate data retention during BPA’s transition to a new work management system. | FAC-501-WECC-1 | R3 | Medium | High | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BPA failed to perform all maintenance tasks required by its TMIP. Such failure could have limited BPA’s awareness of the working order of the devices in scope. However, had overdue maintenance resulted in unanticipated degradation or failure of any of the equipment in scope, BPA’s Energy Management System (EMS) would have resulted in an alarm. No equipment failure occurred as a result of the missed maintenance tasks during the period in question, and no harm was known to have occurred. Additionally, BPA had preventive controls in place throughout the duration of this issue, including a work management system to generate work orders with built-in procedures, which BPA used to track and schedule TMIP-related tasks. BPA also conducted internal reviews of all documentation prior to closing out work orders, and performed annual random sample reviews of the documentation as a compliance quality check. | 7/1/2011 (when FAC-501-WECC-1 became mandatory and enforceable on BPA) | 5/15/2016 (Mitigation Plan completion) | No penalty (for WECC2013012135, WECC2014014021, WECC2015014760, WECC2015015392, and WECC2016015455) | Self-Report | To mitigate this violation, BPA: 1) performed an internal root cause analysis to identify deficiencies in current processes, and solutions to such deficiencies; 2) finalized the oil test sub tasks on diagnostic maintenance for the transformer; 3) reviewed and modified all maintenance standards; 4) created a list of all incomplete TMIP-related tasks to determine the scope of this violation; 5) completed all TMIP-related tasks included in the scope of this violation; and 6) defined procedures for data entry to ensure timely and accurate data will be captured in its work management system; and 7) implemented pocesses, procedures, and trainings for data entry into work tracking system to ensure accurate and timely data collection. | 2016-05-15 | 2016-06-23 | Does Not Contest | WECC reviewed BPA's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA's ICP features measureable compliance performance targets, which contribute to BPA's practice of consistent self-reporting. BPA had one previous violation of this Standard and Requirement, given Violation ID: WECC2012010063, and two previous violations of Standard PRC-STD-005, given Violation IDs: WECC200901299 and WECC200901405. WECC considered BPA's compliance history to be an aggravating factor. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for these violations.
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015014760 | Settlement Agreement | On March 20, 2015, BPA submitted a Self-Report stating that, as a Transmission Operator, it was in violation of MOD-029-1a R2. Specifically, BPA reported that it stopped using outage-informed Total Transfer Capability (TTC) values to calculate Available Transfer Capability (ATC) on an ATC Path, as required in the path’s allocation agreement. As a result, BPA’s TTC values continuously reflected an All Lines in Service (ALIS) condition, and did not take into account system outage conditions. The root cause of this issue was less than adequate training regarding TTC values during outages. | MOD-029-1a | R2; R2.6 | Lower | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BPA failed to use outage-informed TTC values, and therefore failed to allocate TTC values as specified in its contractual agreement with another entity during system outage conditions. Such failure could have effected a mismatch between expected and actual ATC on the Path. However, as a preventive control, BPA keeps physical and electronic copies of subject matter expert (SME)-approved desk level procedures available at all times. Additionally, no curtailments were initiated as a result of this violation and no harm was known to have occurred. | 11/3/2014 (when BPA stopped issuing outage-informed TTCs) | 1/21/2016 (Mitigation Plan completion) | No penalty (for WECC2013012135, WECC2014014021, WECC2015014760, WECC2015015392, and WECC2016015455) | Self-Report | To mitigate this violation, BPA: 1) identified which paths require manual intervention to derive outage-informed TTC values; 2) developed and tested solutions to calculate outage-informed TTC values; 3) updated desk procedure to ensure proper reference material is available during outages; and 4) trained relevant staff regarding the updates. | 2016-01-21 | 2016-10-03 | Does Not Contest | WECC reviewed BPA's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA's ICP features measureable compliance performance targets, which contribute to BPA's practice of consistent self-reporting. BPA had one previous violation of this Standard and Requirement, given Violation ID: WECC201102885. WECC considered BPA's compliance history to be an aggravating factor. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for these violations.
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015015392 | Settlement Agreement | On December 4, 2015, BPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1.1b R2. Specifically, BPA reported that it missed the maximum maintenance interval of a single relay by roughly four months. One transformer relay with 13 child relays had been flagged in BPA's asset register and work management system as being not subject to PRC-005-1 requirements based on the description of the transformer having only one winding greater than 100 kV. However, a BPA field worker was scheduling maintenance on the equipment and noticed that the transformer has two windings greater than 100 kV. The root cause of this issue was human error; the relay was miscategorized in BPA’s work management system because a technician believed it had a single winding greater than 100 kV, and was therefore not subject to PRC-005. | PRC-005-1.1b | R2 | Lower | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BPA failed to test and maintain a single relay within the interval prescribed in its Protection System Maintenance Program (PSMP). Such failure could have limited BPA’s awareness of the working order of the device. However, this issue was limited to a single, miscategorized device, which has since been maintained and tested. BPA identified the issue in a relatively short time frame, which WECC considered an indication of good training practices and detective controls. No harm was known to have occurred. | 12/4/2014 (when maintenance became past due) | 4/1/2015 (when the maintenance interval changed to six years for the relay in scope under PRC-005-2) | No penalty (for WECC2013012135, WECC2014014021, WECC2015014760, WECC2015015392, and WECC2016015455) | Self-Report | To mitigate this violation, BPA: 1) performed maintenance and testing on the relay; 2) corrected the category of the device in its work management system; and 3) conducted an internal review to determine the extent of condition for this issue, which resulted in identification and correction of one additional miscategorized device. The additional device was not overdue for maintenance in accordance with BPA’s PSMP. | 2015-11-12 | 2016-08-29 | Does Not Contest | WECC reviewed BPA's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA's ICP features measureable compliance performance targets, which contribute to BPA's practice of consistent self-reporting. BPA had two previous violations of this Standard and Requirement, given Violation IDs: WECC201103045, WECC2013013091, and WECC2013012135. WECC considered BPA's compliance history to be an aggravating factor. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for these violations.
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015455 | Settlement Agreement | On January 7, 2016, BPA submitted a Self-Report stating that, as a Transmission Service Provider, it was in violation of MOD-001-1a R3. Specifically, BPA reported that during a recent revision to its Available Transfer Capability Implementation Document (ATCID), it had mistakenly removed criteria used to determine when an outage impacts daily and/or monthly Total Transfer Capability (TTC) calculations. The root cause of this issue was a lack of internal controls regarding documentation of the ATCID. | MOD-001-1a | R3; R3.6.1; R3.6.2 | Medium | Moderate | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BPA failed to include a description for how outages are considered in TTC calculations, particularly the criteria BPA uses to determine when at outage impacts daily and/or monthly calculations. Such failure limited awareness of BPA’s available transmission system capability, and could have prevented a customer’s ability to validate BPA’s ATC calculations for economic purchase and dispatch of power. However, this issue largely concerned documentation, and no harm was known to have occurred. | 6/1/2015 (when BPA removed the criteria from its ATCID) | 12/7/2015 (when BPA revised its ATCID to include the criteria) | No penalty (for WECC2013012135, WECC2014014021, WECC2015014760, WECC2015015392, and WECC2016015455) | Self-Report | To mitigate this violation, BPA: 1) revised its ATCID to include mistakenly-removed criteria, specifically, BPA’s methodology for incorporating daily/monthly outages in its TTC calculations; and 2) designated a single point of contact to coordinate future revisions to the ATCID. | 2016-10-04 | 2016-11-22 | Does Not Contest | WECC reviewed BPA's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA's ICP features measureable compliance performance targets, which contribute to BPA's practice of consistent self-reporting. BPA had three previous violations of this Standard and Requirement, given Violation IDs: WECC201102932, WECC2014014494, and WECC2015014911. WECC considered BPA's compliance history to be an aggravating factor. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for these violations.
Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | WECC2016015947 | Settlement Agreement | During a Spot Check from November 3, 2015 to June 23, 2016, NERC determined that VEA, as a Transmission Operator, had an issue with PER-005-1 R1. Specifically, NERC found that VEA failed to provide sufficient evidence to demonstrate that it: 1) developed training materials for company-specific reliability-related tasks in 2013; 2) conducted an annual evaluation to identify and implement changes to its established training program in 2013; and 3) delivered established PER-005 training in 2015. For the 2013 calendar year, the entity failed to conduct an annual evaluation of its training program and develop training materials for its company-specific real-time, Bulk Electric System (BES) reliability-related tasks. Additionally, the entity failed to provide evidence that it delivered the training established in R1.2 for the 2015 calendar year. The entity used consultants and online training for its training program in 2013, which was insufficient to demonstrate that it developed training materials for its company-specific real-time, BES reliability-related tasks. The entity did not use sign-in sheets as attendance records because its process was to collect attendance records through a course exam completion. The exam records were not sufficient to demonstrate that an individual attended the associated course. On July 26, 2016, VEA submitted a Self-Report to WECC addressing NERC’s findings. The root cause of this violation was less than adequate tracking and follow-up by VEA’s management to ensure training tools, materials, and processes were sufficient to meet program requirements and general compliance. | PER-005-1 | R1; R1.2; R1.3; and R1.4 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, VEA failed to establish and verify implementation of its training program as prescribed by PER-005-1 R1. Such failure limited VEA’s awareness of the adequacy of its training program and the individual and collective capabilities of its operating staff to perform company-specific reliability-related tasks. Although VEA could not demonstrate that it established and implemented a training program that met all R1 criteria, it did conduct some form of annual training for its system operators. Specifically, VEA provided some evidence of online and contractor-developed training, which partially addressed company-specific reliability-related tasks. VEA also resolved issues related to the development, modification, and implementation of its training program prior to the NERC Spot Check, which mainly highlighted concerns regarding a prior iteration of the program. This issue had no measurable impact on the BPS during the period in question, and no harm is known to have occurred. | 1/1/2014 (when the annual review and modification of VEA’s 2013 training program became past due) | 3/11/2016 (when VEA conducted training which met all R1 criteria) | $9,000 (for WECC2016015947 and WECC2016015948) | Self-Report | To mitigate this violation, VEA: 1) modified its learning objectives and training materials to meet company-specific reliability-related tasks; 2) established a template for the annual evaluation to guide the evaluation process and performed annual evaluations of its 2014 and 2015 training programs; 3) conducted annual training that met all R1 criteria; 4) revised its process documentation to include an annual review and modification of its training program; and 5) developed a roster to track implementation of its training program, including training course sign-in sheets and process workflows. | 2016-07-26 | 2017-02-16 | Admits | WECC considered VEA’s internal compliance program (ICP) to be a neutral factor in the penalty determination. Although VEA provided a documented ICP to WECC, the facts and circumstances of this violation do not reflect effective implementation of the ICP during the period in question. This violation was identified during a NERC Spot Check, which was initiated following investigation of a Complaint. WECC determined that this violation, in combination with NERC’s other findings, was indicative of a systemic, program-level failure to meet the requirements of PER-005-1. Accordingly, WECC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to an expedited settlement with a proposed penalty. Although VEA self-reported this violation, WECC did not apply mitigating credit because VEA was directed to Self-Report following a NERC Spot Check. WECC reviewed VEA's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | WECC2016015948 | Settlement Agreement | During a Spot Check from November 3, 2015 to June 23, 2016, NERC determined that VEA, as a Transmission Operator, had an issue with PER-005-1 R2. Specifically, NERC found that VEA failed to verify one system operator’s capabilities to perform company-specific reliability-related tasks. The entity assigned the system operator to operate elements of the Bulk Electric System without verifying the system operator's capabilities to perform each assigned task identified in R1.1 of the Reliability Standard. On July 26, 2016, VEA submitted a Self-Report to WECC addressing NERC’s findings. The root cause of this violation was less than adequate tracking and follow-up by VEA’s management to ensure each of its System Operators was verified as capable of performing tasks established in accordance with PER-005-1 R1. | PER-005-1 | R2 | High | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, VEA failed to verify the capabilities of one of its system operators to perform tasks in accordance with VEA’s established training program. Such failure limited VEA’s awareness of the individual and collective capabilities of its operating staff to perform real-time, company-specific, reliability-related tasks. However, this issue was limited to a single individual. The operator in scope was a NERC-certified system operator prior to the start date of this violation, and had terminated employment at VEA prior to the NERC Spot Check. This issue had no measurable impact on the BPS during the period in question. Had inadequate training rendered the individual in scope incapable of performing system operator tasks, other operators on shift would have compensated. No harm is known to have occurred. | 1/1/2014 (when the system operator in scope was scheduled to perform tasks identified in the training program without verification) | 1/30/2015 (when the individual in scope terminated employment at VEA) | $9,000 (for WECC2016015947 and WECC2016015948) | Self-Report | To mitigate this violation, VEA: 1) provided evidence demonstrating requisite verification for each of its current system operators; and 2) revised its process workflows and documentation to improve training program tracking and follow-up. | 2016-07-26 | 2017-02-17 | Admits | WECC considered VEA’s internal compliance program (ICP) to be a neutral factor in the penalty determination. Although VEA provided a documented ICP to WECC, the facts and circumstances of this violation do not reflect effective implementation of the ICP during the period in question. This violation was identified during a NERC Spot Check, which was initiated following investigation of a Complaint. WECC determined that this violation, in combination with NERC’s other findings, was indicative of a systemic, program-level failure to meet the requirements of PER-005-1. Accordingly, WECC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to an expedited settlement with a proposed penalty. Although VEA self-reported this violation, WECC did not apply mitigating credit because VEA was directed to Self-Report following a NERC Spot Check. WECC reviewed VEA's compliance history and determined there were no relevant instances of noncompliance.