## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015015334 | Settlement Agreement | On November 13, 2015, BPA submitted a Self-Report stating that, as a Transmission Operator, it was in violation of MOD-029-1a R2. Specifically, BPA reported that in its Total Transfer Capability (TTC) study reports, it did not identify the percent used, and justification for use, where three-phase fault damping figured in the determination of stability limits. BPA also submitted evidence of mitigation activity completion with the Self-Report. The root cause of this issue was BPA’s misinterpretation of the sub-requirement. BPA considered R2.8 inapplicable to its system because it believed the wording in the sub-requirement referred to performance criteria related to system studies that BPA does not use. | MOD-029-1a | R2; R2.8 | Lower | Moderate | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to identify and include percent used, and justification for the use of three-phase fault damping in determination of stability limits in its TTC study reports. Such failure limited consistency between actual practice and documented practice for calculating TTC. However, this issue solely concerned documentation; BPA did and does use three-phase fault damping to determine stability limits. No harm is known to have occurred. | 4/1/2011 (when the Standard became mandatory and enforceable to BPA) | 9/15/2015 (when BPA revised its System Operating Limit Methodology to include required information for three-phase fault damping) | No penalty | Self-Report | To mitigate this violation, BPA: 1) revised its System Operating Limits Methodology to clarify where three-phase fault damping is used to determine stability limits, including percent used and justification for use; and 2) linked the revised System Operating Limits Methodology to its TTC study report. | 2015-09-25 | 2017-02-02 | Does Not Contest | WECC reviewed BPA’s internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. Due to BPA’s size and resources, BPA faces unique challenges, but has nonetheless invested significant time and effort to implement its ICP. BPA’s ICP features measurable compliance performance targets, which contribute to BPA’s practice of consistent self-reporting. Although BPA self-reported this violation, this was not considered a mitigating factor because the Self-Report was submitted during the Self-Certification period. BPA had two previous violations of this Standard and Requirement, given Violation IDs: WECC201102885 and WECC2015014760. WECC considered BPA's compliance history to be an aggravating factor in the disposition determination. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2016015840 | Settlement Agreement | On June 16, 2016, PGE submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with TOP-002-2.1b R14. Specifically, PGE reported that on four separate instances it failed to notify its Transmission Operator (TOP) when one of its generators tripped offline. PGE discovered this issue during mitigation efforts for a previous issue with the same Standard and Requirement. The root cause of this violation was a gap in PGE’s procedures and training. | TOP-002-2.1b | R14; R14.1 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In four separate instances, PGE failed to notify its TOP when one of its generators tripped. Such failure could have limited the TOP’s awareness of PGE’s real output capabilities. However, each instance involved a generator within PGE’s Balancing Authority area, and PGE both notified the Reliability Coordinator and used its own reserves to recover from each trip. PGE’s lack of notification did not affect the TOP’s awareness of PGE’s real output capabilities, as the TOP had real-time visibility of each generator via telemetering. None of the instances in scope required action by the TOP, and no harm is known to have occurred. | 2/18/2016 (the earliest instance when PGE failed to inform the TOP of changes in real output capabilities after a generator tripped) | 12/8/2016 (when PGE returned to anticipated output following the fourth instance in which PGE failed to notify the TOP regarding a generator trip) | 9000 | Self-Report | To mitigate this violation, PGE: 1) revised its procedures to clarify notification requirements during forced generation reduction, and required all relevant staff to review and confirm understanding of revised procedures; 2) revised its Balancing Authority operator log to include TOP notification as clarified in the revised procedures; 3) initiated a periodic spot check process to ensure implementation of revised procedures; 4) distributed a reminder email to relevant staff regarding notification requirements; and 5) developed system-specific computer-based training to emphasize compliance requirements associated with issues of this nature. | 2017-01-10 | 2017-03-06 | Admits | WECC considered PGE’s internal compliance program (ICP) a mitigating factor in the penalty determination. PGE’s ICP requires review and modification of procedures following identification of potential noncompliance, which promotes early detection and/or prevention of recurrence. In this case, PGE was in the process of adopting preventive controls to address a previous issue when it discovered this violation. PGE self-reported this violation. PGE had one previous issue of noncompliance with this Standard and Requirement, given Violation ID: WECC2015015193. Because WECC processed the previous issue as a Compliance Exception, WECC considered PGE’s compliance history neutral to the penalty determination for the current violation. However, the facts, circumstances and timing of the current violation indicate that PGE failed to fully mitigate the previous issue; therefore, WECC disqualified the current violation for Compliance Exception treatment, and aggravated this disposition to an expedited settlement with a penalty.
Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2016016684 | Settlement Agreement | On December 15, 2016, SRP submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-023-2 R1. During an internal review, SRP discovered that 17 of its 134 applicable relays did not have the switch-on-to-fault (SOTF) protective function capability set in accordance with PRC-023 Attachment A. The root cause of this issue was human error and less than adequate procedures; SRP incorrectly transferred protective functions identified in Attachment A to its loadability spreadsheet, and did not assess loadability criteria for SOTF as a result. | PRC-023-2 | R1 | High | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SRP failed to evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees for the SOTF protective function. Such failure increased the risk of inadvertent tripping and/or loss of associated 230 kV and 500 kV lines. Although SRP validated its phase overcurrent relay settings annually, it did not identify this issue. The scope of this violation involved 17 out of 134 relays, roughly 13% of SRP’s applicable relays. None of the relays in scope were associated with a major WECC Transfer Path, and there were no misoperations due to the SOTF settings during the period in question. No harm is known to have occurred. | 10/1/2013 (when PRC-023-2 became mandatory and enforceable for SOTF schemes) | 10/5/2016 (when SRP adjusted the SOTF protective function setting on the relays in scope) | 26000 | Self-Report | To mitigate this violation, SRP: 1) updated the SOTF protective function settings for the relays in scope; 2) revised its loadability spreadsheet to include all applicable protective functions; and 3) revised its procedure to address applicability of protective functions identified in PRC-023-3 Attachments A and B. | 2016-11-30 | 2017-02-21 | Admits | WECC considered SRP’s internal compliance program (ICP) to be a neutral factor in the penalty determination. Although SRP provided a documented ICP to WECC, the facts and circumstances of this violation do not reflect effective implementation of the ICP. WECC applied an aggravating factor for the violation duration, which was 1,100 days. SRP did not have detective controls in place to identify this violation sooner and/or reduce the duration. WECC applied self-reporting credit to this violation. WECC reviewed SRP's compliance history and determined there were no relevant instances of noncompliance.