## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | EDF Renewable Service (EDFR) | NCR11441 | WECC2016015536 | Settlement Agreement | On February 11, 2016, EDFR submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-2b R2. Specifically, EDFR reported that it failed to consistently monitor the generator voltage or Reactive Power schedule as directed by its Transmission Operator (TOP), and therefore could not confirm whether it consistently maintained the TOP’s voltage or Reactive Power schedule. Instead, EDFR reported it was providing voltage monitoring and or controlling on a longer interval of time, averaging approximately six hours. The root cause of this violation was the failure of EDFR management to provide direction, methods, and means to ensure compliance. | VAR-002-2b | R2 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, EDFR failed to consistently monitor voltage to ensure it met the TOP’s voltage schedule. Such failure limited EDFR’s situational awareness, and could have effected a mismatch between expected and actual generator output voltage or reactive flows, potentially resulting in insufficient voltage support, equipment damage, and/or loss of up to 242 MW of generation. However, the TOP continuously monitored voltage at the point of interconnection throughout the duration of this issue, and notified EDFR when it was not within its voltage schedule. EDFR manually adjusted voltage as directed by the TOP, and no harm is known to have occurred. | 2/6/2014 (when EDFR registered as a GOP) | Present | 30000 | Self-Report | To mitigate this violation, EDFR will: 1) conduct a survey of all facilities to identify voltage and voltage controller status points, and connect voltage and voltage controller status to its supervisory control and data acquisition (SCADA) system; 2) set alarming and establish real-time monitoring of voltage and voltage controller status; and 3) develop and conduct training for all relevant staff regarding VAR-002 compliance requirements. | 2017-05-05 | TBD | Admits | EDFR did not receive mitigating credit for self-reporting because EDFR was directed to self-report following an investigation of similar issues with EDFR affiliates. WECC reviewed EDFR's compliance history and determined there were no relevant instances of noncompliance. As of the issue date of EDFR’s notice of expedited settlement agreement, the violation duration was 1,148 days, and is ongoing. EDFR did not have any detective controls in place to identify this violation in a timely manner, or to reduce the violation duration. WECC considered the violation duration as an aggravating factor, and escalated the disposition to an expedited settlement with a penalty.