## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2016016602 | Settlement Agreement | On September 6, 2016, SERC sent Duke Energy Florida, LLC (DEF) an audit detail letter notifying it of a Compliance Audit scheduled for December 5, 2016 to December 16, 2016. On November 30, 2016, DEF submitted a Self-Report to DEP stating that, as a Generator Operator, DEF was in violation of VAR-002-4 R3. DEP submitted the Self-Report to SERC under an existing multi-regional registered entity agreement. DEF did not notify its Transmission Operator (TOP) within 30 minutes of a status change on an automatic voltage regulator (AVR). On August 21, 2016 at 2:55 p.m., the energy control center (ECC) requested Suwannee River units 2 and 3 to proceed to full load. At 3:58 p.m., the status of the Unit 3 AVR changed from automatic to manual control, but DEF personnel were unaware of the change. At 6:00 p.m. the plant operator shift turnover occurred. At 6:54 p.m. the ECC requested minimum load on units 2 and 3. At approximately 8:00 p.m., while taking logs following the load change, the unit 3 control board operator observed unit 3 operating with abnormally high MVAR output. Operators investigated and found the unit 3 AVR in manual control. A plant operator reviewed indications on the local alarm panel for the AVR and found no other alarms and no indication of why the AVR was in manual control. At 8:27 p.m., after internally discussing the situation, operators returned the AVR to automatic. Plant operators did not communicate either AVR mode change to the TOP because the operators believed they had restored automatic operation within 30 minutes of the change and notification was not required. During an investigation the following week, DEF discovered that the AVR mode changed from automatic to manual at 3:58 p.m. on August 21, 2016, approximately four hours before the operator detected it. The cause of this violation was that DEF did not know that the AVR mode had changed until about four hours later and DEF mistakenly thought it had recently changed. | VAR-002-4 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEF’s failure to notify the TOP of changes to the state of the AVR within 30 minutes could result in the TOP having incorrect expectations regarding its control of reactive capability. However, Suwannee River unit 3 operated in parallel with unit 2 and the unit 2 AVR operated in automatic throughout the violation, minimizing any change in voltage generated by unit 3. Unit 3 maintained output voltage within its voltage schedule and did not exceed its maximum reactive power capability during the time that the AVR was in manual. The Suwannee River unit 3 output capacity was 75 MW out of DEF’s total generation of 10,285 MW (0.73%). DEF concluded that no misoperations or system disturbances occurred as a result of the violation. No harm is known to have occurred. | 8/21/2016 at 4:29 p.m. (when DEF failed to notify its TOP of the change in AVR status within 30 minutes) | 8/21/2016 at 8:27 p.m. (when DEF returned the unit to automatic voltage control mode) | $0 (for SERC2016016602 and SERC2017016814) | Self-Report | To mitigate this violation, DEF: 1) reissued the DEF procedure covering reporting requirements for VAR-002 to all operations personnel for the involved unit; 2) issued an email to all operations personnel for the involved unit defining expectations regarding procedure adherence as well as required communications when adjusting the AVR set point and MVAR input and output; and 3) followed up with a face to face discussion. To mitigate this violation, DEF will: 1) issue an email on expectations to shift personnel on procedure adherence as well as required communication when adjusting AVR set point and MVAR input/output. DEF will follow up with meaningful discussion; 2) implement a required reading for all Duke Energy Carolinas, LLC (DEC) stations' control operators for DEC's procedure for communication to TOP regarding voltage schedule; 3) implement a required reading for all DEF stations' control operators for DEF's procedure for communication to TOP regarding voltage schedule; 4) implement a required reading for all DEP stations' control operators for DEP's procedure for communication to TOP regarding voltage schedule; 5) implement a required reading for all Duke Energy Corporation (DECorp) stations' control operators for DECorp's procedure for communication to TOP regarding voltage schedule; 6) implement AVR status and alarms in manned area for all Duke enterprise stations that do not require an outage to install the alarms; and 7) implement AVR status and alarms in manned area for all Duke enterprise stations that do require an outage to install the alarms. | 8/24/2018 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed DEF’s internal compliance program (ICP) and consider it to be a mitigating factor in the penalty determination. DEF follows Duke’s enterprise-wide ICP, which has been in place since 2013. DEF’s electric reliability executive steering committee (ERESC) meets at least quarterly, regularly reviews the effectiveness of the ICP, provides direction for the ICP, and appoints the chief compliance officer, who has overall responsibility for the ICP. The chief compliance officer reports to the chair of the audit committee of the board of directors. The ERESC considers cases of noncompliance in assessing whether it needs to make any improvements to the ICP. DEF’s NERC corporate compliance program (NCC) is responsible for day to day operations of the ICP, has several dedicated employees who report to the chief compliance officer, and has direct access to the audit committee. DEF makes the ICP available to all staff on its intranet and distributes amendments to business units’ compliance directors or managers for further distribution. DEF requires all staff responsible for NERC compliance to take annual NERC compliance training, disseminates compliance information to staff via a newsletter, and offers additional annual training on compliance expectations and processes. The NCC performs annual formal independent assessments of compliance. DEF encourages self-reporting and uses compliance focused working groups, teams, and programs for staff to collaborate across business units on compliance matters. DEF uses a corrective action process to address staff performance and behavior, which provides management flexible steps to address issues, up to and including termination. DEF did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC would have treated this noncompliance as a Compliance Exception, but the Mitigation Plan expected completion date extended beyond one year from the expected filing date. SERC considered DEF’s VAR-002 R3 compliance history in determining the disposition track. DEF’s relevant prior noncompliance with VAR-002 R3 includes: NERC Violation IDs FRCC2013011834, FRCC2013013105, and SERC2016015593. SERC considered DEF’s affiliate, DECorp, VAR-002-4 R3 compliance history in determining the disposition track. DECorp’s relevant prior noncompliance with VAR-002 R3 includes: NERC Violation IDs RFC2014013319 and RFC2014014482. SERC considered Duke Energy Carolina’s and Duke Energy Progress’s compliance history and determined that there were no relevant instances of noncompliance. SERC determined that DEF’s and its affiliates’ VAR-002 R3 compliance history should not serve as a basis for aggravating the penalty. In FRCC2013011834, DEF intentionally switched units to automatic control mode and did not notify the TOP within 30 minutes. In FRCC2013013105, while DEP notified the TOP of the AVR status change within 30 minutes, it did not notify the TOP of the expected duration of the change of state as required by an earlier version of the Standard. In RFC2014013319, DECorp had inadequate procedures for planned generator maintenance work and also miscommunicated at the time work on the AVR began. In RFC2014014482, DECorp placed the AVR in automatic mode for troubleshooting and did not notify the TOP within 30 minutes. In SERC2016015593, DEF did not notify the TOP within 30 minutes after a new Power System Stabilizer became enabled during an AVR replacement. Each of these noncompliance is substantially different from the instant noncompliance, which involved DEF being unaware of the change of AVR state, and mitigation of the prior noncompliance would not have prevented the instant violation.
SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2017016814 | Settlement Agreement | On January 19, 2017, DEF submitted a Self-Report to DEP stating that, as a Generator Operator (GOP), DEF had a violation of VAR-002-4 R1. DEP submitted the Self-Report to SERC under an existing multi-regional registered entity agreement. SERC identified that DEF had a possible noncompliance with VAR-002-4 R1 while assessing a related Possible Violation (SERC2016016602) and instructed DEF to self-report this violation. DEF operated a generator connected to the interconnected transmission system in a mode other than automatic voltage control mode without notifying the Transmission Operator (TOP). On August 21, 2016 at 2:55 p.m., the energy control center (ECC) requested Suwannee River units 2 and 3 to proceed to full load. At 3:58 p.m., the status of the Unit 3 AVR changed from automatic to manual control, but DEF personnel were unaware of the change. At 6:00 p.m. the plant operator shift turnover occurred. At 6:54 p.m. the ECC requested minimum load on unit 2 and 3. At approximately 8:00 p.m., while taking logs following the load change, the unit 3 control board operator observed unit 3 operating with abnormally high MVAR output. Operators investigated and found the automatic voltage regulator (AVR) in manual control. A plant operator reviewed indications on the local alarm panel for the AVR and found no other alarms and no indication of why the AVR was in manual control. After discussing the matter, at 8:27 p.m., the plant operators returned the AVR to automatic. During an investigation the following week, DEF discovered the AVR mode changed from automatic to manual at 3:58 p.m. on August 21, 2016, approximately four hours before the operator detected it. DEF did not determine the cause for the AVR mode change. The cause for the violation was ineffective or inadequate AVR status indication. | VAR-002-4 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DEF’s failure to notify the TOP prior to the change in the state of the AVR could result in the TOP having incorrect expectations regarding its control of reactive load. However, Suwannee River unit 3 operated in parallel with unit 2 and the unit 2 AVR operated in automatic throughout the violation, minimizing any change in voltage generated by unit 3. Unit 3 maintained output voltage within its voltage schedule and did not exceed its maximum reactive power capability during the time that the AVR was in manual. The Suwannee River unit 3 output capacity is 75 MW out of DEF’s total generation of 10,285 MW (0.73%). DEF concluded that no misoperations or system disturbances occurred as a result of the violation. No harm is known to have occurred. | 8/21/2016 at 3:58 p.m. (when DEF’s AVR mode changed from automatic to manual without first notifying the TOP) | 8/21/2016 at 8:27 p.m. (when DEF returned the unit to automatic voltage control mode) | $0 (for SERC2016016602 and SERC2017016814) | Self-Report | To mitigate this violation, DEF: 1) reissued its procedure which covers reporting requirements for VAR-002 to all operations personnel for the involved unit; 2) issued an email to all operations personnel for the involved unit defining expectations regarding procedure adherence as well as required communications when adjusting the AVR set point and MVAR input and output; and 3) followed up with a face to face discussion. To mitigate this violation, DEF will: 1) issue an email on expectations to shift personnel on procedure adherence as well as required communication when adjusting AVR set point and MVAR input/output. DEF will follow up with meaningful discussion; 2) implement a required reading for all Duke Energy Carolinas, LLC (DEC) stations' control operators for DEC's procedure for communication to TOP regarding voltage schedule; 3) implement a required reading for all DEF stations' control operators for DEF's procedure for communication to TOP regarding voltage schedule; 4) implement a required reading for all DEP stations' control operators for DEP's procedure for communication to TOP regarding voltage schedule; 5) implement a required reading for all Duke Energy Corporation (DECorp) stations' control operators for DECorp's procedure for communication to TOP regarding voltage schedule; 6) implement AVR status and alarms in manned area for all Duke enterprise stations that do not require an outage to install the alarms; and 7) implement AVR status and alarms in manned area for all Duke enterprise stations that do require an outage to install the alarms. | 8/24/2018 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed DEF’s internal compliance program (ICP) and consider it to be a mitigating factor in the penalty determination. DEF follows Duke’s enterprise-wide ICP, which has been in place since 2013. DEF’s electric reliability executive steering committee (ERESC) meets at least quarterly, regularly reviews the effectiveness of the ICP, provides direction for the ICP, and appoints the chief compliance officer, who has overall responsibility for the ICP. The chief compliance officer reports to the chair of the audit committee of the board of directors. The ERESC considers cases of noncompliance in assessing whether it needs to make any improvements to the ICP. DEF’s NERC corporate compliance program (NCC) is responsible for day to day operations of the ICP, has several dedicated employees who report to the chief compliance officer, and has direct access to the audit committee. DEF makes the ICP available to all staff on its intranet and distributes amendments to business units’ compliance directors or managers for further distribution. DEF requires all staff responsible for NERC compliance to take annual NERC compliance training, disseminates compliance information to staff via a newsletter, and offers additional annual training on compliance expectations and processes. The NCC performs annual formal independent assessments of compliance. DEF encourages self-reporting and uses compliance focused working groups, teams, and programs for staff to collaborate across business units on compliance matters. DEF uses a corrective action process to address staff performance and behavior, which provides management flexible steps to address issues, up to and including termination. DEF did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC would have treated this noncompliance as a Compliance Exception, but the Mitigation Plan expected completion date extended beyond one year from the expected filing date. SERC considered DEF’s and its affiliates’ compliance history in determining the disposition track. DEF’s affiliate, DECorp’s relevant prior noncompliance with VAR-002 R1 includes: NERC Violation ID RFC2014013319. SERC determined that DECorp’s compliance history should not serve as a basis for aggravating the penalty. In RFC2014013319, DECorp operated a generator in manual voltage control mode without notifying the TOP in two instances that involved inadequate DECorp procedures for planned generator maintenance work and also miscommunicated at the time work on the AVR began. DECorp’s mitigation of its prior noncompliance would not have prevented the instant violation of DEF.
SERC Reliability Corporation (SERC) | Sam Rayburn & G&T Electric Cooperative Inc. (SRGT) | NCR01307 | SERC2015015247 | Settlement Agreement | During a Compliance Audit conducted from September 9, 2015 to September 10, 2015, SERC determined that SRGT, as a Transmission Owner, was in violation of FAC-009-1 R1. SRGT did not establish Facility Ratings consistent with its Facility Rating Methodology (FRM). SERC later determined that the violation continued under FAC-008-3 R6. SRGT’s FRM requires the use of the most-limiting element (MLE) as the Facility Rating for solely and jointly owned Facilities. In response to a request for information from SERC, SRGT assessed all Facility Ratings and determined Facility Ratings for 51 of its 73 line segments (69.86%) were not consistent with its FRM. In each case, another entity owned the MLE, and SRGT did not consider those elements in establishing the Facility Ratings. In addition, for some elements SRGT owned, SRGT incorrectly converted the amp rating to an MVA rating, which caused calculation errors in determining Facility Ratings. SRGT de-rated or up-rated 42 Facilities out of the 51 line segments that were not consistent with its FRM. Of the 42 line segments that had a ratings change, SRGT de-rated 35 of the line segments with the de-rates ranging from 0.5% to 78.76% of the prior incorrect ratings, with only one de-rate below 10% of the prior incorrect rating. The highest de-rate was 367 MVA. The ratings of nine facilities did not change after SRGT correctly applied its FRM. SRGT increased the ratings for seven line segments (i.e., the original rating was more conservative than required by the FRM). The primary cause of this violation was SRGT’s misunderstanding of the requirement to include Facilities owned by other entities in establishing SRGT’s Facility Ratings. In addition, SRGT should have identified and corrected the conversion errors and miscalculations during previous reviews. The earliest instance of SRGT establishing a Facility Rating that was not consistent with the FRM occurred before the Standard became mandatory and enforceable on SRGT. | FAC-009-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SRGT’s failure to establish Facility Ratings that were consistent with its FRM for approximately 70% of its line segments resulted in 35 line segments being de-rated, with 34 line segments requiring a de-rate of 10% or more, and could have resulted in erroneous outage planning, violations of System Operating Limits, and damage to Facilities. However, the third-party owner of the MLEs, used the correct MLEs in determining Facility Ratings and operated its system accordingly. Further, the Midcontinent Independent System Operator used the jointly-owned Facilities as the MLE where appropriate in its joint-owner modeling process. SRGT is a member of the East Texas Electric Cooperative (ETEC), which has a total of 271 miles of 138 kV lines and 0.5 miles of 230 kV lines. SRGT has a peak load of approximately 430 MW and is interconnected with Entergy and U.S. Army Corps of Engineers. No harm is known to have occurred. | 5/1/2009 (when SRGT's previous audit ended) | 8/25/2016 (Mitigation Plan completion) | 50000 | Compliance Audit | To mitigate this violation, SRGT: 1) requested Entergy and the Corps of Engineers to supply their updated Facility Ratings, including the MLE, for their facilities that are connected to a SRGT facility; 2) updated and re-evaluated its Facility Ratings spreadsheets to include the Entergy and Corps of Engineers ratings and identify the MLE; and 3) implemented reviewing the FRM and Facility Rating reports at least on an annual basis, including confirming ratings and collecting any updates from Entergy and the Corps of Engineers to update the rating documents. | 2016-08-25 | 2017-02-03 | Neither Admits nor Denies | SERC reviewed SRGT's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SRGT is a member of ETEC and uses ETEC's documented ICP, which has been in place since 2010. ETEC makes its ICP accessible through an intranet site and annually distributes it to appropriate personnel. ETEC's ICP is managed by the ETEC compliance manager with oversight and input by the ETEC compliance officer and general manager. Both the compliance manager and officer have direct access to the general managers of ETEC members. ETEC has an internal compliance committee (ICC), chaired by the ETEC compliance manager and made up of engineering and operations staff, consultants, and ETEC members’ staff responsible for compliance with Reliability Standards. The ICC annually reviews the ICP and makes revisions as needed. ETEC’s ICP includes spot checks, annual self-assessments, and annual training for employees responsible for compliance. ETEC reports self-assessment results to the ICC. The ETEC compliance officer and compliance manager make internal determinations on self-reports initiated by engineering and operations staff. ETEC’s ICP includes disciplinary action for employees who fail to comply with the ICP. SERC considered SRGT’s FAC-009-1 R1 and FAC-008-3 R6 compliance history and determined that there were no relevant instances of noncompliance. SERC also considered SRGT’s FAC-008-1 R1 compliance history because FAC-008-1 R1 is closely related to FAC-009-1 R1. SRGT’s relevant prior noncompliance with FAC-008-1 R1 includes: NERC Violation ID SERC200700024. SERC also considered SRGT’s affiliates’ FAC-008-1 R1 compliance history. ETEC and Tex-La Electric Cooperative of Texas (TEXL), SRGT affiliates, have the following relevant prior noncompliance with FAC-008-1 R1: NERC Violation ID SERC200700025 and SERC200700026. SERC considered SRGT’s and its affiliates’ FAC-008-1 R1 compliance history to be an aggravating factor in the penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015786 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW3, as a Generator Owner (GO), had an issue with PRC-005-1 R2. In particular, SW3 failed to provide evidence that certain Protection System devices were maintained and tested within the defined intervals. Texas RE subsequently determined that SW3 has not completely mitigated all of its maintenance and testing issues. Accordingly, SW3 likewise had issues with PRC-005-2(i) for certain devices under the maximum maintenance intervals set forth under that Standard from October 1, 2015 until SW3 completes all required testing for those devices. During the Compliance Audit, Texas RE determined that SW3 did not possess evidence that it maintained five categories of Protection System devices within the intervals defined in various versions of its Protection System Maintenance Program (PSMP). Specifically, SW3 had issues with (1) voltage and current sensing devices; (2) dc control circuitry; (3) relays; (4) batteries; and (5) communication systems. Regarding SW3’s voltage and current sensing devices, SW3’s PSMP in effect on October 3, 2007 required testing of such Protection Systems every 24 months. Because this was SW3’s original PSMP, SW3 should have performed the initial annual testing for 32 devices as required on October 3, 2007. Subsequently, SW3 added a monthly testing requirement for its voltage and current sensing devices on April 28, 2009 and reduced the 24-month testing interval to an annual testing requirement. For 22 voltage and current sensing devises, the earliest tests SW3 could locate were from August 10, 2012. Further, SW3 failed to perform any testing on the remaining 10 voltage and current sensing devices. Following the August 2012 testing, SW3 should have performed the next required test on these 22 voltage and current sensing Protection Systems at issue on September 10, 2012. However, SW3 did not perform any additional testing on these 22 devices. On April 1, 2015, SW3 revised its PSMP to align with the PRC-005-2(i) maintenance and testing intervals. In doing so, SW3 eliminated its monthly and annual testing intervals and now performs required maintenance on its voltage and current sensing devices every 12 years per PRC-005-2(i) Table 1-3. Accordingly, SW3 will perform the next required maintenance and testing on 22 voltage and current sensing devices by August 10, 2024. For the remaining 10 untested voltage and current sensing devices, SW3 will complete testing as part of its Mitigation Plan. Regarding SW3’s dc control circuitry, SW3’s PSMP dated October 3, 2007 required annual testing for these Protection Systems. Because this was SW3’s original PSMP, SW3 should have performed the initial annual testing for six dc control circuit Protection Systems on the date it adopted the PSMP or October 3, 2007. However, SW3 failed to provide any evidence that is performed the required maintenance and testing activities on the six dc control circuit Protection Systems at issue. Regarding SW3’s relays, SW3’s October 3, 2007 PSMP required weekly, annual and 24-month testing for these Protection Systems. Because this was SW3’s original PSMP, SW3 should have performed the initial annual testing for one relay Protection Systems on the date it adopted the PSMP or October 3, 2007. However, SW2 failed to provide any evidence that it performed the required maintenance and testing activities on the single relay at issue. In addition, regarding SW3’s batteries, SW3’s initial PSMP required monthly and annual testing of its batteries. SW3 provided evidence that it last performed testing on four batteries on April 2, 2014. Accordingly, SW3 would have performed its next required maintenance activities on those four batteries by May 2, 2014. However, SW3 failed to perform either the requisite monthly or annual testing as required. On April 1, 2015, SW3 revised its PSMP to require testing at least every four months to align its PSMP with PRC-005-2(i) Tables 1-4(a). However, under either version of the SW3’s PSMP, SW3 failed to perform all required testing until February 15, 2016. Finally, regarding SW3’s communication systems, SW3’s April 28, 2009 PSMP required weekly and five-year testing on these devices. As such, SW3 should have performed initial maintenance activities on four communications systems by April 28, 2009. However, SW3 failed to provide any evidence that it performed the required maintenance and testing activities on the four communication systems at issue. The root cause of the violation was an inadequate process for ensuring that SW3 personnel performed all required testing and maintenance activities in a timely manner. In particular, SW3, did not possess an accurate inventory of its Protection Systems, tracking required maintenance activities and the testing intervals associated with those applicable Protection Systems, and verifying results. As a result, SW3 personnel could not effectively use existing maintenance tracking systems to capture maintenance dates and testing records. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not properly maintaining the equipment could lead to misoperation of protection devices. Moreover, the issue here affected a significant number of Protection Systems. Specifically, SW3 had maintenance and testing issues with 77% (47 out of 61) of its Protection Systems. Texas RE also considered the fact that Sweetwater Facilities did not possess proper tracking of the maintenance and testing intervals in the various iterations of their PSMP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW3 has not experienced any misoperations during the duration of the issues in question to date. Finally, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT Interconnection possessed adequate reserves to respond to any issues. SW3 also produces a relatively small amount of power, with the maximum nameplate rating of 135 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | present | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate the violation, SW3: 1) developed a new process to track and monitor Protection System maintenance and testing activities to ensure compliance with all applicable PRC-005 requirements; 2) completed new equipment list spreadsheets that list all equipment by component and address any missing equipment; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including training on PRC-005 maintenance and testing requirements; 7) verify the plant one-line diagrams match the as-built condition of the plants and ensure the revised equipment list conforms to SW3’s one-line diagrams; 8) review all required maintenance and testing intervals to ensure their alignment with the applicable version of PRC-005; and 9) review records for all identified Protection Systems to ensure maintenance and testing has been properly performed consistent with all PRC-005-6 requirements. Additionally, SW3 will complete the following mitigation actions by September 1, 2017: 1) validate all components in Maximo against the spreadsheets to assure all equipment is listed with the correct maintenance and frequency; 2) establish a new testing record archival process within the Maximo system to facilitate test record keeping and retrieval; 3) provide training to all employees that will be using Maximo as part of their daily activities, including training consists of review of documentation and hands on training in a development database; and 4) perform any additional required maintenance and testing identified during the records review for all identified Protection Systems. | 9/1/2017 (approved completion date) | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' PRC-005 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with PRC-005 include(s): TRE201100503, TRE201100504, TRE201100505, and WECC201001962. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violations pertaining to PRC-005-1 R1 (TRE201100503, TRE201100504, and TRE201100505) constituted repeat violations and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that compliance history of Sweetwater's’ affiliate, Cedar Creek Wind Energy, LLC (CCWE), should not serve as a basis for aggravating the penalty. Texas RE determined that CCWE had a previous violation with PRC-005-1 R2 (WECC201001962). In WECC201001962, CCWE failed to complete its monthly testing on one station battery for approximately six months. As a result, CCWE completed all required testing by June 1, 2008. Texas RE considers that the root causes were dissimilar because they both pertained to a separate company, a separate operations staff and a separate compliance department at the time of the violation. Moreover, Texas RE concluded that, when these violations occurred, Sweetwater did not own or was not an affiliate of these registered entities. Accordingly, Texas RE did not consider this noncompliance as an aggravating factor.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015770 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Operators (GOPs), were in violation of VAR-002-2b R2. Specifically, Sweetwater Facilities did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the TOP. During the Compliance Audit, Texas RE reviewed the seasonal voltage schedules published by Sweetwater Facilities’ TOP. The GOP is expected to maintain voltage amounts within a +/- 2.0% tolerance. Voltage amounts are measured at the Point of Interconnection. As such, because Sweetwater Facilities share a common Point of Interconnection, any voltage deviations will be the same for all four entities. Based on a review of Sweetwater Facilities’ actual voltage measured at the Point of Interconnection, Texas RE determined that Sweetwater Facilities deviated from their voltage schedules by more than +/- 2.0% for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE further determined that Sweetwater Facilities did not receive any exemptions from their TOP regarding their voltage schedule obligations. Sweetwater Facilities also did not receive any instructions from their TOP directing them to exceed the +/-2.0% tolerance throughout the duration of the issue. The root cause of this noncompliance is that Sweetwater Facilities did not have an adequate process in place to ensure they maintained their prescribed voltage schedules. While Sweetwater Facilities did have processes in place stating that they shall maintain their voltage schedule, these processes were outdated, and not current with the requirements set forth in the current version of VAR-002. More importantly, these processes did not contain clear instructions for their operating personnel to reference in regards to the methods in which Sweetwater Facilities are expected to recognize voltage deviations and subsequently act in order to maintain their voltage schedule or convey information regarding unit capabilities to their TOP. In particular, Sweetwater Facilities’ voltage excursions were almost entirely limited to the spring and fall seasons during which their TOP established lower voltage levels for Sweetwater Facilities to follow. However, Sweetwater Facilities’ personnel did not have a process for recognizing these seasonal voltage excursion issues and communicating Sweetwater Facilities’ actual seasonal voltage capabilities to their TOP. | VAR-002-2b | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure of a GOP to maintain its voltage schedule can affect voltages in the area surrounding its Point of Interconnection. Voltage instability can cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear voltage control procedures designed to ensure compliance with relevant NERC Standards. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ voltage deviations most commonly occurred while Sweetwater was producing low amounts of generation, limiting the potential impact of the voltage issues on other Transmission and Generation Facilities. Second, the actual amount of Sweetwater Facilities’ voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons only on one, limited occasion. Finally, at no time did Sweetwater Facilities’ TOP request that Sweetwater modify their voltage output. No harm is known to have occurred. | 9/1/2013 (the earliest date of deviation) | 9/29/2016 (the last recorded date of deviation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW2: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) requested new voltage schedules that were approved and are currently followed; 3) installed alarms to notify their operating personnel when voltage is out of tolerance; 4) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for Sweetwater Facilities’ operating personnel to follow in order to meet voltage schedule the recognition and reporting requirements; 5) installed new Wind Farm Management System (WFMS) that includes voltage modules (Automatic Voltage Regulator (AVR Status)) and returned their AVRs to service; 6) trained personnel on the operational characteristics of the new AVRs, including voltage control; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 9) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; and 10) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' and its affiliates' VAR-002-2b R2 compliance history in determining the penalty. Sweetwater Facilities' affiliate, Allegheny Ridge Wind Farm, LLC's (ARWF) relevant prior noncompliance with VAR-002-2b R2 include(s): RFC2015014740. Texas RE determined that ARWF's compliance history should not serve as a basis for aggravating the penalty. In RFC2015014740, RF determined during a Compliance Audit that ARWF failed to follow its issued voltage schedule on three occasions. In the current circumstances, Texas RE similarly determined that Sweetwater Facilities deviated from their issued voltage schedules for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE accordingly determined that the previous violation referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered a repeat violation. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel maintained prescribed voltage schedules, again reflecting deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015771 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, as a Generator Operator (GOP), was in violation of VAR-002-4 R3. Specifically, SW2 failed to notify its associated Transmission Operator (TOP) of a status change on the Automatic Voltage Regulator (AVR) within 30 minutes of the change. On June 29, 2015, SW2 performed certain reactive power tests on their respective Facilities. During the testing, SW2 personnel determined that the Wind Farm Management Systems (WFMS), which serves both Facilities, was not operational. SW2’s respective AVRs require a functioning WFMS to operate. Despite the WFMS being offline, SW2 personnel did not believe this constituted an AVR status change requiring notification as they incorrectly considered the reactive devices and Load Tap Changers to be the relevant AVR components for status change reporting purposes. Accordingly, SW2 did not notify its TOP regarding the AVR status changes in question. On December 30, 2016, SW2 replaced its WFMS and restored the AVR to service. The root cause of this instance of noncompliance was an inadequate internal controls to ensure SW2 provided proper and timely notices of AVR status changes to their TOP. Specifically, SW2’s notification processes did not clearly identify both what constituted an AVR status change, as well as the conditions in which SW2 personnel should notify its TOP of such an AVR status change. Moreover, the existing processes were outdated and did not reflect current NERC requirements. Finally, SW2 did not have additional controls in place, such as operator alarms, to alert their personnel of when their Facilities’ respective AVRs were offline. | VAR-002-4 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. SW2’s failure to notify its TOP of the AVR status change limited the TOP’s situational awareness, and could have resulted in unplanned tripping of the unit due to undamped voltage oscillations. Such localized unit tripping could also cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration was lengthy, and SW2 did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including controls to detect AVR issues and ensure timely notification of those issues is provided to the TOP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against these facts is that the specific issue only affected SW2 and SW3. Sweetwater Facilities share a common Point of Interconnection and throughout the issue duration the AVRs for SW4 and SW5 were online and actively regulating voltage. Due to these factors, Sweetwater Facilities collectively had compensating measures in place to help regulate voltage, and even make up for the lack of voltage control from SW2 and SW3. Second, the actual amount of SW2 and SW3’s voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons in only one, limited instance. Finally, at no time did SW2's TOP request that SW2 modify its actual voltage output. No harm is known to have occurred. | 6/29/2015 (the earliest date Texas RE could determine SW2’s AVR to be offline and SW2 failed to notify its TOP) | 11/03/2016 (when SW2 restored its AVR to service) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2: 1) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for SW2 and SW3’s operating personnel to follow in order to ensure proper; 2) designed and installed alarms to notify operators when their AVRs are out of service; 3) installed new WFMS that include a Voltage Modules (AVR Status) and returned their AVRs to service; 4) trained personnel on the operational characteristics of the new AVRs and requirements to update telemetry set points provided to their Reliability Coordinator (RC) when the AVRs are offline; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; and 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to VAR-002 R3.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015772 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, as a Generator Operator (GOP), was in violation of VAR-002-4 R4. Specifically, SW2 did not notify its associated Transmission Operator (TOP) within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in VAR-002-4 R3. At 1:45 p.m. on February 15, 2016, one of SW2’s capacitor banks experienced an outage, resulting in a change in that Facility’s reactive capability. As such, SW2 personnel should have notified SW2’s TOP regarding the reactive capability change within 30 minutes, or 2:15 p.m. However, SW2 did not notify its TOP of the capacitor bank outage until 1:35 p.m. on February 16, 2016, nearly 24 hours after the outage occurred. The root cause of this instance of noncompliance was inadequate internal controls to ensure SW2 provided proper and timely notices of certain reactive capability changes to their TOP. Specifically, SW2’s existing processes were outdated and did not reflect current NERC requirements. Further, SW2 did not have additional controls in place, such as operator alarms, to alert its personnel of changes in reactive capability. | VAR-002-4 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. SW2’s failure to notify their TOP of changes in its reactive capability limited the TOP’s situational awareness regarding the amount of reactive capability available to it. As a result, SW2’s TOP would not fully understand the generation resources available to respond to unplanned events or actively manage the grid. Balanced against this is the fact that the duration of the issue was short, lasting only approximately one day. Second, the SW2 Facility contains three other 14.4 MVAR capacitor banks, which were online and able to control voltage throughout the period of noncompliance. Third, the SW2 Facility shares a common Point of Interconnection with four other Wind Farm Facilities, which each contain varying degrees of reactive capability. Because of the common Point of Interconnection, the reactive capabilities at these other Facilities would have been able to compensate for the outage of the single capacitor bank at SW2. Fourth, SW2’s TOP did not request SW2 modify its voltage output during the duration of the issue in question. Finally, the SW2 Facility has a maximum output capability of only 91.5 MW. No harm is known to have occurred. | 2/15/2016 (when SW2 failed to provide notification to its TOP following a change in reactive capability) | 2/16/2016 (when SW2 notified its TOP of the change in reactive capability) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW2: 1) placed the Capacitor Banks back in service after repair and made appropriate notifications; 2) issued a new VAR-002 procedure that aligns with the current version of the Standard; 3) trained personnel to understand that capacitor banks are reactive sources and must be reported to the TOP when removed and restored to service; 4) developed a new internal compliance review process that includes regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create a fully documented set of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to VAR-002 R4.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015773 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2 and SW3, as Generator Owners (GOs) and Generator Operators (GOPs), were in violation of IRO-010-1a R3. In particular, SW2 and SW3 did not provide the accurate status of their Automatic Voltage Regulators (AVRs) through telemetry data as specified by their Reliability Coordinator (RC). On June 29, 2015, SW2 and SW3 performed certain reactive power tests on their respective Facilities. During the testing, SW2 and SW3 personnel determined that the Wind Farm Management System (WFMS), which serves both Facilities, was not operational. SW2 and SW3’s respective AVRs require a functioning WFMS to operate. Despite their AVRs being offline, SW2 and SW3 personnel continued to telemeter their AVR statuses as ONLINE. The root cause of these instances of noncompliance was a lack of a process to ensure SW2 and SW3 telemetered the correct AVR statuses to their RC as specified. Specifically, SW2 and SW3 processes did not clearly identify the conditions in which SW2 and SW3 personnel should change the telemetered set points for their AVRs. As a result, although SW2 and SW3 personnel recognized that the WFMS was offline, they did not believe this constituted an AVR status change requiring a corresponding change in their respective Facilities’ telemetered data. Rather, SW2 and SW3 operators believed that because reactive devices and Load Tap Changers remained operational, voltage could be maintained. Further, SW2 and SW3 did not have additional controls in place, such as operator alarms, to alert their personnel of when their Facilities’ AVRs were offline. | IRO-010-1a | R3 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SW2 and SW3’s failure to properly telemeter their AVR status limited the RC’s situational awareness, but did not and could not result in unplanned tripping of the units due to undamped voltage oscillations. Given the nature of the wind turbines, localized unit tripping would remain isolated from the Bulk Electric System. Sweetwater Facilities represent a small fraction of the generation available within the Transmission Operator’s footprint and an even smaller fraction available within the ERCOT Interconnection. Furthermore, Sweetwater Facilities are comprised solely of intermittent generation and are not considered nor required for serving baseload. Finally, although Texas RE determined the issue duration at each applicable Facility was lengthy, Sweetwater Facilities did take immediate voluntary corrective action once Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. This was evidenced in the current circumstances by the fact that Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including controls to detect AVR issues and ensure accurate AVR statuses were telemetered to their RC. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that the issue only affected SW2 and SW3. Sweetwater Facilities’ share a common Point of Interconnection and throughout the issue duration the AVRs for SW4 and SW5 were online and actively regulating voltage. Due to these factors, Sweetwater Facilities collectively had compensating measures in place to help regulate voltage, and even make up for the lack of voltage control from SW2 and SW3. Second, the actual amount of SW2 and SW3’s voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and only exceeding the designated voltage schedule for the summer and winter seasons on one, limited occasion. Finally, at no time did SW2 and SW3’s RC request that SW2 and SW3 modify their actual voltage output. No harm is known to have occurred. | 6/29/2015 (the date when the WFMS was found to be offline for both Facilities and SW2 and SW3 telemetered their status as ONLINE) | 4/26/2017 (the date when SW2 restored AVR telemetry to its TOP) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2 and SW3: 1) installed a new WFMS that includes a Voltage Module (AVR Status) and returned their AVR to service so that the actual AVR status matched the telemetered status; 2) issued new IRO-010 procedures that include the current version of the Standard; 3) designed and installed alarms to notify operators when their AVR is out of service; 4) trained personnel on the operational characteristics of the new AVR and requirements to update telemetry set points provided to their RC when the AVR is offline; 5) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 6) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 7) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plants; 8) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; and 9) telemetered the status of their WFMS as the AVR statuses for each respective Facility. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to IRO-010 R3.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015776 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-1 R1. Specifically, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-1 R1.2.1 for determining Sweetwater Facilities’ respective Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not specifically include two categories of required equipment specified in FAC-008-1 R.1.2.1. First, Sweetwater Facilities’ FRM documentation failed to consider padmount transformers connected to the wind turbines. Second, Sweetwater Facilities’ FRM documentation did not include the disconnect switches located between the wind turbines and the main step up transformers at each Facility. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-1 | R1; R1.2.1 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The overall failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue, Sweetwater Facilities had controls in place to operate below the most limiting parameter, including the preventative controls in the FRM itself. Specifically the FRM included a statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. Sweetwater acknowledges that an incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum rating without compromising the omitted equipment for the duration of the issue. Second, as stated above Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 12/31/2012 (the last day FAC-008-1 R1 was enforceable) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015777 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-3 R2. In particular, Sweetwater Facilities’ documented methodology for determining Facility Ratings of their solely and jointly owned equipment connected between the high side of the main step up transformer and Sweetwater Facilities’ point of interconnection with their Transmission Owner did not specifically identify how Sweetwater Facilities considered the operational limitations of certain equipment as required under FAC-008-3 R2.2.4. Further, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-3 R2.4.1 in Sweetwater Facilities’ process for determining Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents addressing Sweetwater Facilities’ methodology for determining Facility Ratings between the high side of the main step up transformers and their point of interconnection. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not include two required elements. First, Sweetwater Facilities’ FRM did not identify how operating limitations are considered in determining equipment ratings as required by FAC-008-3 R2.2.4. In particular, Sweetwater Facilities failed to consider the operational limitations of their main 138/345 transformers in determining their overall Facility Ratings. Regarding these devices, Sweetwater Facilities’ FRM did not address the possibility that the loss of the transformers’ forced air cooling systems would require a derate of the transformers in question. Second, Sweetwater Facilities excluded two disconnect switches located between the high side of Sweetwater Facilities’ main step up transformers and the point of interconnection from their FRM documentation. The two disconnect switches constitute terminal equipment that is within the scope of equipment specifically addressed in FAC-008-3 R2.4.1. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-3 | R2; R2.2.4; R2.4.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific operational limitations on series equipment or omitting categories of series equipment altogether could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum ratings without compromising the omitted equipment for the duration of the issue. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 1/1/2013 (when the Standard became mandatory and enforceable on Sweetwater Facilities) | 1/3/2017 (the date Sweetwater Facilities revised their FRM documentation to include all required elements) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015778 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Owners (GOs), were in violation of FAC-009-1 R1 and FAC-008-3 R6. Specifically, SW2, SW3, and SW4 did not establish Facility Ratings for one of their Facilities in a manner consistent with their associated Facility Ratings methodology or documentation for determining their Facility Ratings. Texas RE subsequently determined that the duration of the issues was from April 16, 2011 until January 3, 2017. Accordingly, Texas RE determined that SW2, SW3, and SW4 each had an issue with FAC-009-1 R1 from April 16, 2011 until December 31, 2012, when that Standard was retired. SW2, SW3, and SW4 each then had an issue with FAC-008-3 R6 from January 1, 2013 until January 3, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in SW2, SW3, and SW4’s respective compliance obligations under the two applicable Standards. During the Compliance Audit, SW2 indicated that the Facility Rating for its Facility was 112.09 MVA. SW3 in turn calculated its Facility Rating as 142.76 MVA. Finally, SW4 determined that its Facility Rating was 238.68 MVA. Subsequently, Texas RE determined that in calculating these Facility Ratings, SW2, SW3, and SW4 failed to consider both their padmount transformers as well as the output of shunt capacitors located below the Facilities’ main step up transformers. When this equipment was properly considered, the main transformer or transformers at each Facility became the appropriate most limited series element. As a result, the correct rating for SW2 and SW3 should have been their main transformer 160 MVA equipment rating. Correspondingly, the Facility Rating for SW4 should have that Facility’s main transformers, which had a combined 255 MVA rating. The root cause of these violations pertained to SW2, SW3, and SW4 not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, personnel at SW2, SW3, and SW4 grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. SW2, SW3, and SW4 personnel, therefore, failed to properly identify all necessary equipment to determine the correct Facility Ratings for their respective Facilities. | FAC-009-1 FAC-008-3 | R1 R6 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. That is, because SW2, SW3, and SW4 largely failed to consider the output of their shunt capacitors, the resulting Facility Ratings were lower than their respective Facilities’ actual capabilities. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, and SW4 being 240.8 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 1/3/2017 (the date when SW2, SW3, and SW4 each properly calculated the Facility Ratings for their respective Facilities in a manner consistent with their FRM documentation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) recalculated their Facility Ratings using the correct equipment components; 3) developed a new written procedure for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015779 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-009-1 R2 and FAC-008-3 R7. Specifically, Sweetwater Facilities did not provide Facility Ratings for their respective solely and jointly owned Facilities to their associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. Texas RE subsequently determined that the duration of the issue was from April 16, 2011 until the present. Accordingly, Texas RE determined that Sweetwater Facilities had an issue with FAC-009-1 R2 from April 16, 2011 until December 31, 2012, when that Standard was retired. Sweetwater Facilities then had an issue with FAC-008-3 R6 from January 1, 2013 until the present. Texas RE further determined that, for purposes of this issue, there was no substantive change in Sweetwater Facilities’ respective compliance obligations under the two applicable Standards. During the Compliance Audit, Texas RE determined that Sweetwater Facilities did not provide Facility Ratings to their Reliability Coordinator as scheduled by such requesting entity. A “Facility Rating” is defined as the “maximum or minimum voltage, current, frequency, or real or reactive power flow through a Facility that does not violate the applicable equipment rating of any equipment comprising the Facility.” In the present circumstances, Sweetwater Facilities did not provide the maximum real power flow that would not violate applicable equipment ratings at equipment comprising its wind generation Facilities as required. In particular, the numbers Sweetwater Facilities provided to its Reliability Coordinator neither matched Sweetwater Facilities’ then current FRM nor matched the actual Facility Ratings for those Facilities. SW2 provided evidence that it had calculated the Facility Rating for its applicable Facility as 112.09 MVA. SW3 in turn calculated its Facility Rating for its applicable Facility as 142.76 MVA. SW4 determined that the Facility Rating for its applicable Facility was 238.68 MVA. Finally, SW5 calculated the Facility Rating for its applicable Facility as 89.25 MVA. However, each of the Sweetwater Facilities provided different, inaccurate Facilities Ratings to their associated Reliability Coordinator. In particular, SW2 stated in its Facility Ratings submission to its RC that the Facility Rating for its applicable Facility was 129.40 MVA. Similarly, SW3 provided a 147.66 MVA rating. SW4 in turn provided a 249.60 MVA Facility Rating to its Reliability Coordinator. Finally, SW5 provided an 89.5 MVA Facility Rating to its Reliability Coordinator. Further, none of these Facilities Ratings matched the correct Facilities Rating for the Sweetwater Facilities. The root cause of these violations pertained to Sweetwater Facilities lacking a process to compare those results and verify that the Facilities Ratings were accurate prior to the submission to their Reliability Coordinator. | FAC-009-1 FAC-008-3 | R2 R7 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. In addition, Sweetwater Facilities’ failure to provide their Reliability Coordinator with accurate Facility Ratings reduces the Reliability Coordinator’s situational awareness by impacting its ability to develop accurate operational models of real-time demands, contingency analyses, and system planning analyses. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. Moreover, the difference between the correct SW5 Facility Rating and the Facility Rating provided to SW5’s Reliability Coordinator was only 0.25 MVA, significantly reducing the possibility of an overload. Second, throughout the duration of the issue to date, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 6/28/2017 (when SW2 and SW3 submitted their Facility Ratings to the RC) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedures for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 3) developed written processes to verify Facility Ratings before submittal to the requesting Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator, as applicable; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) updated the Facility Ratings provided to their Reliability Coordinator. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015780 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Operators (GOPs), were in violation of TOP-002-2.1b R14.1. Specifically, SW2, SW3, and SW4 failed to notify their Balancing Authority (BA), without any intentional time delay, of changes in their respective real output capabilities. During the compliance audit, SW2, SW3, and SW4 provided a list of outages and derates at their respective Facilities. Based on this evidence, Texas RE determined that SW2 failed to notify its BA of five changes in SW2’s real output capability stemming from outages occurring between May 13, 2015 and September 9, 2015. The root cause of these violations is that SW2, SW3, and SW4 did not possess an adequate process to ensure that they timely communicated all changes in each Facility’s respective real output capabilities to their BA. In particular, SW2, SW3, and SW4 recorded various changes in capabilities and characteristics, including changes in real power, but SW2, SW3, and SW4’s procedures did not clearly specify the need to communicate those real output capability changes to their BA and did not include clear processes for verifying that such information was accurately provided. | TOP-002-2.1b | R14; R14.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SW2, SW3, and SW4’s failure to notify their BA of the changes to the real power capability of their respective Facilities reduced the BA’s situational awareness. In particular, the BA would not fully understand the generation resources available to respond to unplanned events or actively manage the grid. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified Texas RE also considered the fact that SW2, SW3, and SW4 lacked sufficient procedures to ensure their overall compliance with NERC Reliability Standards. In the current circumstances, SW2, SW3, and SW4 collectively failed to notify their BA of 29 changes in real output capability at the three Facilities out of 47 such occurrences, approximately 61% of all sampled occurrences during the duration of the issue. This reflects the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s respective processes for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4 respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW and SW4 being 240.8 MW. Second, the real output capability changes did not occur simultaneously at all three Facilities, further reducing their impact. Third, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of SW2, SW3, and SW4’s capacity. As such, even if additional real output had been unexpectedly needed, the ERCOT interconnection had sufficient reserves to meet that demand. Finally, SW2, SW3, and SW4 are wind generation Facilities and, as such, not normally expected to provide responsive reserves. No harm is known to have occurred. | 5/13/2015 (when SW2 first failed to notify its BA of a change in its real output capability) | 9/9/2015 (the last instance in which SW2 failed to notify its BA of a change in its real output capability) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) issued new TOP-002 procedures that align with the current version of the Standard; 2) developed new processes to verify that all required real output capability change notifications are correctly provided to the BA; 3) enhanced their communications processes to ensure that they report changes in real output capability as required in all circumstances; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) approved and issued internal compliance procedure Assessment Processes to ensure that TOP-002 is assessed for compliance; 6) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 7) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to SW2, SW3, and SW4; and 8) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties. | 2017-01-31 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to TOP-002 R14.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2016015774 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW2. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, as a Generator Owner (GO), had an issue with PRC-005-1 R2. In particular, SW2 failed to provide evidence that certain Protection System devices were maintained and tested within the defined intervals. Texas RE subsequently determined that SW2 has not completely mitigated all of its maintenance and testing issues. Accordingly, SW2 likewise had issues with PRC-005-2(i) for certain devices under the maximum maintenance intervals set forth under that Standard from October 1, 2015 until SW2 completes all required testing for those devices. During the Compliance Audit, Texas RE determined that SW2 did not possess evidence that it maintained five categories of Protection System devices within the intervals defined in various versions of its Protection System Maintenance Program (PSMP). Specifically, SW2 had issues with (1) voltage and current sensing devices; (2) dc control circuitry; (3) relays; (4) batteries; and (5) communication systems. Regarding SW2’s voltage and current sensing devices, SW2’s PSMP in effect on October 3, 2007 required testing of such Protection Systems every 24 months. Because this was SW2’s original PSMP, SW2 should have performed the initial annual testing for 29 devices as required on October 3, 2007. Subsequently, SW2 added a monthly testing requirement for its voltage and current sensing devices on April 28, 2009 and reduced the 24-month testing interval to an annual testing requirement. However, SW2 did not perform the required monthly and annual testing on 26 voltage and current sensing devices at issue until August 10, 2012. Further, SW2 failed to perform any testing on the remaining three voltage and current sensing devices. Following the August 2012 testing, SW2 should have again performed the next required test on the 26 voltage and current sensing Protection Systems at issue on September 10, 2012. However, SW2 did not perform any additional testing on these devices. On April 1, 2015, SW2 revised its PSMP to align with the PRC-005-2(i) maintenance and testing intervals. In doing so, SW2 eliminated its monthly and annual testing intervals and now performs required maintenance on its voltage and current sensing devices every 12 years per PRC-005-2(i) Table 1-3. Accordingly, SW2 will perform the next required maintenance and testing on 26 voltage and current sensing devices by August 10, 2024. For the remaining three untested voltage and current sensing devices, SW2 will complete testing as part of its Mitigation Plan. Regarding SW2’s dc control circuitry, SW2’s October 3, 2007 PSMP required annual testing for these Protection Systems. Because this was SW2’s original PSMP, SW2 should have performed the initial annual testing for three dc control circuit Protection Systems on the date it adopted the PSMP or October 3, 2007. However, SW2 failed to provide any evidence that is performed the required maintenance and testing activities on the three dc control circuit Protection Systems at issue. Regarding SW2’s relays, SW2’s October 3, 2007 PSMP required weekly, annual and 24-month testing for these Protection Systems. Because this was SW2’s original PSMP, SW2 should have performed the initial annual testing for three relay Protection Systems on the date it adopted the PSMP or October 3, 2007. However, SW2 failed to provide any evidence that it performed the required maintenance and testing activities on the three relays at issue. In addition, SW2’s applicable PSMP required monthly and annual testing of its batteries. SW2 provided evidence that it last performed testing on eight batteries on April 2, 2014. Accordingly, SW2 would have performed its next required maintenance activities on those eight batteries by May 2, 2014. However, between May 2, 2014 and September 30, 2015, SW2 failed to perform nine required monthly tests on the batteries at issue. Further, SW2 did not perform any required annual testing during this same period. On April 1, 2015, SW2 revised its PSMP to require testing at least every four or six months depending on the battery type to align its PSMP with PRC-005-2(i) Tables 1-4(a)-(d). However, SW2 could not produce evidence of the required testing on these eight batteries until December 7, 2015, when it provided evidence of required testing on seven of the eight affected batteries. SW2 subsequently performed the required testing on the eighth battery on February 1, 2017. Finally, regarding SW2’s communication systems, SW2’s April 28, 2009 PSMP required weekly and five-year testing on these devices. As such, SW2 should have performed initial maintenance activities on four communications systems at issue by April 28, 2009. However, SW2 failed to provide any evidence that it performed the required maintenance and testing activities on the four communication systems at issue. The root cause of the violation was an inadequate process for ensuring that SW2 personnel performed all required testing and maintenance activities in a timely manner. In particular, SW2 did not possess an accurate inventory of its Protection Systems, tracking required maintenance activities and the testing intervals associated with those applicable Protection Systems, and verifying results. As a result, SW2 personnel could not effectively use existing maintenance tracking systems to capture maintenance dates and testing records. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not properly maintaining the equipment could lead to misoperation of protection devices. Moreover, the issue here affected a large number of Protection Systems. Specifically, SW2 had maintenance and testing issues with 80% (47 out of 59) of its Protection Systems. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. This was evidenced in the current circumstances by the fact that Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including proper tracking of the maintenance and testing intervals in the various iterations of their PSMP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2 did not experience any misoperations during the duration of the issues in question. SW2 also produces a relatively small amount of power, with the maximum nameplate rating of 91.5 MW. Finally, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT Interconnection possessed adequate reserves to respond to any issues. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | present | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW2: 1) developed a new process to track and monitor Protection System maintenance and testing activities to ensure compliance with all applicable PRC-005 requirements; 2) completed new equipment list spreadsheets that list all equipment by component and address any missing equipment; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including training on PRC-005 maintenance and testing requirements; 7) verified the plant one-line diagrams match the as-built condition of the plants and ensure the revised equipment list conforms to SW2’s one-line diagrams; 8) reviewed all required maintenance and testing intervals to ensure their alignment with the applicable version of PRC-005; and 9) reviewed records for all identified Protection Systems to ensure maintenance and testing has been properly performed consistent with all PRC-005-6 requirements. Additionally, SW2 will complete the following mitigation actions by September 1, 2017: 1) validate all components in Maximo against the spreadsheets to assure all equipment is listed with the correct maintenance and frequency; 2) establish a new testing record archival process within the Maximo system to facilitate test record keeping and retrieval; 3) provide training to all employees that will be using Maximo as part of their daily activities, including training consists of review of documentation and hands on training in a development database; and 4) perform any additional required maintenance and testing identified during the records review for all identified Protection Systems. | 9/1/2017 (approved completion date) | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' PRC-005 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with PRC-005 include(s): TRE201100503, TRE201100504, TRE201100505, and WECC201001962. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violations pertaining to PRC-005-1 R1 (TRE201100503, TRE201100504, and TRE201100505) constituted repeat violations and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that compliance history of Sweetwater's’ affiliate, Cedar Creek Wind Energy, LLC (CCWE), should not serve as a basis for aggravating the penalty. Texas RE determined that CCWE had a previous violation with PRC-005-1 R2 (WECC201001962). In WECC201001962, CCWE failed to complete its monthly testing on one station battery for approximately six months. As a result, CCWE completed all required testing by June 1, 2008. Texas RE considers that the root causes were dissimilar because they both pertained to a separate company, a separate operations staff and a separate compliance department at the time of the violation. Moreover, Texas RE concluded that, when these violations occurred, Sweetwater did not own or was not an affiliate of these registered entities. Accordingly, Texas RE did not consider this noncompliance as an aggravating factor.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015787 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Operators (GOPs), were in violation of VAR-002-2b R2. Specifically, Sweetwater Facilities did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the TOP. During the Compliance Audit, Texas RE reviewed the seasonal voltage schedules published by Sweetwater Facilities’ TOP. The GOP is expected to maintain voltage amounts within a +/- 2.0% tolerance. Voltage amounts are measured at the Point of Interconnection. As such, because Sweetwater Facilities share a common Point of Interconnection, any voltage deviations will be the same for all four entities. Based on a review of Sweetwater Facilities’ actual voltage measured at the Point of Interconnection, Texas RE determined that Sweetwater Facilities deviated from their voltage schedules by more than +/- 2.0% for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE further determined that Sweetwater Facilities did not receive any exemptions from their TOP regarding their voltage schedule obligations. Sweetwater Facilities also did not receive any instructions from their TOP directing them to exceed the +/-2.0% tolerance throughout the duration of the issue. The root cause of this noncompliance is that Sweetwater Facilities did not have an adequate process in place to ensure they maintained their prescribed voltage schedules. While Sweetwater Facilities did have processes in place stating that they shall maintain their voltage schedule, these processes were outdated, and not current with the requirements set forth in the current version of VAR-002. More importantly, these processes did not contain clear instructions for their operating personnel to reference in regards to the methods in which Sweetwater Facilities are expected to recognize voltage deviations and subsequently act in order to maintain their voltage schedule or convey information regarding unit capabilities to their TOP. In particular, Sweetwater Facilities’ voltage excursions were almost entirely limited to the spring and fall seasons during which their TOP established lower voltage levels for Sweetwater Facilities to follow. However, Sweetwater Facilities’ personnel did not have a process for recognizing these seasonal voltage excursion issues and communicating Sweetwater Facilities’ actual seasonal voltage capabilities to their TOP. | VAR-002-2b | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure of a GOP to maintain its voltage schedule can affect voltages in the area surrounding its Point of Interconnection. Voltage instability can cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear voltage control procedures designed to ensure compliance with relevant NERC Standards. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ voltage deviations most commonly occurred while Sweetwater was producing low amounts of generation, limiting the potential impact of the voltage issues on other Transmission and Generation Facilities. Second, the actual amount of Sweetwater Facilities’ voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons only on one, limited occasion. Finally, at no time did Sweetwater Facilities’ TOP request that Sweetwater modify their voltage output. No harm is known to have occurred. | 9/1/2013 (the earliest date of deviation) | 9/29/2016 (the last recorded date of deviation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW3: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) requested new voltage schedules that were approved and are currently followed; 3) installed alarms to notify their operating personnel when voltage is out of tolerance; 4) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for Sweetwater Facilities’ operating personnel to follow in order to meet voltage schedule the recognition and reporting requirements; 5) installed new Wind Farm Management System (WFMS) that includes voltage modules (Automatic Voltage Regulator (AVR Status)) and returned their AVRs to service; 6) trained personnel on the operational characteristics of the new AVRs, including voltage control; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 9) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; and 10) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' and its affiliates' VAR-002-2b R2 compliance history in determining the penalty. Sweetwater Facilities' affiliate, Allegheny Ridge Wind Farm, LLC's (ARWF) relevant prior noncompliance with VAR-002-2b R2 include(s): RFC2015014740. Texas RE determined that ARWF's compliance history should not serve as a basis for aggravating the penalty. In RFC2015014740, RF determined during a Compliance Audit that ARWF failed to follow its issued voltage schedule on three occasions. In the current circumstances, Texas RE similarly determined that Sweetwater Facilities deviated from their issued voltage schedules for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE accordingly determined that the previous violation referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered a repeat violation. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel maintained prescribed voltage schedules, again reflecting deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015788 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW3, as a Generator Operator (GOP), was in violation of VAR-002-4 R3. Specifically, SW3 failed to notify its associated Transmission Operator (TOP) of a status change on the Automatic Voltage Regulator (AVR) within 30 minutes of the change. On June 29, 2015, SW3 performed certain reactive power tests on their respective Facilities. During the testing, SW3 personnel determined that the Wind Farm Management Systems (WFMS), which serves both Facilities, was not operational. SW3’s respective AVRs require a functioning WFMS to operate. Despite the WFMS being offline, SW3 personnel did not believe this constituted an AVR status change requiring notification as they incorrectly considered the reactive devices and Load Tap Changers to be the relevant AVR components for status change reporting purposes. Accordingly, SW3 did not notify its TOP regarding the AVR status changes in question. On December 30, 2016, SW3 replaced its WFMS and restored the AVR to service. The root cause of this instance of noncompliance was inadequate internal controls to ensure SW3 provided proper and timely notices of AVR status changes to their TOP. Specifically, SW3’s notification processes did not clearly identify both what constituted an AVR status change, as well as the conditions in which SW3 personnel should notify its TOP of such an AVR status change. Moreover, the existing processes were outdated and did not reflect current NERC requirements. Finally, SW3 did not have additional controls in place, such as operator alarms, to alert their personnel of when their Facilities’ respective AVRs were offline. | VAR-002-4 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. SW3’s failure to notify its TOP of the AVR status change limited the TOP’s situational awareness, and could have resulted in unplanned tripping of the unit due to undamped voltage oscillations. Such localized unit tripping could also cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration was lengthy, and SW3 did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including controls to detect AVR issues and ensure timely notification of those issues is provided to the TOP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that the specific issue only affected SW2 and SW3. Sweetwater Facilities share a common Point of Interconnection and throughout the issue duration the AVRs for SW4 and SW5 were online and actively regulating voltage. Due to these factors, Sweetwater Facilities collectively had compensating measures in place to help regulate voltage, and even make up for the lack of voltage control from SW2 and SW3. Second, the actual amount of SW2 and SW3’s voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons in only one, limited instance. Finally, at no time did SW3’s TOP request that SW3 modify its actual voltage output. No harm is known to have occurred. | 6/29/2015 (the earliest date Texas RE could determine SW3’s AVR to be offline and SW3 failed to notify its TOP) | 11/03/2016 (when SW3 restored its AVR to service) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW3: 1) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for SW2 and SW3’s operating personnel to follow in order to ensure proper; 2) designed and installed alarms to notify operators when their AVRs are out of service; 3) installed new WFMS that include a Voltage Modules (AVR Status) and returned their AVRs to service; 4) trained personnel on the operational characteristics of the new AVRs and requirements to update telemetry set points provided to their Reliability Coordinator (RC) when the AVRs are offline; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; and 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to VAR-002 R3.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015785 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2 and SW3, as Generator Owners (GOs) and Generator Operators (GOPs), were in violation of IRO-010-1a R3. In particular, SW2 and SW3 did not provide the accurate status of their Automatic Voltage Regulators (AVRs) through telemetry data as specified by their Reliability Coordinator (RC). On June 29, 2015, SW2 and SW3 performed certain reactive power tests on their respective Facilities. During the testing, SW2 and SW3 personnel determined that the Wind Farm Management System (WFMS), which serves both Facilities, was not operational. SW2 and SW3’s respective AVRs require a functioning WFMS to operate. Despite their AVRs being offline, SW2 and SW3 personnel continued to telemeter their AVR statuses as ONLINE. The root cause of these instances of noncompliance was a lack of a process to ensure SW2 and SW3 telemetered the correct AVR statuses to their RC as specified. Specifically, SW2 and SW3 processes did not clearly identify the conditions in which SW2 and SW3 personnel should change the telemetered set points for their AVRs. As a result, although SW2 and SW3 personnel recognized that the WFMS was offline, they did not believe this constituted an AVR status change requiring a corresponding change in their respective Facilities’ telemetered data. Rather, SW2 and SW3 operators believed that because reactive devices and Load Tap Changers remained operational, voltage could be maintained. Further, SW2 and SW3 did not have additional controls in place, such as operator alarms, to alert their personnel of when their Facilities’ AVRs were offline. | IRO-010-1a | R3 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SW2 and SW3’s failure to properly telemeter their AVR status limited the RC’s situational awareness, but did not and could not result in unplanned tripping of the units due to undamped voltage oscillations. Given the nature of the wind turbines, localized unit tripping would remain isolated from the Bulk Electric System. Sweetwater Facilities represent a small fraction of the generation available within the Transmission Operator’s footprint and an even smaller fraction available within the ERCOT Interconnection. Furthermore, Sweetwater Facilities are comprised solely of intermittent generation and are not considered nor required for serving baseload. Finally, although Texas RE determined the issue duration at each applicable Facility was lengthy, Sweetwater Facilities did take immediate voluntary corrective action once Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. This was evidenced in the current circumstances by the fact that Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including controls to detect AVR issues and ensure accurate AVR statuses were telemetered to their RC. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that the issue only affected SW2 and SW3. Sweetwater Facilities’ share a common Point of Interconnection and throughout the issue duration the AVRs for SW4 and SW5 were online and actively regulating voltage. Due to these factors, Sweetwater Facilities collectively had compensating measures in place to help regulate voltage, and even make up for the lack of voltage control from SW2 and SW3. Second, the actual amount of SW2 and SW3’s voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and only exceeding the designated voltage schedule for the summer and winter seasons on one, limited occasion. Finally, at no time did SW2 and SW3’s RC request that SW2 and SW3 modify their actual voltage output. No harm is known to have occurred. | 6/29/2015 (the date when the WFMS was found to be offline for both Facilities and SW2 and SW3 telemetered their status as ONLINE) | 3/24/2017 (the date when SW3 restored AVR telemetry to its TOP) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2 and SW3: 1) installed a new WFMS that includes a Voltage Module (AVR Status) and returned their AVR to service so that the actual AVR status matched the telemetered status; 2) issued new IRO-010 procedures that include the current version of the Standard; 3) designed and installed alarms to notify operators when their AVR is out of service; 4) trained personnel on the operational characteristics of the new AVR and requirements to update telemetry set points provided to their RC when the AVR is offline; 5) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 6) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 7) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plants; 8) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; and 9) telemetered the status of their WFMS as the AVR statuses for each respective Facility. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to IRO-010 R3.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015781 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-1 R1. Specifically, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-1 R1.2.1 for determining Sweetwater Facilities’ respective Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not specifically include two categories of required equipment specified in FAC-008-1 R.1.2.1. First, Sweetwater Facilities’ FRM documentation failed to consider padmount transformers connected to the wind turbines. Second, Sweetwater Facilities’ FRM documentation did not include the disconnect switches located between the wind turbines and the main step up transformers at each Facility. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-1 | R1; R1.2.1 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The overall failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue, Sweetwater Facilities had controls in place to operate below the most limiting parameter, including the preventative controls in the FRM itself. Specifically the FRM included a statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. Sweetwater acknowledges that an incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum rating without compromising the omitted equipment for the duration of the issue. Second, as stated above Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 12/31/2012 (the last day FAC-008-1 R1 was enforceable) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015782 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-3 R2. In particular, Sweetwater Facilities’ documented methodology for determining Facility Ratings of their solely and jointly owned equipment connected between the high side of the main step up transformer and Sweetwater Facilities’ point of interconnection with their Transmission Owner did not specifically identify how Sweetwater Facilities considered the operational limitations of certain equipment as required under FAC-008-3 R2.2.4. Further, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-3 R2.4.1 in Sweetwater Facilities’ process for determining Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents addressing Sweetwater Facilities’ methodology for determining Facility Ratings between the high side of the main step up transformers and their point of interconnection. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not include two required elements. First, Sweetwater Facilities’ FRM did not identify how operating limitations are considered in determining equipment ratings as required by FAC-008-3 R2.2.4. In particular, Sweetwater Facilities failed to consider the operational limitations of their main 138/345 transformers in determining their overall Facility Ratings. Regarding these devices, Sweetwater Facilities’ FRM did not address the possibility that the loss of the transformers’ forced air cooling systems would require a derate of the transformers in question. Second, Sweetwater Facilities excluded two disconnect switches located between the high side of Sweetwater Facilities’ main step up transformers and the point of interconnection from their FRM documentation. The two disconnect switches constitute terminal equipment that is within the scope of equipment specifically addressed in FAC-008-3 R2.4.1. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-3 | R2; R2.2.4; R2.4.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific operational limitations on series equipment or omitting categories of series equipment altogether could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum ratings without compromising the omitted equipment for the duration of the issue. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 1/1/2013 (when the Standard became mandatory and enforceable on Sweetwater Facilities) | 1/3/2017 (the date Sweetwater Facilities revised their FRM documentation to include all required elements) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015783 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Owners (GOs), were in violation of FAC-009-1 R1 and FAC-008-3 R6. Specifically, SW2, SW3, and SW4 did not establish Facility Ratings for one of their Facilities in a manner consistent with their associated Facility Ratings methodology or documentation for determining their Facility Ratings. Texas RE subsequently determined that the duration of the issues was from April 16, 2011 until January 3, 2017. Accordingly, Texas RE determined that SW2, SW3, and SW4 each had an issue with FAC-009-1 R1 from April 16, 2011 until December 31, 2012, when that Standard was retired. SW2, SW3, and SW4 each then had an issue with FAC-008-3 R6 from January 1, 2013 until January 3, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in SW2, SW3, and SW4’s respective compliance obligations under the two applicable Standards. During the Compliance Audit, SW2 indicated that the Facility Rating for its Facility was 112.09 MVA. SW3 in turn calculated its Facility Rating as 142.76 MVA. Finally, SW4 determined that its Facility Rating was 238.68 MVA. Subsequently, Texas RE determined that in calculating these Facility Ratings, SW2, SW3, and SW4 failed to consider both their padmount transformers as well as the output of shunt capacitors located below the Facilities’ main step up transformers. When this equipment was properly considered, the main transformer or transformers at each Facility became the appropriate most limited series element. As a result, the correct rating for SW2 and SW3 should have been their main transformer 160 MVA equipment rating. Correspondingly, the Facility Rating for SW4 should have that Facility’s main transformers, which had a combined 255 MVA rating. The root cause of these violations pertained to SW2, SW3, and SW4 not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, personnel at SW2, SW3, and SW4 grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. SW2, SW3, and SW4 personnel, therefore, failed to properly identify all necessary equipment to determine the correct Facility Ratings for their respective Facilities. | FAC-009-1 FAC-008-3 | R1 R6 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. That is, because SW2, SW3, and SW4 largely failed to consider the output of their shunt capacitors, the resulting Facility Ratings were lower than their respective Facilities’ actual capabilities. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, and SW4 being 240.8 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 1/3/2017 (the date when SW2, SW3, and SW4 each properly calculated the Facility Ratings for their respective Facilities in a manner consistent with their FRM documentation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) recalculated their Facility Ratings using the correct equipment components; 3) developed a new written procedure for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015784 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-009-1 R2 and FAC-008-3 R7. Specifically, Sweetwater Facilities did not provide Facility Ratings for their respective solely and jointly owned Facilities to their associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. Texas RE subsequently determined that the duration of the issue was from April 16, 2011 until the present. Accordingly, Texas RE determined that Sweetwater Facilities had an issue with FAC-009-1 R2 from April 16, 2011 until December 31, 2012, when that Standard was retired. Sweetwater Facilities then had an issue with FAC-008-3 R6 from January 1, 2013 until the present. Texas RE further determined that, for purposes of this issue, there was no substantive change in Sweetwater Facilities’ respective compliance obligations under the two applicable Standards. During the Compliance Audit, Texas RE determined that Sweetwater Facilities did not provide Facility Ratings to their Reliability Coordinator as scheduled by such requesting entity. A “Facility Rating” is defined as the “maximum or minimum voltage, current, frequency, or real or reactive power flow through a Facility that does not violate the applicable equipment rating of any equipment comprising the Facility.” In the present circumstances, Sweetwater Facilities did not provide the maximum real power flow that would not violate applicable equipment ratings at equipment comprising its wind generation Facilities as required. In particular, the numbers Sweetwater Facilities provided to its Reliability Coordinator neither matched Sweetwater Facilities’ then current FRM nor matched the actual Facility Ratings for those Facilities. SW2 provided evidence that it had calculated the Facility Rating for its applicable Facility as 112.09 MVA. SW3 in turn calculated its Facility Rating for its applicable Facility as 142.76 MVA. SW4 determined that the Facility Rating for its applicable Facility was 238.68 MVA. Finally, SW5 calculated the Facility Rating for its applicable Facility as 89.25 MVA. However, each of the Sweetwater Facilities provided different, inaccurate Facilities Ratings to their associated Reliability Coordinator. In particular, SW2 stated in its Facility Ratings submission to its RC that the Facility Rating for its applicable Facility was 129.40 MVA. Similarly, SW3 provided a 147.66 MVA rating. SW4 in turn provided a 249.60 MVA Facility Rating to its Reliability Coordinator. Finally, SW5 provided an 89.5 MVA Facility Rating to its Reliability Coordinator. Further, none of these Facilities Ratings matched the correct Facilities Rating for the Sweetwater Facilities. The root cause of these violations pertained to Sweetwater Facilities lacking a process to compare those results and verify that the Facilities Ratings were accurate prior to the submission to their Reliability Coordinator. | FAC-009-1 FAC-008-3 | R2 R7 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. In addition, Sweetwater Facilities’ failure to provide their Reliability Coordinator with accurate Facility Ratings reduces the Reliability Coordinator’s situational awareness by impacting its ability to develop accurate operational models of real-time demands, contingency analyses, and system planning analyses. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. Moreover, the difference between the correct SW5 Facility Rating and the Facility Rating provided to SW5’s Reliability Coordinator was only 0.25 MVA, significantly reducing the possibility of an overload. Second, throughout the duration of the issue to date, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 6/28/2017 (when SW2 and SW3 submitted their Facility Ratings to the RC) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedures for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 3) developed written processes to verify Facility Ratings before submittal to the requesting Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator, as applicable; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) updated the Facility Ratings provided to their Reliability Coordinator. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2016015789 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW3. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Operators (GOPs), were in violation of TOP-002-2.1b R14.1. Specifically, SW2, SW3, and SW4 failed to notify their Balancing Authority (BA), without any intentional time delay, of changes in their respective real output capabilities. During the compliance audit, SW2, SW3, and SW4 provided a list of outages and derates at their respective Facilities. Based on this evidence, Texas RE determined that SW3 failed to notify its BA of 12 changes in that Facility’s real output capability as a result of outages and derates. These 12 instances occurred between January 27, 2015 and February 16, 2016. The root cause of these violations is that SW2, SW3, and SW4 did not possess an adequate process to ensure that they timely communicated all changes in each Facility’s respective real output capabilities to their BA. In particular, SW2, SW3, and SW4 recorded various changes in capabilities and characteristics, including changes in real power, but SW2, SW3, and SW4’s procedures did not clearly specify the need to communicate those real output capability changes to their BA and did not include clear processes for verifying that such information was accurately provided. | TOP-002-2.1b | R14; R14.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SW2, SW3, and SW4’s failure to notify their BA of the changes to the real power capability of their respective Facilities reduced the BA’s situational awareness. In particular, the BA would not fully understand the generation resources available to respond to unplanned events or actively manage the grid. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified Texas RE also considered the fact that SW2, SW3, and SW4 lacked sufficient procedures to ensure their overall compliance with NERC Reliability Standards. In the current circumstances, SW2, SW3, and SW4 collectively failed to notify their BA of 29 changes in real output capability at the three Facilities out of 47 such occurrences, approximately 61% of all sampled occurrences during the duration of the issue. This reflects the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s respective processes for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4 respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, and SW4 being 240.8 MW. Second, the real output capability changes did not occur simultaneously at all three Facilities, further reducing their impact. Third, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of SW2, SW3, and SW4’s capacity. As such, even if additional real output had been unexpectedly needed, the ERCOT interconnection had sufficient reserves to meet that demand. Finally, SW2, SW3, and SW4 are wind generation Facilities and, as such, not normally expected to provide responsive reserves. No harm is known to have occurred. | 1/27/2015 (when SW3 first failed to notify its BA of a change in its real output capability) | 2/16/2016 (the last instance in which SW3 failed to notify its BA of a change in its real output capability) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) issued new TOP-002 procedures that align with the current version of the Standard; 2) developed new processes to verify that all required real output capability change notifications are correctly provided to the BA; 3) enhanced their communications processes to ensure that they report changes in real output capability as required in all circumstances; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) approved and issued internal compliance procedure Assessment Processes to ensure that TOP-002 is assessed for compliance; 6) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 7) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to SW2, SW3, and SW4; and 8) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties. | 2017-01-31 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to TOP-002 R14.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015795 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Operators (GOPs), were in violation of VAR-002-2b R2. Specifically, Sweetwater Facilities did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the TOP. During the Compliance Audit, Texas RE reviewed the seasonal voltage schedules published by Sweetwater Facilities’ TOP. The GOP is expected to maintain voltage amounts within a +/- 2.0% tolerance. Voltage amounts are measured at the Point of Interconnection. As such, because Sweetwater Facilities share a common Point of Interconnection, any voltage deviations will be the same for all four entities. Based on a review of Sweetwater Facilities’ actual voltage measured at the Point of Interconnection, Texas RE determined that Sweetwater Facilities deviated from their voltage schedules by more than +/- 2.0% for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE further determined that Sweetwater Facilities did not receive any exemptions from their TOP regarding their voltage schedule obligations. Sweetwater Facilities also did not receive any instructions from their TOP directing them to exceed the +/-2.0% tolerance throughout the duration of the issue. The root cause of this noncompliance is that Sweetwater Facilities did not have an adequate process in place to ensure they maintained their prescribed voltage schedules. While Sweetwater Facilities did have processes in place stating that they shall maintain their voltage schedule, these processes were outdated, and not current with the requirements set forth in the current version of VAR-002. More importantly, these processes did not contain clear instructions for their operating personnel to reference in regards to the methods in which Sweetwater Facilities are expected to recognize voltage deviations and subsequently act in order to maintain their voltage schedule or convey information regarding unit capabilities to their TOP. In particular, Sweetwater Facilities’ voltage excursions were almost entirely limited to the spring and fall seasons during which their TOP established lower voltage levels for Sweetwater Facilities to follow. However, Sweetwater Facilities’ personnel did not have a process for recognizing these seasonal voltage excursion issues and communicating Sweetwater Facilities’ actual seasonal voltage capabilities to their TOP. | VAR-002-2b | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure of a GOP to maintain its voltage schedule can affect voltages in the area surrounding its Point of Interconnection. Voltage instability can cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear voltage control procedures designed to ensure compliance with relevant NERC Standards. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ voltage deviations most commonly occurred while Sweetwater was producing low amounts of generation, limiting the potential impact of the voltage issues on other Transmission and Generation Facilities. Second, the actual amount of Sweetwater Facilities’ voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons only on one, limited occasion. Finally, at no time did Sweetwater Facilities’ TOP request that Sweetwater modify their voltage output. No harm is known to have occurred. | 9/1/2013 (the earliest date of deviation) | 9/29/2016 (the last recorded date of deviation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW4: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) requested new voltage schedules that were approved and are currently followed; 3) installed alarms to notify their operating personnel when voltage is out of tolerance; 4) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for Sweetwater Facilities’ operating personnel to follow in order to meet voltage schedule the recognition and reporting requirements; 5) installed new Wind Farm Management System (WFMS) that includes voltage modules (Automatic Voltage Regulator (AVR Status)) and returned their AVRs to service; 6) trained personnel on the operational characteristics of the new AVRs, including voltage control; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 9) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; and 10) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' and its affiliates' VAR-002-2b R2 compliance history in determining the penalty. Sweetwater Facilities' affiliate, Allegheny Ridge Wind Farm, LLC's (ARWF) relevant prior noncompliance with VAR-002-2b R2 include(s): RFC2015014740. Texas RE determined that ARWF's compliance history should not serve as a basis for aggravating the penalty. In RFC2015014740, RF determined during a Compliance Audit that ARWF failed to follow its issued voltage schedule on three occasions. In the current circumstances, Texas RE similarly determined that Sweetwater Facilities deviated from their issued voltage schedules for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE accordingly determined that the previous violation referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered a repeat violation. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel maintained prescribed voltage schedules, again reflecting deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015790 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-1 R1. Specifically, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-1 R1.2.1 for determining Sweetwater Facilities’ respective Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not specifically include two categories of required equipment specified in FAC-008-1 R.1.2.1. First, Sweetwater Facilities’ FRM documentation failed to consider padmount transformers connected to the wind turbines. Second, Sweetwater Facilities’ FRM documentation did not include the disconnect switches located between the wind turbines and the main step up transformers at each Facility. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-1 | R1; R1.2.1 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The overall failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue, Sweetwater Facilities had controls in place to operate below the most limiting parameter, including the preventative controls in the FRM itself. Specifically the FRM included a statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. Sweetwater acknowledges that an incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum rating without compromising the omitted equipment for the duration of the issue. Second, as stated above Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 12/31/2012 (the last day FAC-008-1 R1 was enforceable) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015791 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-3 R2. In particular, Sweetwater Facilities’ documented methodology for determining Facility Ratings of their solely and jointly owned equipment connected between the high side of the main step up transformer and Sweetwater Facilities’ point of interconnection with their Transmission Owner did not specifically identify how Sweetwater Facilities considered the operational limitations of certain equipment as required under FAC-008-3 R2.2.4. Further, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-3 R2.4.1 in Sweetwater Facilities’ process for determining Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents addressing Sweetwater Facilities’ methodology for determining Facility Ratings between the high side of the main step up transformers and their point of interconnection. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not include two required elements. First, Sweetwater Facilities’ FRM did not identify how operating limitations are considered in determining equipment ratings as required by FAC-008-3 R2.2.4. In particular, Sweetwater Facilities failed to consider the operational limitations of their main 138/345 transformers in determining their overall Facility Ratings. Regarding these devices, Sweetwater Facilities’ FRM did not address the possibility that the loss of the transformers’ forced air cooling systems would require a derate of the transformers in question. Second, Sweetwater Facilities excluded two disconnect switches located between the high side of Sweetwater Facilities’ main step up transformers and the point of interconnection from their FRM documentation. The two disconnect switches constitute terminal equipment that is within the scope of equipment specifically addressed in FAC-008-3 R2.4.1. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-3 | R2; R2.2.4; R2.4.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific operational limitations on series equipment or omitting categories of series equipment altogether could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum ratings without compromising the omitted equipment for the duration of the issue. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 1/1/2013 (when the Standard became mandatory and enforceable on Sweetwater Facilities) | 1/3/2017 (the date Sweetwater Facilities revised their FRM documentation to include all required elements) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015792 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Owners (GOs), were in violation of FAC-009-1 R1 and FAC-008-3 R6. Specifically, SW2, SW3, and SW4 did not establish Facility Ratings for one of their Facilities in a manner consistent with their associated Facility Ratings methodology or documentation for determining their Facility Ratings. Texas RE subsequently determined that the duration of the issues was from April 16, 2011 until January 3, 2017. Accordingly, Texas RE determined that SW2, SW3, and SW4 each had an issue with FAC-009-1 R1 from April 16, 2011 until December 31, 2012, when that Standard was retired. SW2, SW3, and SW4 each then had an issue with FAC-008-3 R6 from January 1, 2013 until January 3, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in SW2, SW3, and SW4’s respective compliance obligations under the two applicable Standards. During the Compliance Audit, SW2 indicated that the Facility Rating for its Facility was 112.09 MVA. SW3 in turn calculated its Facility Rating as 142.76 MVA. Finally, SW4 determined that its Facility Rating was 238.68 MVA. Subsequently, Texas RE determined that in calculating these Facility Ratings, SW2, SW3, and SW4 failed to consider both their padmount transformers as well as the output of shunt capacitors located below the Facilities’ main step up transformers. When this equipment was properly considered, the main transformer or transformers at each Facility became the appropriate most limited series element. As a result, the correct rating for SW2 and SW3 should have been their main transformer 160 MVA equipment rating. Correspondingly, the Facility Rating for SW4 should have that Facility’s main transformers, which had a combined 255 MVA rating. The root cause of these violations pertained to SW2, SW3, and SW4 not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, personnel at SW2, SW3, and SW4 grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. SW2, SW3, and SW4 personnel, therefore, failed to properly identify all necessary equipment to determine the correct Facility Ratings for their respective Facilities. | FAC-009-1 FAC-008-3 | R1 R6 | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. That is, because SW2, SW3, and SW4 largely failed to consider the output of their shunt capacitors, the resulting Facility Ratings were lower than their respective Facilities’ actual capabilities. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, and SW4 being 240.8 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 1/3/2017 (the date when SW2, SW3, and SW4 each properly calculated the Facility Ratings for their respective Facilities in a manner consistent with their FRM documentation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) recalculated their Facility Ratings using the correct equipment components; 3) developed a new written procedure for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015793 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-009-1 R2 and FAC-008-3 R7. Specifically, Sweetwater Facilities did not provide Facility Ratings for their respective solely and jointly owned Facilities to their associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. Texas RE subsequently determined that the duration of the issue was from April 16, 2011 until the present. Accordingly, Texas RE determined that Sweetwater Facilities had an issue with FAC-009-1 R2 from April 16, 2011 until December 31, 2012, when that Standard was retired. Sweetwater Facilities then had an issue with FAC-008-3 R6 from January 1, 2013 until the present. Texas RE further determined that, for purposes of this issue, there was no substantive change in Sweetwater Facilities’ respective compliance obligations under the two applicable Standards. During the Compliance Audit, Texas RE determined that Sweetwater Facilities did not provide Facility Ratings to their Reliability Coordinator as scheduled by such requesting entity. A “Facility Rating” is defined as the “maximum or minimum voltage, current, frequency, or real or reactive power flow through a Facility that does not violate the applicable equipment rating of any equipment comprising the Facility.” In the present circumstances, Sweetwater Facilities did not provide the maximum real power flow that would not violate applicable equipment ratings at equipment comprising its wind generation Facilities as required. In particular, the numbers Sweetwater Facilities provided to its Reliability Coordinator neither matched Sweetwater Facilities’ then current FRM nor matched the actual Facility Ratings for those Facilities. SW2 provided evidence that it had calculated the Facility Rating for its applicable Facility as 112.09 MVA. SW3 in turn calculated its Facility Rating for its applicable Facility as 142.76 MVA. SW4 determined that the Facility Rating for its applicable Facility was 238.68 MVA. Finally, SW5 calculated the Facility Rating for its applicable Facility as 89.25 MVA. However, each of the Sweetwater Facilities provided different, inaccurate Facilities Ratings to their associated Reliability Coordinator. In particular, SW2 stated in its Facility Ratings submission to its RC that the Facility Rating for its applicable Facility was 129.40 MVA. Similarly, SW3 provided a 147.66 MVA rating. SW4 in turn provided a 249.60 MVA Facility Rating to its Reliability Coordinator. Finally, SW5 provided an 89.5 MVA Facility Rating to its Reliability Coordinator. Further, none of these Facilities Ratings matched the correct Facilities Rating for the Sweetwater Facilities. The root cause of these violations pertained to Sweetwater Facilities lacking a process to compare those results and verify that the Facilities Ratings were accurate prior to the submission to their Reliability Coordinator. | FAC-009-1 FAC-008-3 | R2 R7 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. In addition, Sweetwater Facilities’ failure to provide their Reliability Coordinator with accurate Facility Ratings reduces the Reliability Coordinator’s situational awareness by impacting its ability to develop accurate operational models of real-time demands, contingency analyses, and system planning analyses. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. Moreover, the difference between the correct SW5 Facility Rating and the Facility Rating provided to SW5’s Reliability Coordinator was only 0.25 MVA, significantly reducing the possibility of an overload. Second, throughout the duration of the issue to date, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 6/29/2017 (when SW4 and SW5 submitted their Facility Ratings to the RC) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedures for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 3) developed written processes to verify Facility Ratings before submittal to the requesting Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator, as applicable; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) updated the Facility Ratings provided to their Reliability Coordinator. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015802 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW2, SW3, and SW4, as Generator Operators (GOPs), were in violation of TOP-002-2.1b R14.1. Specifically, SW2, SW3, and SW4 failed to notify their Balancing Authority (BA), without any intentional time delay, of changes in their respective real output capabilities. During the compliance audit, SW2, SW3, and SW4 provided a list of outages and derates at their respective Facilities. Based on this evidence, Texas RE determined that SW4 failed to notify its BA of 12 changes in SW4’s real output capability stemming from outages occurring between January 3, 2015 and February 9, 2016. The root cause of these violations is that SW2, SW3, and SW4 did not possess an adequate process to ensure that they timely communicated all changes in each Facility’s respective real output capabilities to their BA. In particular, SW2, SW3, and SW4 recorded various changes in capabilities and characteristics, including changes in real power, but SW2, SW3, and SW4’s procedures did not clearly specify the need to communicate those real output capability changes to their BA and did not include clear processes for verifying that such information was accurately provided. | TOP-002-2.1b | R14; R14.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SW2, SW3, and SW4’s failure to notify their BA of the changes to the real power capability of their respective Facilities reduced the BA’s situational awareness. In particular, the BA would not fully understand the generation resources available to respond to unplanned events or actively manage the grid. Finally, the issue duration at each applicable Facility was lengthy, and SW2, SW3, and SW4 did not detect and begin mitigation actions until Texas RE identified Texas RE also considered the fact that SW2, SW3, and SW4 lacked sufficient procedures to ensure their overall compliance with NERC Reliability Standards. In the current circumstances, SW2, SW3, and SW4 collectively failed to notify their BA of 29 changes in real output capability at the three Facilities out of 47 such occurrences, approximately 61% of all sampled occurrences during the duration of the issue. This reflects the fact that SW2, SW3, and SW4 did not effectively manage their compliance obligations. Further, SW2, SW3, and SW4’s respective processes for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that SW2, SW3, and SW4 would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, and SW4 respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW and SW4 being 240.8 MW. Second, the real output capability changes did not occur simultaneously at all three Facilities, further reducing their impact. Third, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of SW2, SW3, and SW4’s capacity. As such, even if additional real output had been unexpectedly needed, the ERCOT interconnection had sufficient reserves to meet that demand. Finally, SW2, SW3, and SW4 are wind generation Facilities and, as such, not normally expected to provide responsive reserves. No harm is known to have occurred. | 1/3/2015 (when SW4 first failed to notify its BA of a change in its real output capability) | 2/9/2016 (the last instance in which SW4 failed to notify its BA of a change in its real output capability) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, SW2, SW3, and SW4: 1) issued new TOP-002 procedures that align with the current version of the Standard; 2) developed new processes to verify that all required real output capability change notifications are correctly provided to the BA; 3) enhanced their communications processes to ensure that they report changes in real output capability as required in all circumstances; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) approved and issued internal compliance procedure Assessment Processes to ensure that TOP-002 is assessed for compliance; 6) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 7) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to SW2, SW3, and SW4; and 8) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties. | 2017-01-31 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities’ compliance history and determined there were no relevant instances of noncompliance pertaining to TOP-002 R14.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2016015794 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW4. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW4, as a Generator Owner (GO), had an issue with PRC-005-1 R2. In particular, SW4 failed to provide evidence that certain Protection System devices were maintained and tested within the defined intervals. Texas RE subsequently determined that SW4 has not completely mitigated all of its maintenance and testing issues. Accordingly, SW4 likewise had issues with PRC-005-2(i) for certain devices under the maximum maintenance intervals set forth under that Standard from October 1, 2015 until SW4 completes all required testing for those devices. During the Compliance Audit, Texas RE determined that SW4 did not possess evidence that it maintained four categories of Protection System devices within the intervals defined in various versions of its Protection System Maintenance Program (PSMP). Specifically, SW4 had issues with (1) voltage and current sensing devices; (2) dc control circuitry; (3) batteries; and (4) communications systems. Regarding SW4’s voltage and current sensing devices, SW4’s PSMP in effect on October 3, 2007 required testing of such Protection Systems every 24 months. Because this was SW4’s original PSMP, SW4 should have performed the initial annual testing for 30 devices as required on October 3, 2007. Subsequently, SW4 added a monthly testing requirement for its voltage and current sensing devices on April 28, 2009 and reduced the 24-month testing interval to an annual testing requirement. However, SW4 did not perform the required monthly and annual testing on the 30 voltage and current sensing devices at issue until August 10, 2012. Following the August 10, 2012 testing, SW4 should have again performed the next required test on its voltage and current sensing Protection Systems on September 10, 2012. However, SW4 did not perform any additional testing on these devices. On April 1, 2015, SW4 revised its PSMP to align with the PRC-005-2(i) maintenance and testing intervals. In doing so, SW4 eliminated its monthly and annual testing intervals and now performs required maintenance on its voltage and current sensing devices every 12 years per PRC-005-2(i) Table 1-3. Accordingly, SW4 will perform the next required maintenance and testing on these devices by August 10, 2024. Regarding SW4’s dc control circuitry, SW4’s PSMP dated October 3, 2007 required annual testing for these Protection Systems. Because this was SW4’s original PSMP, SW4 should have performed the initial annual testing for four dc control circuit Protection Systems on the date it adopted the PSMP or October 3, 2007. However, SW4 failed to provide any evidence that is performed the required maintenance and testing activities on the four dc control circuit Protection Systems at issue. Regarding SW4’s batteries, SW4’s initial PSMP required monthly and annual testing of its batteries. SW4 provided evidence that it last performed testing on two batteries on April 3, 2014. Accordingly, SW4 would have performed its next required maintenance activities on those two batteries by May 3, 2014. However, SW4 failed to perform either the requisite monthly or annual testing as required. On April 1, 2015, SW4 revised its PSMP to require testing at least every four months to align its PSMP with PRC-005-2(i) Tables 1-4(a). However, under either version of the SW4’s PSMP, SW4 failed to perform all required testing until February 15, 2016. Finally, regarding SW4’s communications systems, SW4’s April 28, 2009 PSMP required weekly and five-year testing on these devices. As such, SW4 should have performed initial maintenance activities on one communications system by April 28, 2009. However, SW4 failed to provide any evidence that it performed the required maintenance and testing activities on the single communication systems at issue. The root cause of the violation was an inadequate process for ensuring that SW4 personnel performed all required testing and maintenance activities in a timely manner. In particular, SW4 did not possess an accurate inventory of its Protection Systems, tracking required maintenance activities and the testing intervals associated with those applicable Protection Systems, and verifying results. As a result, SW4 personnel could not effectively use existing maintenance tracking systems to capture maintenance dates and testing records. | PRC-005-1 | R2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not properly maintaining the equipment could lead to misoperation of protection devices. Moreover, the issue here affected a significant number of Protection Systems at Sweetwater Facilities. Specifically, SW4 had maintenance and testing issues with 66% (37 out of 56) of its Protection Systems. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. This was evidenced in the current circumstances by the fact that Sweetwater Facilities did not possess clear procedures designed to ensure compliance with relevant NERC Standards, including proper tracking of the maintenance and testing intervals in the various iterations of their PSMP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW4 only experienced a single misoperation during the five-year duration of the issues in question. SW4 also produces a relatively small amount of power, with the maximum nameplate rating of 240.8 MW. Finally, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT Interconnection possessed adequate reserves to respond to any issues. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | present | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate the violation, SW4: 1) developed a new process to track and monitor Protection System maintenance and testing activities to ensure compliance with all applicable PRC-005 requirements; 2) completed new equipment list spreadsheets that list all equipment by component and address any missing equipment; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including training on PRC-005 maintenance and testing requirements; 7) verify the plant one-line diagrams match the as-built condition of the plants and ensure the revised equipment list conforms to SW4’s one-line diagrams; 8) review all required maintenance and testing intervals to ensure their alignment with the applicable version of PRC-005; and 9) review records for all identified Protection Systems to ensure maintenance and testing has been properly performed consistent with all PRC-005-6 requirements. Additionally, SW4 will complete the following mitigation actions by September 1, 2017: 1) validate all components in Maximo against the spreadsheets to assure all equipment is listed with the correct maintenance and frequency; 2) establish a new testing record archival process within the Maximo system to facilitate test record keeping and retrieval; 3) provide training to all employees that will be using Maximo as part of their daily activities, including training consists of review of documentation and hands on training in a development database; and 4) perform any additional required maintenance and testing identified during the records review for all identified Protection Systems. | 9/1/2017 (approved completion date) | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' PRC-005 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with PRC-005 include(s): TRE201100503, TRE201100504, TRE201100505, and WECC201001962. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violations pertaining to PRC-005-1 R1 (TRE201100503, TRE201100504, and TRE201100505) constituted repeat violations and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that compliance history of Sweetwater's’ affiliate, Cedar Creek Wind Energy, LLC (CCWE), should not serve as a basis for aggravating the penalty. Texas RE determined that CCWE had a previous violation with PRC-005-1 R2 (WECC201001962). In WECC201001962, CCWE failed to complete its monthly testing on one station battery for approximately six months. As a result, CCWE completed all required testing by June 1, 2008. Texas RE considers that the root causes were dissimilar because they both pertained to a separate company, a separate operations staff and a separate compliance department at the time of the violation. Moreover, Texas RE concluded that, when these violations occurred, Sweetwater did not own or was not an affiliate of these registered entities. Accordingly, Texas RE did not consider this noncompliance as an aggravating factor.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2016015801 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW5. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Operators (GOPs), were in violation of VAR-002-2b R2. Specifically, Sweetwater Facilities did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the TOP. During the Compliance Audit, Texas RE reviewed the seasonal voltage schedules published by Sweetwater Facilities’ TOP. The GOP is expected to maintain voltage amounts within a +/- 2.0% tolerance. Voltage amounts are measured at the Point of Interconnection. As such, because Sweetwater Facilities share a common Point of Interconnection, any voltage deviations will be the same for all four entities. Based on a review of Sweetwater Facilities’ actual voltage measured at the Point of Interconnection, Texas RE determined that Sweetwater Facilities deviated from their voltage schedules by more than +/- 2.0% for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE further determined that Sweetwater Facilities did not receive any exemptions from their TOP regarding their voltage schedule obligations. Sweetwater Facilities also did not receive any instructions from their TOP directing them to exceed the +/-2.0% tolerance throughout the duration of the issue. The root cause of this noncompliance is that Sweetwater Facilities did not have an adequate process in place to ensure they maintained their prescribed voltage schedules. While Sweetwater Facilities did have processes in place stating that they shall maintain their voltage schedule, these processes were outdated, and not current with the requirements set forth in the current version of VAR-002. More importantly, these processes did not contain clear instructions for their operating personnel to reference in regards to the methods in which Sweetwater Facilities are expected to recognize voltage deviations and subsequently act in order to maintain their voltage schedule or convey information regarding unit capabilities to their TOP. In particular, Sweetwater Facilities’ voltage excursions were almost entirely limited to the spring and fall seasons during which their TOP established lower voltage levels for Sweetwater Facilities to follow. However, Sweetwater Facilities’ personnel did not have a process for recognizing these seasonal voltage excursion issues and communicating Sweetwater Facilities’ actual seasonal voltage capabilities to their TOP. | VAR-002-2b | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure of a GOP to maintain its voltage schedule can affect voltages in the area surrounding its Point of Interconnection. Voltage instability can cause other Generation Facilities in the surrounding area to trip offline, which can lead to further voltage collapse. Additionally, high or low voltages can overload nearby Transmission Facilities and possibly damage equipment. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not possess clear voltage control procedures designed to ensure compliance with relevant NERC Standards. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ voltage deviations most commonly occurred while Sweetwater was producing low amounts of generation, limiting the potential impact of the voltage issues on other Transmission and Generation Facilities. Second, the actual amount of Sweetwater Facilities’ voltage deviations were limited, representing less than a +/-3.0% deviation from the designated voltage schedule and exceeding the designated voltage schedule for the summer and winter seasons only on one, limited occasion. Finally, at no time did Sweetwater Facilities’ TOP request that Sweetwater modify their voltage output. No harm is known to have occurred. | 9/1/2013 (the earliest date of deviation) | 9/29/2016 (the last recorded date of deviation) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate this violation, SW5: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) requested new voltage schedules that were approved and are currently followed; 3) installed alarms to notify their operating personnel when voltage is out of tolerance; 4) issued new VAR-002 procedures that align with the current version of the Standard and will provide instructions for Sweetwater Facilities’ operating personnel to follow in order to meet voltage schedule the recognition and reporting requirements; 5) installed new Wind Farm Management System (WFMS) that includes voltage modules (Automatic Voltage Regulator (AVR Status)) and returned their AVRs to service; 6) trained personnel on the operational characteristics of the new AVRs, including voltage control; 7) conducted training on the new documented internal compliance programs for all personnel with NERC compliance-related duties, including Sweetwater Facilities’ voltage schedule obligations; 8) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 9) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; and 10) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities. | 2017-04-26 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' and its affiliates' VAR-002-2b R2 compliance history in determining the penalty. Sweetwater Facilities' affiliate, Allegheny Ridge Wind Farm, LLC's (ARWF) relevant prior noncompliance with VAR-002-2b R2 include(s): RFC2015014740. Texas RE determined that ARWF's compliance history should not serve as a basis for aggravating the penalty. In RFC2015014740, RF determined during a Compliance Audit that ARWF failed to follow its issued voltage schedule on three occasions. In the current circumstances, Texas RE similarly determined that Sweetwater Facilities deviated from their issued voltage schedules for approximately 8.86% of the hours between the earliest date for which Texas RE could obtain voltage data and the date Sweetwater Facilities mitigated their voltage issue. Texas RE accordingly determined that the previous violation referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered a repeat violation. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel maintained prescribed voltage schedules, again reflecting deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2016015796 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW5. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-1 R1. Specifically, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-1 R1.2.1 for determining Sweetwater Facilities’ respective Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not specifically include two categories of required equipment specified in FAC-008-1 R.1.2.1. First, Sweetwater Facilities’ FRM documentation failed to consider padmount transformers connected to the wind turbines. Second, Sweetwater Facilities’ FRM documentation did not include the disconnect switches located between the wind turbines and the main step up transformers at each Facility. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-1 | R1; R1.2.1 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The overall failure to consider specific series equipment could have resulted in incorrect Facility Ratings at each Facility at issue, Sweetwater Facilities had controls in place to operate below the most limiting parameter, including the preventative controls in the FRM itself. Specifically the FRM included a statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. Sweetwater acknowledges that an incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages at the Facility. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum rating without compromising the omitted equipment for the duration of the issue. Second, as stated above Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 12/31/2012 (the last day FAC-008-1 R1 was enforceable) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2016015797 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW5. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-008-3 R2. In particular, Sweetwater Facilities’ documented methodology for determining Facility Ratings of their solely and jointly owned equipment connected between the high side of the main step up transformer and Sweetwater Facilities’ point of interconnection with their Transmission Owner did not specifically identify how Sweetwater Facilities considered the operational limitations of certain equipment as required under FAC-008-3 R2.2.4. Further, the documentation used by Sweetwater Facilities to develop their Facility Ratings did not include all required equipment specified in FAC-008-3 R2.4.1 in Sweetwater Facilities’ process for determining Facility Ratings. During the Compliance Audit, Texas RE reviewed Sweetwater Facilities’ Facility Ratings Methodology (FRM) documents addressing Sweetwater Facilities’ methodology for determining Facility Ratings between the high side of the main step up transformers and their point of interconnection. Based on this review, Texas RE determined that Sweetwater Facilities’ FRM documentation did not include two required elements. First, Sweetwater Facilities’ FRM did not identify how operating limitations are considered in determining equipment ratings as required by FAC-008-3 R2.2.4. In particular, Sweetwater Facilities failed to consider the operational limitations of their main 138/345 transformers in determining their overall Facility Ratings. Regarding these devices, Sweetwater Facilities’ FRM did not address the possibility that the loss of the transformers’ forced air cooling systems would require a derate of the transformers in question. Second, Sweetwater Facilities excluded two disconnect switches located between the high side of Sweetwater Facilities’ main step up transformers and the point of interconnection from their FRM documentation. The two disconnect switches constitute terminal equipment that is within the scope of equipment specifically addressed in FAC-008-3 R2.4.1. The root cause of these violations pertained to Sweetwater Facilities not possessing detailed written procedures for tracking equipment, comparing equipment lists to one-line diagrams, determining Facility Ratings, and verifying results. As a result, Sweetwater Facilities’ personnel grouped certain equipment in the Facility Ratings process rather than identifying each equipment component in series to calculate and document the ultimate Facility Rating. Sweetwater Facilities personnel, therefore, failed to properly identify and document the equipment ratings of all required equipment in determining each Facility’s respective Facility Ratings. | FAC-008-3 | R2; R2.2.4; R2.4.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to consider specific operational limitations on series equipment or omitting categories of series equipment altogether could have resulted in incorrect Facility Ratings at each Facility at issue. An incorrect Facility Rating in turn could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that the Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that Sweetwater Facilities’ overall Facility Ratings did not change as a result of incorporating the omitted equipment categories into their Facility Ratings documentation. Because the omitted equipment did not limit the output of the turbines and capacitors, Sweetwater Facilities could operate a full output up to their maximum ratings without compromising the omitted equipment for the duration of the issue. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 1/1/2013 (when the Standard became mandatory and enforceable on Sweetwater Facilities) | 1/3/2017 (the date Sweetwater Facilities revised their FRM documentation to include all required elements) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedure for calculating Facility Ratings, including processes for validating the Facility Rating spreadsheets against one-line diagrams and as-built Facility conditions to ensure their accuracy; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 7) verified the plant one-line diagrams match Facility one-line diagrams, as well as the as-built condition of the affected Facilities; and 8) notified their associated Reliability Coordinator, Planning Coordinator, Transmission Planner, Transmission Owner, and Transmission Operator of any updated Facility Ratings resulting from the equipment verification process at each Facility. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2016015799 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW5. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that Sweetwater Facilities, as Generator Owners (GOs), were in violation of FAC-009-1 R2 and FAC-008-3 R7. Specifically, Sweetwater Facilities did not provide Facility Ratings for their respective solely and jointly owned Facilities to their associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. Texas RE subsequently determined that the duration of the issue was from April 16, 2011 until the present. Accordingly, Texas RE determined that Sweetwater Facilities had an issue with FAC-009-1 R2 from April 16, 2011 until December 31, 2012, when that Standard was retired. Sweetwater Facilities then had an issue with FAC-008-3 R6 from January 1, 2013 until the present. Texas RE further determined that, for purposes of this issue, there was no substantive change in Sweetwater Facilities’ respective compliance obligations under the two applicable Standards. During the Compliance Audit, Texas RE determined that Sweetwater Facilities did not provide Facility Ratings to their Reliability Coordinator as scheduled by such requesting entity. A “Facility Rating” is defined as the “maximum or minimum voltage, current, frequency, or real or reactive power flow through a Facility that does not violate the applicable equipment rating of any equipment comprising the Facility.” In the present circumstances, Sweetwater Facilities did not provide the maximum real power flow that would not violate applicable equipment ratings at equipment comprising its wind generation Facilities as required. In particular, the numbers Sweetwater Facilities provided to its Reliability Coordinator neither matched Sweetwater Facilities’ then current FRM nor matched the actual Facility Ratings for those Facilities. SW2 provided evidence that it had calculated the Facility Rating for its applicable Facility as 112.09 MVA. SW3 in turn calculated its Facility Rating for its applicable Facility as 142.76 MVA. SW4 determined that the Facility Rating for its applicable Facility was 238.68 MVA. Finally, SW5 calculated the Facility Rating for its applicable Facility as 89.25 MVA. However, each of the Sweetwater Facilities provided different, inaccurate Facilities Ratings to their associated Reliability Coordinator. In particular, SW2 stated in its Facility Ratings submission to its RC that the Facility Rating for its applicable Facility was 129.40 MVA. Similarly, SW3 provided a 147.66 MVA rating. SW4 in turn provided a 249.60 MVA Facility Rating to its Reliability Coordinator. Finally, SW5 provided an 89.5 MVA Facility Rating to its Reliability Coordinator. Further, none of these Facilities Ratings matched the correct Facilities Rating for the Sweetwater Facilities. The root cause of these violations pertained to Sweetwater Facilities lacking a process to compare those results and verify that the Facilities Ratings were accurate prior to the submission to their Reliability Coordinator. | FAC-009-1 FAC-008-3 | R2 R7 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An incorrect Facility Rating could result in overloading on equipment, potentially damaging the affected Facilities and resulting in unanticipated outages. In addition, Sweetwater Facilities’ failure to provide their Reliability Coordinator with accurate Facility Ratings reduces the Reliability Coordinator’s situational awareness by impacting its ability to develop accurate operational models of real-time demands, contingency analyses, and system planning analyses. Finally, the issue duration at each applicable Facility was lengthy, and Sweetwater Facilities did not detect and begin mitigation actions until Texas RE identified the issues during the Compliance Audit. Texas RE also considered the fact that Sweetwater Facilities did not effectively manage their compliance obligations. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW2, SW3, SW4’s inaccurate Facility Ratings were more conservative than the Facilities’ actual capabilities. Moreover, the difference between the correct SW5 Facility Rating and the Facility Rating provided to SW5’s Reliability Coordinator was only 0.25 MVA, significantly reducing the possibility of an overload. Second, throughout the duration of the issue to date, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT interconnection possessed adequate reserves to respond to any issues. Finally, Sweetwater Facilities respectively produce a relatively small amount of power, with the maximum nameplate rating for SW2 being 91.5 MW, SW3 being 135 MW, SW4 being 240.8 MW, and SW5 being 80.5 MW. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | 6/29/2017 (when SW4 and SW5 submitted their Facility Ratings to the RC) | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate these violations, Sweetwater Facilities: 1) completed new Facility Rating spreadsheets that list all equipment by component and address specific missing equipment; 2) developed new written procedures for calculating Facility Ratings, including a process for validating the Facility Rating spreadsheet against one-line diagrams and as-built Facility condition to ensure their accuracy; 3) developed written processes to verify Facility Ratings before submittal to the requesting Reliability Coordinator, Planning Authority, Transmission Planner, and Transmission Operator, as applicable; 4) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 5) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to the plant; 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance-related duties, including the new Facility Rating process; 8) verified the plant one-line diagrams match the as-built condition of the plants; and 9) updated the Facility Ratings provided to their Reliability Coordinator. | 2017-06-30 | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' FAC-008 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with FAC-008 include(s): TRE201100507, RFC2015014711, RFC2015014712, and RFC2015014730. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violation pertaining to FAC-008-1 R1 (TRE201100507) for Sweetwater Wind 5 LLC (SW5) constituted a repeat violation and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that the compliance history of Sweetwater's’ affiliate, Allegheny Ridge Wind Farm, LLC (ARWF), should not serve as a basis for aggravating the penalty. Texas RE determined that ARWF's had previous violations with FAC-008-1 R1 (RFC2015014711), FAC-008-1 R2 (RFC2015014712), and FAC-008-3 R6 (RFC2015014730). In RFC201514711, RFC201514712 and RFC201514730, RF determined during a Compliance Audit that ARWF failed to properly document and calculate its Facility Ratings. Texas RE determined that the previous violations referenced above pertained to similar circumstances, but the duration of the issues overlapped and should not be considered repeat violations. Nevertheless, Texas RE did consider the root cause of both issues to be related to inadequate processes for ensuring that Sweetwater Facilities and ARWF personnel accurately developed, calculated, and reported all Facility Ratings. Texas RE further determined that ARWF’s failures to timely establish a Facility Rating Methodology, as well as Sweetwater Facilities’ overall issues with calculating Facility Ratings reflected the deficiencies in Sweetwater Facilities’ ICP.
Texas Reliability Entity, Inc. (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2016015800 | Settlement Agreement | Sweetwater Wind 2 LLC (SW2), Sweetwater Wind 3 LLC (SW3), Sweetwater Wind 4 LLC (SW4), and Sweetwater Wind 5 LLC (SW5) are collectively referred to as Sweetwater Facilities. This violation pertains to SW5. During a Compliance Audit conducted from April 26, 2016 through May 23, 2016, Texas RE determined that SW5, as a Generator Owner (GO), was in violation of PRC-005-1 R2. In particular, SW5 failed to provide evidence that Protection System devices were maintained and tested within the defined intervals. Texas RE subsequently determined that SW5 has not completely mitigated all of its maintenance and testing issues. Accordingly, SW5 likewise had issues with PRC-005-2(i) for certain devices under the maximum maintenance intervals set forth under that Standard from October 1, 2015 until SW5 completes all required testing for those devices. During the Compliance Audit, Texas RE determined that SW5 did not possess evidence that it maintained three categories of Protection System devices within the intervals defined in various versions of its Protection System Maintenance Program (PSMP). Specifically, SW5 had issues with (1) voltage and current sensing devices; (2) dc control circuitry; and (3) communications systems. Regarding SW5’s voltage and current sensing devices, SW5’s PSMP in effect on October 3, 2007 required testing of such Protection Systems every 24 months. Because this was SW5’s original PSMP, SW5 should have performed the initial annual testing for 27 devices as required on its Generator Owner registration date of November 1, 2007. Subsequently, SW5 added a monthly testing requirement for its voltage and current sensing devices on April 28, 2009 and reduced the 24-month testing interval to an annual testing requirement. However, SW5 did not perform the required monthly and annual testing on the 27 voltage and current sensing devices at issue until August 1, 2012. Following the August 1, 2012 testing, SW5 should have again performed the next required test on the 27 voltage and current sensing Protection Systems at issue on September 1, 2012. However, SW5 did not perform any additional testing on these devices. On April 1, 2015, SW5 revised its PSMP to align with the PRC-005-2(i) maintenance and testing intervals. In doing so, SW5 eliminated its monthly and annual testing intervals and now performs required maintenance on its voltage and current sensing devices every 12 years per PRC-005-2(i) Table 1-3. Accordingly, SW5 will perform the next required maintenance and testing on these devices by August 1, 2024. Regarding SW5’s dc control circuitry, SW5’s PSMP dated October 3, 2007 required annual testing for these Protection Systems. Because this was SW5’s original PSMP, SW5 should have performed the initial annual testing for 10 dc control circuit Protection Systems on the date it was registered as a Generator Owner on November 1, 2007. However, SW5 failed to provide any evidence that is performed the required maintenance and testing activities on the 10 dc control circuit Protection Systems at issue. Finally, regarding SW5’s communications systems, SW5’s April 28, 2009 PSMP required weekly and five-year testing on these devices. As such, SW5 should have performed initial maintenance activities on three communications systems by April 28, 2009. However, SW5 failed to provide any evidence that it performed the required maintenance and testing activities on the three communication systems at issue. The root cause of the violation was an inadequate process for ensuring that SW5 personnel performed all required testing and maintenance activities in a timely manner. In particular, SW5 did not possess an accurate inventory of its Protection Systems, tracking required maintenance activities and the testing intervals associated with those applicable Protection Systems, and verifying results. As a result, SW5 personnel could not effectively use existing maintenance tracking systems to capture maintenance dates and testing records. | PRC-005-1 | R2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not properly maintaining the equipment could lead to misoperation of protection devices. Moreover, the issue here affected a significant number of Protection Systems. Specifically, SW5 had maintenance and testing issues with 74% (40 out of 54) of its Protection Systems. Texas RE also considered the fact that the Sweetwater Facilities did not possess proper tracking of the maintenance and testing intervals in the various iterations of their PSMP. Further, Sweetwater Facilities’ process for monitoring their compliance obligations and fostering a robust internal compliance culture was lacking. Therefore, there was an additional risk that Sweetwater Facilities would not have detected the issues identified during the Texas RE Compliance Audit. As a result, these issues could have become more severe or widespread. Balanced against this fact is that SW5 did not experience any misoperations during the duration of the issues in question. Further, SW5 also produces a relatively small amount of power, with the maximum nameplate rating of 80.5 MW. Finally, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves in excess of the Sweetwater Facilities corresponding generation output. As such, even if one or all of the Sweetwater Facilities had tripped offline, the ERCOT Interconnection possessed adequate reserves to respond to any issues. No harm is known to have occurred. | 4/16/2011 (the day following the end of the previous Compliance Audit) | present | $80,000 (for TRE2016015770, TRE2016015771, TRE2016015772, TRE2016015773, TRE2016015774, TRE2016015776, TRE2016015777, TRE2016015778, TRE2016015779, TRE2016015780, TRE2016015781, TRE2016015782, TRE2016015783, TRE2016015784, TRE2016015785, TRE2016015786, TRE2016015787, TRE2016015788, TRE2016015789, TRE2016015790, TRE2016015791, TRE2016015792, TRE2016015793, TRE2016015794, TRE2016015795, TRE2016015796, TRE2016015797, TRE2016015799, TRE2016015800, TRE2016015801, and TRE2016015802) | Compliance Audit | To mitigate the violation, SW5: 1) developed a new process to track and monitor Protection System maintenance and testing activities to ensure compliance with all applicable PRC-005 requirements; 2) completed new equipment list spreadsheets that list all equipment by component and address any missing equipment; 3) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ chief operating officer; 4) developed new internal compliance review processes that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every NERC standard applicable to Sweetwater Facilities; and 6) conducted training on the new documented internal compliance program (ICP) for all personnel with NERC compliance-related duties, including training on PRC-005 maintenance and testing requirements; 7) verify the plant one-line diagrams match the as-built condition of the plants and ensure the revised equipment list conforms to SW5’s one-line diagrams; 8) review all required maintenance and testing intervals to ensure their alignment with the applicable version of PRC-005; and 9) review records for all identified Protection Systems to ensure maintenance and testing has been properly performed consistent with all PRC-005-6 requirements. Additionally, SW5 will complete the following mitigation actions by September 1, 2017: 1) validate all components in Maximo against the spreadsheets to assure all equipment is listed with the correct maintenance and frequency; 2) establish a new testing record archival process within the Maximo system to facilitate test record keeping and retrieval; 3) provide training to all employees that will be using Maximo as part of their daily activities, including training consists of review of documentation and hands on training in a development database; and 4) perform any additional required maintenance and testing identified during the records review for all identified Protection Systems. | 9/1/2017 (approved completion date) | TBD | Admits | Texas RE found that Sweetwater Facilities’ internal compliance program (ICP), as implemented by Leeward, was deficient and was a contributing factor to the violations discovered during the Compliance Audit. This included a lack of effective management oversight of compliance personnel, which manifested itself both in the number of issues found during the Compliance Audit and the general issues Sweetwater Facilities’ experienced in providing accurate and timely responses to demonstrate their compliance with NERC Reliability Standards. As a result, Texas RE did not award any mitigating credit for Sweetwater Facilities’ ICP. Sweetwater Facilities have been improving their ICP. As detailed in the mitigating activities, Sweetwater Facilities hired a new director of regulatory compliance that will report directly to the chief operating officer. Sweetwater Facilities have also retained a third-party consultant with extensive NERC experience to support Sweetwater Facilities’ overall NERC compliance program. Sweetwater Facilities’ consultant performed a detailed review of the existing ICP and developed a phased plan to improve the program. The initial phase of Sweetwater Facilities’ ICP enhancement program began on August 15, 2016. Sweetwater Facilities’ consultants engaged in a review of Sweetwater Facilities’ existing ICP and related procedures. The consultants also met with Leeward’s compliance personnel to participate in a compliance kick-off meeting from August 16-19, 2016. Based on these meetings and review, Leeward’s consultants developed new processes, procedures, and a new ICP for Sweetwater Facilities. Sweetwater Facilities’ consultant, in coordination with the new director of regulatory compliance, then developed new procedures and internal controls to ensure continuing compliance beyond the specific issues noted in the Compliance Audit. These steps included: (1) development and control of policies and procedures; (2) reliability and compliance assessment process and procedures; and (3) a detailed Self-Certification process and procedure. Sweetwater Facilities have also begun to provide training to applicable personnel to ensure that they understand and comply with the ICP and all applicable NERC Standards. Leeward, acting on behalf of Sweetwater Facilities, implemented its new ICP and supporting procedures during the week of September 19, 2016. As part of Sweetwater Facilities’ new ICP, Sweetwater Facilities’ chief operating officer now meets regularly with the new director of regulatory compliance. The chief operating officer is also part of regularly scheduled meetings with the consulting team and director of regulatory compliance to consider and review progress made toward implementing the new ICP. Finally, as detailed above, Sweetwater Facilities’ chief operating officer and director of regulatory compliance now conduct monthly meetings with Sweetwater Facilities’ chief executive officer to provide updates on the mitigation activities and to maintain engagement with senior management on regulatory compliance matters. In addition to ICP enhancements, Leeward and Sweetwater Facilities personnel conduct weekly meetings with their consultants to discuss ongoing compliance activities, upcoming submittals, the status of any Mitigation Plans, and long-term horizon planning activities. In addition, these consultants provide assistance to Sweetwater Facilities and Leeward with compliance filings and other NERC submissions. To support the overall Sweetwater Facilities compliance enhancement process, Sweetwater Facilities are developing and implementing a compliance tracking system for ongoing NERC compliance activities. In addition to training on the new ICP and related procedures, Sweetwater Facilities’ have implemented a Compliance Training Process and Procedure. Under this training program, Sweetwater Facilities personnel will be trained, among other things, on the results of the Texas RE Compliance Audit, the specific violations discussed in this disposition, and the appropriate compliance responsibilities, mitigation and lessons learned to prevent their recurrence. At the end of 2016, the new director of regulatory compliance and chief operating officer required the Sweetwater Facilities’ consultants develop a similar plan for four additional Leeward registered entities in the WECC, SPP RE, and RF regions. Combined, Leeward estimates it has committed several hundred thousand dollars to improving its ICP since the Texas RE audit. Texas RE considered Sweetwater Facilities' PRC-005 compliance history in determining the penalty. Sweetwater Facilities' and its affiliates' relevant prior noncompliance with PRC-005 include(s): TRE201100503, TRE201100504, TRE201100505, and WECC201001962. Texas RE considered Sweetwater Facilities’ compliance history and determined that the previous violations pertaining to PRC-005-1 R1 (TRE201100503, TRE201100504, and TRE201100505) constituted repeat violations and therefore was an aggravating factor in the overall penalty determination. Texas RE also determined that compliance history of Sweetwater's’ affiliate, Cedar Creek Wind Energy, LLC (CCWE), should not serve as a basis for aggravating the penalty. Texas RE determined that CCWE had a previous violation with PRC-005-1 R2 (WECC201001962). In WECC201001962, CCWE failed to complete its monthly testing on one station battery for approximately six months. As a result, CCWE completed all required testing by June 1, 2008. Texas RE considers that the root causes were dissimilar because they both pertained to a separate company, a separate operations staff and a separate compliance department at the time of the violation. Moreover, Texas RE concluded that, when these violations occurred, Sweetwater did not own or was not an affiliate of these registered entities. Accordingly, Texas RE did not consider this noncompliance as an aggravating factor.