## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
ReliabilityFirst Corporation (ReliabilityFirst) | Potomac Electric Power Company (Pepco) | NCR00881 | RFC2015015290 | Settlement Agreement | On October 16, 2015, Pepco submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-005-1b R2. After a low voltage disturbance event in the Washington D.C. area on April 7, 2015 (the DC Event), ReliabilityFirst initiated its compliance assessment process with Pepco. As part of that process, ReliabilityFirst requested certain Pepco Protection System Maintenance and Testing Program (Testing Program). ReliabilityFirst determined the violation of PRC-005-1b R2 was not a causal factor in the DC Event. Pepco provided its PRC-005 test records and procedures associated with its 2012 testing cycle (the last testing cycle before the DC Event), for the 23071 and 23072 terminals at the Morgantown, Ryceville, and Chalk Point Substations. Pepco’s PRC-005 procedures stated breaker trip tests be conducted in conjunction with the 4 year relay test cycle. Pepco’s relay test records for the 23071 and 23072 terminals at the Morgantown, Ryceville, and Chalk Point Substations did not show that Pepco completed the breaker trip tests in conjunction with the last line relay test cycle in 2012. Specifically, with regard to the Chalk Point 2C breaker (the breaker involved in the DC Event), Pepco provided evidence of the breaker being tripped upon commissioning in 2010 and subsequently again in 2014 as the result of a system fault, but could not provide evidence that the breaker was tripped in conjunction with the 2012 line relay test. Therefore, Pepco could not demonstrate that it followed its PRC-005 testing procedures or that it completed its 2012 relay test. Even if Pepco had performed the breaker trip test as scheduled in 2012, Pepco may not have found the loose connection because Pepco’s program did not require checking for the existence of such conditions. In fact, most PRC-005 maintenance and testing programs do not contain this check step because it is both impractical and of limited benefit. Checking for loose connections introduces human error that can result in damaged equipment. Further, there is no evidence that loose connections are a systemic issue across the Electric Reliability Organization (ERO) causing negative impacts to the Bulk Electric System (BES). While a loose connection associated with the Chalk Point 2C breaker was among the causal factors that contributed to the protracted clearing of the fault in the DC Event, the breaker at issue was tripped as a result of a fault in July 2014 and performed correctly. This further supports the conclusion that an absence of a breaker trip test in 2012 was not a causal factor of the DC Event. It appears that the loose connection at issue may have occurred sometime after July 2014, but before the DC Event (i.e., after the last 2012 testing cycle and before the then-scheduled 2016 testing cycle). Pepco identified two root causes for its failure to perform testing and its failure to adequately demonstrate that it performed maintenance and testing of the DC control circuitry in accordance with Pepco’s Testing Program. First, Pepco's Testing Program requires circuit breaker trip testing of the DC control circuitry to occur at the same time as relay testing. Field personnel did not always conduct circuit breaker trip testing due to concerns that equipment may be damaged by repetitive breaker tripping and/or system limitations preventing circuit breaker trip testing from being completed at the same time as the relay testing. Second, documentation used by Pepco’s technicians to collect evidence of maintenance and testing (i.e., Aspen Data Sheets) does not sufficiently capture all maintenance and testing activities conducted pursuant to Pepco’s Testing Program. The root causes involves ineffective workforce management practices and training because Pepco and its employees were not properly following its established PRC-005-1b R2 maintenance and testing procedures. If followed and documented correctly, the established maintenance and testing procedures would have been adequate to ensure compliance. Pepco field personnel did not follow Pepco’s procedures when they failed to coordinate and complete breaker trip testing with the line relay test in 2012. The test sheets Pepco used to perform and record its maintenance and testing were confusing and inadequate. | PRC-005-1b | R2; R2.1; R2.2 | High | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Failure to perform the prescribed PRC-005 maintenance and testing can result in degraded performance or equipment failure and possible negative impacts to the BES such as load loss. This risk is magnified by this violation’s long duration because the breaker at issue had not been tested since commissioning in November 2010. The fact that Pepco has had past violations of PRC-005-1b R2 involving relays that were not tested within the testing interval outlined in Pepco’s Testing Program, that ReliabilityFirst noted three separate areas of concern with Pepco’s PRC-005 program in ReliabilityFirst’s 2014 Compliance Audit of Pepco, that Pepco did not adequately address ReliabilityFirst’s concerns with Pepco’s documentation of its PRC-005 program, and that Pepco only found the current violation as a result of ReliabilityFirst’s request for test records following the DC Event evidences ReliabilityFirst's concern that Pepco needs to improve its PRC-005 program and its detective controls. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The harm realized during the DC Event cannot be reasonably connected to Pepco’s missed breaker trip test in 2012 because (i) the breaker in question successfully tripped in 2014 as the result of a system fault, demonstrating that, during the trip, the breaker was properly functioning after the missed trip test in 2012 and before the DC Event; and (ii) Pepco would not have checked for a loose connection if it had performed the 2012 test. PRC-005-1b R2 does not require registered entities to check for loose connections. Pepco also provided evidence that it performed continuous maintenance and testing activities on relays across its system including relay settings verification, operational status test, PT/CT inputs, and current pick-up and time sync. As part of an extent of condition review conducted after the DC event, Pepco has not identified any additional loose trip coil connections or other wire continuity problems in any of its breakers or relays. No harm is known to have occurred. | 3/14/2012 (when the Standard became mandatory and enforceable on Pepco) | 3/23/2016 (Mitigation Plan completion) | 45000 | Self-Report | To mitigate this violation, Pepco: 1) performed a comprehensive review of existing BES Microprocessor Relay maintenance and testing activities to determine the need for any modifications to corresponding test templates to accurately and completely reflect required activities; 2) modified the Microprocessor Relay test templates as necessary; 3) developed a periodic monitoring control mechanism to be performed by its corporate compliance team to review testing variances, in order to ensure resolution; 4) performed a comprehensive review of existing BES Electromechanical Relay maintenance and testing activities to determine the need for any modifications to corresponding test templates to accurately and completely reflect required activities; 5) modified the Electromechanical Relay test templates as necessary; 6) reviewed and updated Pepco’s Protection System and Maintenance Program to ensure alignment with requisite activities captured in the modified Microprocessor and Electromechanical Relay test templates. The new templates are better organized, easier to follow, and will better ensure that Pepco field personnel performing maintenance and testing will document that maintenance and testing appropriately; 7) modified and improved the evidence templates that it uses to complete and track its BES Microprocessor Relay maintenance and testing activities. The new templates are better organized, easier to follow, and will better ensure that Pepco field personnel performing maintenance and testing will document that maintenance and testing appropriately. Pepco began using the modified evidence templates on March 24, 2016; and 8) scheduled and provided training on all modifications made to Pepco’s Protection System and Maintenance Program and applicable test templates. ReliabilityFirst verified Pepco's completion of these Mitigating Activities. Pepco also undertook additional mitigating activities outside of its Mitigation Plan. As a result of the following mitigating activities, Pepco has taken and is taking all reasonable measures to ensure that there are no other loose connections on Pepco’s system. Since the DC Event, Pepco has replaced and upgraded the microprocessor relays on the 23071/23072 line terminals at Morgantown and Chalk Point. All associated breakers with the new relays were tested and tripped as part of the relay replacement effort and performed as designed. As of March 17, 2017, Pepco has completed testing on 573 BES relay schemes using the modified and improved PRC-005 program documents and evidence templates that were placed into effect on March 24, 2016. This constitutes more than 38% of Pepco’s approximately 1477 NERC BES relay schemes. Pepco will complete maintenance and testing on its remaining BES relay schemes over the next three years, completing approximately 25% of its relays each year using its modified Protection System Maintenance and Testing Program and modified Aspen Data Sheets. For the 38% of relay schemes tested so far using the improved PRC-005 program documents and evidence templates, Pepco’s testing has not identified any additional loose trip coils to date. Pepco expedited the LFZR relay replacement project to replace LFZR relays with higher performing relays. (Pursuant to a Corrective Action Plan (CAP) on file with ReliabilityFirst (Misoperation ID 2012082601), Pepco was already in the process of replacing all of the LFZR relays on its system at the time of the event. The initial LFZR misoperation resulting in the CAP was timely reported in accordance with PRC-004. There were no known defects with LFZR relays when Pepco initially installed them on its system.) This project was successfully completed by the end of 2015 (originally scheduled for completion in 2017), resulting in the replacement of all 26 BES LFZR relays on the Pepco system. In order to complete the project within the accelerated time frame, Pepco spent $2,577,872.25 in labor and materials. Further, all breakers associated with the impacted lines were tested and performed as designed during the new relay commissioning process. (Although the misoperation of the LFZR relays were not a causal factor of the DC Event because an independent and redundant set of relays operated properly at the same time, ReliabilityFirst remains concerned that the misoperation occurred and notes that such misoperations can be contributory factors to events.) After the DC Event, Pepco engaged an independent consultant to review the work performed and to evaluate the continuity of the DC trip paths for the Line Relay 1 (LR1) and Line Relay 2 (LR2) schemes at issue in the DC Event. The consultant found that the loose connection on the LR1 scheme was corrected, and no issues were identified on the LR2 scheme. The consultant further assisted in the review of all Pepco BES line protection schemes to identify all locations where both the tripping and breaker failure initiate signals are developed in the same auxiliary relay. The cost of this work totaled $14,247.50. Pepco hired an additional resource to provide greater support and further focus to its PRC-005 program oversight. This individual will be responsible for working with the Pepco electric maintenance department to ensure the mitigated PRC-005 procedures are properly implemented and adequate records are retained to reduce the likelihood of future missed testing. Pepco’s estimated annual cost for this additional resource is $164,000. Pepco will implement a Failure Modes Effects Analysis (FMEA) to review its PRC-005 processes, procedures and practices, in order to improve its Protection System and Maintenance Program and to minimize BES risk. The FMEA will identify potential gaps in the PRC-005 program and Pepco will complete the FMEA within four months of executing the Agreement. The FMEA is an internal control measure that improves processes through the identification and mitigation of potential causes of error and variability in processes. Pepco will utilize the FMEA to identify additional controls where appropriate to enhance its PRC-005 program within four months after executing this Agreement. Pepco’s estimated cost to conduct this additional risk analysis is $80,000. Within six months after executing this Agreement, Pepco will submit a final report to RF discussing the FMEA project and the status of implementing the mitigation measures. Pepco’s parent company, Pepco Holdings, LLC, recently closed a merger with Exelon. Exelon Companies include three Transmission Owners: BGE, ComEd, and PECO. In addition to the work performed in its mitigation plan, Pepco commits to working with these newly affiliated companies to perform a review to identify potential best practices that may be adopted by Pepco to improve its PRC-005 program. This review will be completed by September 1, 2017. | 2016-03-23 | 2016-06-16 | Neither Admits nor Denies | ReliabilityFirst considered Pepco’s cooperation during the Settlement Agreement process and awarded significant mitigating credit. Pepco has been cooperative throughout the entire enforcement process. Following the DC Outage, Pepco met with ReliabilityFirst on a regular basis to discuss the violation, the root cause of the violation, and the mitigation. Throughout the enforcement process, Pepco voluntarily provided ReliabilityFirst with an abundance of information regarding the violation in a manner that was transparent, detailed, and timely. Pepco’s cooperation was exemplary. ReliabilityFirst awards mitigating credit for certain extenuating circumstances surrounding this violation. Throughout the Event Analysis process led by NERC and ReliabilityFirst, Pepco was extremely cooperative and participated fully and without reservation. Pepco actively participated in the event analysis process and all assessment related activities by promptly responding to questions from NERC and ReliabilityFirst and providing responsive, transparent, and detailed answers and documentation to questions that it received. Pepco’s conduct with all parties involved in the event analysis process warrants mitigating credit. ReliabilityFirst considered Pepco's internal compliance program and considered it a neutral factor in the penalty determination. Pepco did not receive mitigating credit for self-reporting because the Self-Report was submitted in response to a request for information during ReliabilityFirst's compliance assessment process with Pepco following the DC Event. As a result of Pepco’s difficulties in identifying this violation, the moderate risk posed by this violation, and this violation’s connection with the DC Outage, ReliabilityFirst shall impose the following nonmonetary sanctions on Pepco. ReliabilityFirst will suspend Pepco’s privilege to self-log noncompliances with PRC-005-1b R2, PRC-005-2 R2, and PRC-005-6 R2 until ReliabilityFirst is satisfied that Pepco has demonstrated that it should once again be allowed to self-log noncompliances for these standards. ReliabilityFirst will also perform a Spot Check of Pepco’s compliance with PRC-005-2 and PRC-005-6 in 2017. The purpose of the Spot Check is to ensure that Pepco is following its revised program and templates in performing PRC-005 maintenance and testing. The Spot Check will specifically focus on Pepco’s documentation of its PRC-005 maintenance and testing activities. ReliabilityFirst will determine the scope of the Spot Check and the date in 2017 when the Spot Check will occur and inform Pepco accordingly. After completion of this Spot Check, ReliabilityFirst will make a determination on whether Pepco is allowed to self-log non-compliances for the above standards. ReliabilityFirst considered Pepco's PRC-005 R2 compliance history an aggravating factor in determining the penalty and disposition track. Pepco's relevant prior noncompliance with PRC-005 R2 includes: RFC2013013073. A Find, Fix and Track covering a violation of PRC-005-1b R2 was filed with FERC on February 27, 2014. The prior noncompliance is not distinguishable from the current violation. In the prior noncompliance, Pepco identified relays that were not tested within the testing interval outlined in Pepco’s Testing Program. Pepco’s Testing Program required that it trip test relays every four years with a 10% grace period. Based on the requirements of its Testing Program and the last documented test, Pepco was scheduled to trip test two sets of breaker failure relays (a total of four relays) no later than January 20, 2013 (including the 10% grace period), but failed to complete this testing. Pepco completed the overdue tests on September 23, 2013, more than nine months late. Like the prior PRC-005-1b R2 noncompliance, the current violation involves Pepco not following its Testing Program and missing its 2012 breaker failure relay trip test. Therefore, ReliabilityFirst considered Pepco’s violation history and will treat its prior noncompliance as an aggravating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Northeast Texas Electric Cooperative, Inc. (NTEC) | NCR01124 | SPP2015015225 | Settlement Agreement | During a Compliance Audit conducted from September 9, 2015 through September 10, 2015, SPP RE determined that NTEC, as a Distribution Provider, was in violation of PRC-008-0 R2 because NTEC failed to test its underfrequency relays in accordance with its underfrequency load shed testing and maintenance program (UFLS Program). NTEC was unable to provide SPP RE with the test data for eight underfrequency relays. Upon further investigation of the evidence provided by NTEC, SPP RE subsequently determined that in addition to the noncompliance cited during the audit, the evidence provided by NTEC was insufficient to substantiate testing of another underfrequency relay. Collectively, NTEC was unable to substantiate the maintenance/testing of nine of the 19 UFLS relays sampled by SPP RE. Additionally, SPP RE determined that NTEC failed to perform other UFLS relay mechanical maintenance and self-tests on all its UFLS relays in accordance with its UFLS Program. The root cause of NTEC’s violation of PRC-008-0 R2 was a lack of training for the NTEC member cooperatives on the requirements for maintaining and testing UFLS equipment and a lack of management controls to ensure maintenance activities were performed as expected and within established intervals. | PRC-008-0 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to properly maintain underfrequency relays increases the probability that these relays will not respond appropriately to a system underfrequency condition. Although NTEC was not maintaining its underfrequency relays in accordance with its UFLS Program, NTEC uses microprocessor underfrequency relays exclusively, which are inherently reliable. Furthermore, the NTEC total UFLS requirement is only 162 MW, less than two percent of the regional UFLS inventory. No actual harm is known to have occurred. | 5/1/2009 (when the audit period began) | 9/15/2016 (when NTEC completed maintenance and testing of its UFLS relays) | $53,900 (for SPP2015015225 and SPP2015015226) | Compliance Audit | To mitigate this violation and prevent reoccurrence NTEC: 1) performed a review of UFLS test records to verify the completion of all required maintenance activities; 2) completed testing of UFLS relays; 3) revised its PRC-005 PSMP to include the UFLS maintenance program to allow for better management; and 4) implemented annual training for its member cooperatives and contractors on the UFLS maintenance program via on-site training and webinars. | 12/01/2016 | 12/21/2016 | Neither Admits nor Denies | SPP RE reviewed NTEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE considered NTEC's and its affiliates' compliance history in determining the penalty. The compliance history for NTEC and its affiliates includes: A Settlement Agreement covering violation of PRC-008-0 R1 (SPP200900077) for East Texas Electric Cooperative, Inc. (ETEC) was filed with the Federal Energy Regulatory Commission (FERC) under NP10-162-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty (NOP). ETEC’s Implementation and Documentation of UFLS Equipment Maintenance Program procedure did not include a schedule for the UFLS relay maintenance and testing. A Settlement Agreement covering violation of PRC-008-0 R1 (SPP200900078) for Tex-La Electric Cooperative of Texas, Inc. (TEXLA) was filed with FERC under NP10-162-000 on November 30, 2010. On December, 2010, FERC issued an order stating it would not engage in further review of the NOP. The TEXLA’s UFLS procedure, Implementation and Documentation of UFLS Equipment Maintenance Program, did not include a list of TEXLA’s UFLS devices and a schedule for the UFLS relay maintenance and testing. It is SPP RE’s determination that the previous violations of PRC-008-0 R1 by ETEC and TEXLA, NTEC’s sister generation and transmission cooperatives, are indicative of an inadequate ICP and a lack of procedural controls to ensure UFLS relays are maintained and tested. Accordingly, SPP RE finds that the prior violations cited above are an aggravating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Northeast Texas Electric Cooperative, Inc. (NTEC) | NCR01124 | SPP2015015226 | Settlement Agreement | During a Compliance Audit conducted from September 9, 2015 through September 10, 2015, SPP RE determined that NTEC, as a Distribution Provider, was in violation of PRC-006-1 R9 because NTEC did not provide for the automatic tripping of load in accordance with the Underfrequency Load Shed (UFLS) Plan established by the Southwest Power Pool Planning Coordinator (SPP PC). During the audit, NTEC provided SPP RE with the UFLS inventory that was submitted to the SPP PC on January 8, 2015 (2014 UFLS Inventory) in compliance with the SPP PC UFLS Plan. SPP RE observed that the total UFLS inventory identified by NTEC was only 24.56% of its total load and did not meet the 10%, 20%, and 30% minimum accumulated load relief required by Steps one, two, and three of the SPP PC UFLS Plan. Upon further investigation, similar discrepancies were identified with the UFLS inventory submitted by NTEC to the SPP PC for 2015. The root cause of NTEC’s violation of PRC-006-1 R9 was failure to inform its member cooperatives of the requirements to maintain a UFLS program and a lack of controls to ensure the member cooperatives followed the UFLS guidelines established in the SPP PC UFLS Plan. | PRC-006-1 | R9 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although NTEC was not complying with the specific load shed requirements of the SPP PC’s UFLS Plan, it had established an UFLS inventory that substantially met the SPP PC’s UFLS Plan requirements. Based upon NTEC’s total load of 659.8 MW in 2014, it was required by the SPP PC UFLS Plan to have a total UFLS inventory of 198 MW with 66 MW of load shed in three steps. The NTEC UFLS 2014 inventory included 162 MW or 82% of the total requirement, and the load dispersion across the SPP PC UFLS Plan Steps was 49.8 MW for Step one, 61.7 MW for Step two, and 50.4 MW for Step three. NTEC’s UFLS obligation is less than two percent of the regional UFLS inventory. No actual harm is known to have occurred. | 10/1/2013 (when PRC-006-1 became mandatory and enforceable) | 2/16/2017 (Mitigation Plan completion) | $53,900 (for SPP2015015225 and SPP2015015226) | Compliance Audit | To mitigate this violation and prevent reoccurrence NTEC: 1) redesigned its UFLS program based upon load data collected from its member cooperatives; 2) installed new UFLS relays or modified existing UFLS relays to comply with the SPP PC UFLS Plan; 3) conducted a Fall and Winter test of the UFLS relays; 4) implemented an agenda item for discussion of the UFLS program at its annual member meeting to increase program awareness; 5) implemented an annual review of member cooperative load data to ensure compliance with the SPP PC UFLS Plan; and 6) implemented an annual UFLS test to be performed before the SPP PC UFLS data request to validate program compliance. | 2/16/2017 | 2017-04-13 | Neither Admits nor Denies | SPP RE reviewed NTEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE determined that there were no previously filed violations of the same or similar reliability standards or requirements against NTEC or its affiliates.
Southwest Power Pool Regional Entity (SPP RE) | East Texas Electric Cooperative Inc. (ETEC) | NCR01227 | SPP2015015221 | Settlement Agreement | During a Compliance Audit conducted September 9–10, 2015, the Audit Team determined that ETEC, as a Generation Owner and Transmission Owner, was in violation of FAC-009-1 R1. As to the Generator Owner function, the facility rating that ETEC provided the Audit Team for the Harrison County Power Project (HCPP) was not consistent with its Facility Rating Methodology (FRM). ETEC’s FRM for its generating facilities states that ETEC “bases its rating methodology on industry standards and original equipment manufacturer ratings.” Additionally, the emergency rating of equipment comprising its generator facilities is the same as the normal rating. The facility rating documentation provided by ETEC for HCPP included amp ratings for the equipment comprising HCPP’s two combustion turbine (CT) generators and one steam turbine (ST) generator. Although the rating document included columns for Normal and Emergency MVA ratings, the only MVA ratings provided were the Normal MVA ratings for the CT and ST generator step-up transformers. The Audit Team found the Normal MVA ratings for the step-up transformers to be inconsistent with ETEC’s FRM because ETEC listed three ratings for each of the transformers. No explanation was provided in the ratings document for the three ratings. It was only after comparing the ratings document with the HCPP one line diagram that the Audit Team was able to confirm the three ratings were associated with the natural and forced cooling available on the generator step-up transformers. Although ETEC’s FRM for transmission facilities clearly states that the normal and emergency rating for power transformers shall be the highest nameplate rating with all cooling equipment operating, the generation FRM makes no such distinction. Upon further examination of the HCPP one line diagram, the Audit Team identified a discrepancy between the MVA ratings of the CT generators (216.4 MVA) and the amp rating for the two CT generators in the rating document (6,325 amps / 197 MVA). It was subsequently determined that the 197 MVA rating for the CT generators was based upon the generator nameplate and not the one line diagram. As to the Transmission Owner function, the Audit Team determined that ETEC had not considered the ratings of facilities owned by its neighbor, the Southwestern Electric Power Company (SWEPCO), in determining the facility rating for the transmission facilities connecting ETEC to the SWEPCO transmission system. For the Latexo – Crockett and Pine Grove – Jacksonville 138 kV transmission lines, the ratings documentation provided by ETEC did not identify the ratings for SWEPCO equipment at the SWEPCO end of the transmission tie lines. Because the ratings for SWEPCO equipment had not been identified, the Audit Team determined that ETEC could not conclusively identify the most limiting element and thus the facility rating for two of its eight 138 kV transmission lines. A subsequent comparison of the ratings established by ETEC for the Latexo – Crockett and Pine Grove – Jacksonville 138 kV transmission lines with the ratings established by SWEPCO for the same transmission lines revealed an 81 MVA disparity for the winter normal ratings of both transmission lines. The root cause of ETEC’s violation of FAC-009-1 R1 was a lack of internal controls to ensure the facility ratings of tie lines with neighboring utilities are consistent and that facility ratings are periodically reviewed and updated following system changes and changes to its FRM. | FAC-009-1 | R1 | Medium | High | ETEC’s violation of FAC-009-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to establish accurate generation and transmission facility ratings increases the potential risk for such facilities to be operated in excess of their operating limits, thereby creating the opportunity for equipment damage and facility outages. Regarding the generator facility rating inconsistencies cited by the Audit Team, the risk is reduced because: (1) the disparity in the CT ratings is for two small CT generators (less than 200 MVA); (2) the maximum rating of the HCPP step-up transformers is the highest rating available with forced cooling; and (3) the step-up transformers are not the most limiting element of the HCPP facility. As to ETEC’s failure to consider the rating of SWEPCO’s facilities in establishing the ratings of two 138 kV transmission tie lines, although the actual disparity existed only in the winter normal ratings and the transmission lines were at the lower 138 kV voltage level, the ratings established by ETEC were 81 MVA (28.3%) higher than the rating of the facilities at the SWEPCO end of the transmission tie lines. No harm is known to have occurred. | 5/1/2009 (when the audit period began) | 8/19/2016 (Mitigation Plan completion) | $47,600 (for SPP2015015221 SPP2015015222 SPP2015015223 and SPP2015015224) | Compliance Audit | To mitigate this violation, ETEC: 1) revised the Facility Rating spreadsheet to capture the maximum Generator step-up transformer (GSU) rating; 2) verified that other generator facilities have the correct rating identified in the spreadsheet; 3) corrected the errors in the one line diagram for HCPP and created a new one line for the facility; 4) reviewed all transmission connections with AEP and verified with AEP that the ratings for the lines connecting to ETEC’s facility have the correct rating; 5) updated the rating spreadsheet to reflect the AEP line ratings.; 6) initiated an annual verification of the facility ratings with all neighboring entities to ensure consistent ratings; and 7) implemented internal controls, requiring the engineer responsible for developing its facility raitings to annually review, verify, and sign the facility ratings report. | 8/19/2016 | 2016-08-19 | Neither Admits nor Denies | SPP RE reviewed ETEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE considered ETEC’s FAC-009-1 R1 compliance history in determining the penalty. ETEC's relevant prior noncompliance with FAC-009-1 R1 includes: NERC Violation ID SERC200700025, SERC200700024, and SERC200700026. The compliance history for ETEC and its affiliates include: A Notice of Confirmed Violation covering violation of FAC-008-1 R1 (SERC200700025) for ETEC was filed with FERC under NP8-17-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ETEC’s FRM did not state that the most limiting equipment rating of the Facility determines the Facility Rating. Additionally, the methodology for Normal and Emergency ratings of facilities was not defined within the FRM; A Notice of Confirmed Violation covering violation of FAC-008-1 R1 (SERC200700024) for Sam Rayburn G & T Electric Cooperative (SRG&T), an affiliate of ETEC, was filed with FERC under NP8-22-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SRG&T’s FRM document did not state that the most limiting equipment rating of the Facility determines the Facility Rating. Additionally, the methodology for Normal and Emergency ratings of facilities was not defined within the FRM; and A Notice of Confirmed Violation covering violation of FAC-008-1 R1 (SERC200700026) for TexLa Electric Cooperative of Texas (TexLa), an affiliate of ETEC, was filed with FERC under NP8-22-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. TexLa’s FRM did not state that the most limiting equipment rating of the Facility determines the Facility Rating. Additionally, the methodology for Normal and Emergency ratings of facilities was not defined within the FRM. SPP RE considered ETEC's compliance history and determined that the violations do not involve recurring conduct and should not serve as a basis for aggravating the penalty.
Southwest Power Pool Regional Entity (SPP RE) | East Texas Electric Cooperative Inc. (ETEC) | NCR01227 | SPP2015015222 | Settlement Agreement | During a Compliance Audit conducted September 9 – 10, 2015, the Audit Team determined that ETEC, as a Transmission Owner and Distribution Provider, was in violation of PRC-008-0 R2 because ETEC failed to test its underfrequency relays in accordance with its underfrequency load shed (UFLS) testing and maintenance program (UFLS Program). Specifically, the test data provided by ETEC for the Slocum substation UFLS relay did not verify proper operation of the relay at the designated frequency. Upon further investigation of the evidence provided by ETEC, SPP RE has determined that in addition to the noncompliance cited by the Audit Team, ETEC failed to maintain additional UFLS relays in accordance with its UFLS Program. Overall, ETEC missed the UFLS testing dates for two relays out of 15 relays. ETEC has revised its UFLS Program procedures multiple times during the May 30, 2009 to September 10, 2015 audit period. ETEC provided no evidence to indicate that mainteance and/or self-tests were being performed on microprocesser and solid state UFLS relays despite a requirement to perform mechanical maintenance and self-tests, either on an annual basis or concurrent with electrical testing on an eight or twelve calendar year interval. Regarding the SLOCUM4 UFLS relay noncompliance identified by the Audit Team, the test data sheet provided by ETEC indicated that the relay was tested on May 8, 2014. However, unlike other test data results provided by ETEC, there was no indication in the test data sheet that the underfrequency function of the relay had been tested. ETEC subsequently provided test data for the SLOCUM4 UFLS relay indicating that the relay was utilized to trip three breakers at different times. All three of the underfrequency trips were tested on August 17, 2010. Additionally, the SLOCUM4 UFLS relay test data sheet indicated that a previous test had been performed on February 29, 2012, however, ETEC did not produce the previous test results to substantiate a test of the relays underfrequency function. Nevertheless, the Summary Report provided by ETEC indicated that the SLOCUM4 UFLS relay had been tested on February 29, 2012. SPP RE noted that the previous test date in the Summary Report for the GARDVAL4 UFLS relay was blank, indicating no previous data was available, however, the most recent test data provided by ETEC indicated that a previous test had been performed on March 27, 2008. SPP RE noted that the UFLS test data provided by ETEC was inconsistent with the UFLS inventory data provided to the SPP RTO Planning Coordinator. ETEC has not maintained its UFLS relays in accordance with the maintenance/testing prescribed in its UFLS Program. The root cause of ETEC’s violation of PRC-008-0 R2 was a lack of training for ETEC member cooperatives on the requirements for maintaining and testing UFLS equipment and a lack of management controls to ensure maintenance activities are performed as expected and within established intervals. | PRC-008-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to maintain and properly arm underfrequency relays increases the potential risk that these relays will not respond appropriately to an underfrequency event. Although ETEC was not maintaining its underfrequency relays in accordance with its UFLS Program, the ETEC system is small (less than 110 MW), with a total UFLS load shed of approximately 33 MW or less than 1% of the regional UFLS load shed inventory. No harm is known to have occurred. | 5/1/2009 (when the audit period began) | 8/12/2016 (when ETEC completed the maintenance and testing of its UFLS relays) | $47,600 (for SPP2015015221 SPP2015015222 SPP2015015223 and SPP2015015224) | Compliance Audit | To mitigate this violation, ETEC: 1) tested its UFLS relays; 2) performed a review of UFLS test records to verify the completion of all required maintenance activities; 3) revised its Protection System Maintenance Program (PSMP) to include the UFLS maintenance program to allow for better management; and 4) initiated annual training for its member cooperatives and contractors on the UFLS maintenance program via on-site training and webinars. | 2016-09-29 | 2016-10-05 | Neither Admits nor Denies | SPP RE reviewed ETEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE considered ETEC’s PRC-008-0 compliance history in determining the penalty. ETEC's relevant prior noncompliance with PRC-008-0 includes: NERC Violation ID SPP200900077 and SPP200900078. The compliance history for ETEC and its affiliates includes: A Settlement Agreement covering violation of PRC-008-0 R1 (SPP200900077) for ETEC was filed with FERC under NP10-162-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ETEC’s Implementation and Documentation of UFLS Equipment Maintenance Program procedure did not include a schedule for the UFLS relay maintenance and testing; and A Settlement Agreement covering violation of PRC-008-0 R1 (SPP200900078) for TexLa Electric Cooperative of Texas (TexLa), an affiliate of ETEC, was filed with FERC under NP10-162-000 on November 30, 2010. On December, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The TexLa’s UFLS procedure, Implementation and Documentation of UFLS Equipment Maintenance Program, did not include a list of TexLa’s UFLS devices and a schedule for the UFLS relay maintenance and testing. SPP RE considered ETEC's compliance history and determined that the violations do not involve recurring conduct and should not serve as a basis for aggravating the penalty.
Southwest Power Pool Regional Entity (SPP RE) | East Texas Electric Cooperative Inc. (ETEC) | NCR01227 | SPP2015015223 | Settlement Agreement | During a Compliance Audit conducted September 9 – 10, 2015, the Audit Team determined that ETEC, as a Transmission Owner and Distribution Provider, was in violation of PRC-006-1 R9 because it did not provide for the automatic tripping of load in accordance with the Underfrequency Load Shed (UFLS) Plan established by the Southwest Power Pool Planning Coordinator (SPP PC). Additionally, the Audit Team determined that the intentional time delay for three of the seven ETEC UFLS relays sampled during the audit was set in excess of the maximum 30 cycle delay allowed by the SPP PC UFLS Plan. During the audit, ETEC provided the Audit Team with the UFLS inventory that was submitted to the SPP PC on January 8, 2015 (2014 UFLS Inventory) in compliance with the SPP UFLS Plan. The Audit Team observed that the total UFLS inventory identified by ETEC was only 28% of its total load and did not meet the 30% minimum accumulated load relief required by the SPP UFLS Plan. Additionally, the Audit Team observed that the Cycle Time identified with load shed by the PINEGRV4 relay(s) exceeded the intentional relay time delay identified in the SPP UFLS Plan. ETEC failed to provide automatic tripping of load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator. The root cause was the failure to inform its member cooperatives of the requirements to maintain a UFLS program and a lack of controls to ensure the member cooperatives were following the UFLS guidelines established in the SPP PC UFLS Plan. | PRC-006-1 | R9 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to comply with the minimum requirements of the regional Planning Coordinator’s UFLS program increases the risk that the regional response to an underfrequency event will be insufficient to halt the collapse of the transmission system following the loss of generation resources. Although ETEC was not complying with the SPP Planning Coordinator’s UFLS Program, the ETEC system is small (less than 110 MW), with a total UFLS load shed of approximately 33 MW or less than 1% of the regional UFLS inventory. No harm is known to have occurred. | 10/1/2013 (when the Standard became mandatory and enforceable) | 8/12/2016 (when ETEC completed testing of its UFLS relays) | $47,600 (for SPP2015015221 SPP2015015222 SPP2015015223 and SPP2015015224) | Compliance Audit | To mitigate this violation, ETEC: 1) updated Member cooperative UFLS data to verify how many changed and new UFLS relays have been put into service according to the new plan; 2) performed a UFLS test to verify the load meets the expected load shed values and meet SPP Criteria; 3) completed the changes to UFLS settings and locations; 4) verified that all the new UFLS relays have been placed in service; 5) initiated annual requests for detailed load information from member cooperatives in order to review and modify its UFLS program as load levels change; 6) established an internal UFLS program test each year, prior to submitting UFLS data ot SPP RE; and 7) added discussion of the UFLS program to the agenda tof the annual member cooperative meeting in order to keep member cooperatives aware of the requirement to maintain the UFLS program. | 12/27/2016 | 2017-01-04 | Neither Admits nor Denies | SPP RE reviewed ETEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE considered ETEC's compliance history and determined that there were no previously filed violations of the same or similar reliability standards or requirements.
Southwest Power Pool Regional Entity (SPP RE) | East Texas Electric Cooperative Inc. (ETEC) | NCR01227 | SPP2015015224 | Settlement Agreement | During a Compliance Audit conducted September 9 – 10, 2015, the Audit Team determined that ETEC, as a Transmission Owner, was in violation of PRC-005-1 R2.1 for failing to maintain its battery chargers in accordance with its Protection System Maintenance Program (PSMP). Upon further investigation of the evidence provided by ETEC, SPP RE has determined that ETEC failed to maintain additional Transmission and Generation Protection System devices in accordance with its PSMP and is in violation of R2.2 for failing to accurately document the date each of its Protection System devices were last tested/maintained. ETEC has revised its PSMP multiple times during the May 30, 2009 – September 10, 2015 audit period. The revisions include: Version 8, effective June 30, 2009 (090630 PSMP); Version 9, effective September 4, 2009 (090904 PSMP); Version 10, effective March 5, 2010 (100205 PSMP); Version 11, effective June 15, 2010 (100615 PSMP); Version 12, effective March 16, 2011 (110316 PSMP); and Version 13, effective August 1, 2011 (110801 PSMP). Except as noted herein, these versions of ETEC’s PSMP are substantially similar and hereinafter are collectively referred to as (09-11 PSMP). On February 21, 2014, ETEC revised its PSMP to address the implementation of PRC-005-2. Therein, ETEC elected to continue a time-based approach to Protection System maintenance/testing; revised protection system device maintenance/testing intervals to be consistent with the maximum maintenance interval identified in the PRC-005-2 tables; and modified its maintenance activities to meet the minimum requirements established in the PRC-005-2 tables. ETEC bifurcated this PSMP, creating separate procedures for Transmission and Generation protection system devices. Hereinafter, the Transmission and Generation PSMPs are collectively referred to as the 140221 PSMP. ETEC has not maintained its transmission substation battery banks, transmission substation instrument transformers, transmission substation direct current circuitry, and generation protective relays in accordance with its 09-11 PSMP and 140221 PSMP. ETEC has also failed to maintain/test generation battery chargers, generation batteries, and its direct current circuitry in accordance with its 110801 PSMP and 140221 PSMP. The root cause of ETEC’s violation of PRC-005-1 was failure to provide guidance to its technicians, supervisors, and contractors on the requirements to maintain protection system equipment and a lack of controls and reporting to ensure the testing activities and timelines identified in the PSMP are being followed. | PRC-005-1 | R2, R2.1, R2.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failure to maintain and test protection system devices increases the potential risk of relay misoperations. A misoperation, i.e., a false operation of a protection system, or a failure of the protection system to operate as designed, can result in equipment damage, personnel hazards, and other system disturbances. Although ETEC was not maintaining its protection system devices in accordance with its PSMP, SPP RE determined that failure of any of its protection system devices would have minimal impact on the BPS. ETEC is a small electric cooperative, serving less than 100 MW of load. Its transmission system consists of four Bulk Electric System substations which operate at 138 kV. It is the Generator Owner for one combined cycle power plant consisting of two 170 MW combustion turbines and one 230 MW steam turbine. ETEC makes extensive use of microprocessor relays in its protection systems, which are inherently reliable and are monitored continuously by operations personnel. No actual harm is known to have occurred. | 5/1/2009 (when the audit period began) | 12/5/2016 (when ETEC completed testing its protection system devices) | $47,600 (for SPP2015015221 SPP2015015222 SPP2015015223 and SPP2015015224) | Compliance Audit | To mitigate this violation, ETEC: 1) reviewed the testing records for all transmission and generation facility PRC-005 elements to identify those that have not been tested according to the PSMP; 2) tested all elements identified in the review; 3) updated testing spreadsheets to further track testing performance; 4) created new testing schedules to merge the already tested with the newly tested elements to meet the timing intervals in the new PSMP; 5) updated its PSMP to provide additional guidance for the testing technicians and clearly identified the testing intervals. The revised PSMP combines the generation, transmission, and UFLS maintenance and tesitng programs under one procedure that is compliant with PRC-005-6; 6) added independent annual PRC-005 spot check and increased reporting requirements to verify that the testing meets the PSMP requirements for both testing activities; and 7) added the PRC-005 requirements to the agenda for the annual member cooperatives meeting to keep the topic as a priority in daily operations. | 2016-12-21 | 2017-01-03 | Neither Admits nor Denies | SPP RE reviewed ETEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SPP RE considered ETEC’s PRC-005 R1 compliance history in determining the penalty. ETEC's relevant prior noncompliance with PRC-005 R1 includes: NERC Violation ID SERC200700017, SERC200700018, SERC200700020, SERC200900267, SERC200900268, SERC2011007373, SPP200900067, SPP200900068, SPP200900069, and SPP200900070. The compliance history for ETEC and its affiliates includes: A Notice of Confirmed Violation covering violation of PRC-005-1 R1 (SERC200700017) for ETEC was filed with FERC under NP8-17-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ETEC’s PSMP program did not include maintenance cycles or their basis for all of the devices identified in the PRC-005 standard; A Notice of Confirmed Violation covering violation of PRC-005-1 R1 (SERC200700018) for Sam Rayburn G & T Electric Cooperative (SRGT), an affiliate of ETEC, was filed with FERC under NP8-22-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SRGT’s PSMP program did not include maintenance cycles or their basis for all of the devices identified in the PRC-005 standard; A Notice of Confirmed Violation covering violation of PRC-005-1 R1 (SERC200700020) for TexLa Electric Cooperative of Texas (TexLa), an affiliate of ETEC, was filed with FERC under NP8-22-000 on June 4, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. TexLa’s PSMP program did not include maintenance cycles or their basis for all of the devices identified in the PRC-005 standard; A Settlement Agreement covering violations of PRC-005-1 R1 (SERC200900267) and PRC-005-1 R2 (SERC200900268) for SRGT, an affiliate of ETEC, was filed with FERC under NP11-103-000 on January 31, 2011. On March 2, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SRG&T did not have a maintenance and testing procedure that included the interval and basis, or a summary of maintenance and testing procedures for its circuit breaker bushing current transformers, associated communication systems and capacitive coupled voltage transformers. Additionally, SRGT did not have test records and test intervals for its current transformers, potential transformers, station batteries, protective relays, and associated communication equipment; The North American Electric Reliability Corporation filed a Spreadsheet NOP covering violation of PRC-005-1 R1 (SERC2011007373) for ETEC with FERC under NP13-27-000 on February 28, 2013. On March 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ETEC had self-reported that the PSMP for two of its generation facilities did not include a summary of maintenance and testing procedures for station batteries. Additionally, its generation facility PSMP did not include the maintenance and testing intervals or the basis for such intervals for any of the protection system devices; A Settlement Agreement covering violations of PRC-005-1 R1 (SPP200900067) and PRC-005-1 R2 (SPP200900068) for ETEC was filed with FERC under NP10-162-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ETEC was found in violation of PRC-005-1 R1 because ETEC’s PSMP procedures did not include all of its Protection Systems instrument transformers and associated communication systems. Additionally, ETEC did not have evidence that all of its instrument transformers and associated communications systems had been tested and maintained within the intervals identified in its PSMP; and A Settlement Agreement covering violations of PRC-005-1 R1 (SPP200900069) and PRC-005-1 R2 (SPP200900070) for TexLa, an affiliate of ETEC, was filed with FERC under NP10-162-000 on November 30, 2010. On December 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. TexLa’s PSMP procedures did not include routine maintenance and testing of its Protection System instrument transformers. Additionally, TexLa did not have evidence that all of its Protection System devices were maintained within the intervals identified in its PSMP. It is SPP RE’s determination that the previous violations of PRC-005 R1 and R2 by ETEC and its affiliates are indicative of a lack of procedural controls to ensure protection system devices are maintained and tested. Accordingly, SPP RE finds that the prior violations cited above are an aggravating factor in the penalty determination.