## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Tampa Electric Company (TEC) | NCR00074 | FRCC2016015955 | Settlement Agreement | On July 29, 2016, TEC submitted a Self-Report stating that, as a Transmission Owner, it had an issue of FAC-009-1 R1. TEC failed to establish Facility Ratings that were consistent with the associated Facility Ratings Methodology. The Facility Ratings of three 230 kV transmission lines were not consistent with TEC’s associated Facility Rating Methodology. Specifically, the Facility Rating for each of the three circuits contained incorrect Elements, which led to overstated Element Ratings, and consequently, overstated Facility Ratings. During an extent of condition review, an additional five transmission lines were found to have overstated Facility Ratings. The incorrect Facility Ratings affected 6% (8 of 138) of TEC’s Facilities. The Facility Rating for circuit #1 was based on the incorrect rating of a line switch Element that resulted in a Normal Facility Rating that was overstated by 13.4% for the 651-day period between April 30, 2014 and February 10, 2016. However, during this period the actual load on the Facility did not exceed 84.6% of the corrected Normal Facility Rating. The Facility Ratings for circuits #2 and #3 were based on an incorrect wire type for the down leads indicated on the Substation One-Line diagram and in the Facility’s Rating database. Consequently, the Normal Facility Rating for both lines was overstated by 2.1% and the Short-Term Emergency (STE) Rating was overstated by 3.7% for the 3232-day period between enforcement date of FAC-009-1 R1., June 18, 2007 and April 22, 2016. During this time period the maximum line flows did not exceed the Normal or STE Facility Ratings. During the extent of condition review, three additional lines were found with the incorrect down leads and Facility Ratings overstated by 2.1%. The maximum line flows during the period of noncompliance did not exceed the corrected Normal or STE Facility Ratings. During the extent of condition review, two additional types of incorrect ratings were identified on other transmission lines: • A 230 kV line from the high side bushings of a Generator step-up transformer (GSU) to the switchyard had the Facility Rating overrated by 23%. The Facility Rating for the GSU was lower than the corrected rating for this line. The new Facility Ratings were verified on February 15, 2017, and it was determined the maximum line flows did not exceed the corrected Normal or STE Facility Ratings during the period of noncompliance. • A 138 kV line's Facility Rating was overstated by 7%. The line was connected to a 138/69 kV transformer, which is the only load on the line. The Facility Rating for the transformer was lower than the corrected rating for this line. The new Facility Ratings were verified on February 27, 2017, and it was determined the maximum line flows did not exceed the corrected Normal or STE Facility Ratings during the period of noncompliance. The root cause for this violation was incomplete procedures that did not require field verifications of actual equipment, nor validations to ensure drawings reflected that equipment before establishing Facility Ratings. This issue started on June 18, 2007, the first day of mandatory compliance and ended on February 27, 2017, when the entity developed Facility Ratings that were consistent with their methodology. | FAC-009-1 | R1. | Medium | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk of not having adequate procedures and incomplete field verification of components could lead to incorrect Facility Ratings; which are used by the Planning Authority and Reliability Coordinator to plan and monitor the system. This could lead to inaccurate planning models and studies for the reliability of the FRCC Region. The switch rating error on circuit #1 resulted in a Normal Facility Rating that exceeded the capacity of the switch by 13.4%. An overload of 13.4% might have reduced the life of the switch, but would not have faulted the Facility. Additionally, the switch is only used for isolation and not for current interruption. The conductor rating error on circuits #2 and #3 resulted in a Normal Facility Rating that exceeded the capacity of the down lead conductors by 2.1%, and a STE Rating that exceeded the capacity by 3.8%. These small differences would not affect the useful life or the reliability of the conductors in this application. For the lines connected to the GSU and 138/69 kV transformer the adjacent facilities had lower Facility Ratings than the two lines, thus preventing the lines from exceeding their Facility Ratings. For all lines with incorrect Facility Ratings, TEC validated, since 2007, none of the lines had exceeded the corrected Normal and STE Facility Ratings that were determined during the mitigation. In addition, TEC's transmission system is designed such that no single n-1 event (e.g. single line with an incorrect rating being overloaded) could cause a significant reliability concern. The incorrect Facility Ratings affected 6% (8 of 138) of TEC’s Facilities. No harm is known to have occurred. | 2007-06-18 | 2017-02-27 | 0 | Self-Report | To mitigate this violation, TEC: 1) corrected the Facility Rating for circuit #1 and the RC was notified; 2) replaced the AAC termination conductors with ACSS on circuits #2 and #3 and updated the substation one-line drawings; also the three additional lines that were overrated by 2.1% had the down leads replaced and the ratings corrected; 3) determined a methodology to verify in the field that switch ratings match the Element Rating utilized in the Facility Rating for previously re-rated switches; 4) conducted a field inspection to confirm the switch rating and conductor elements match the Element Rating utilized in the Facility Rating database for 50% of previously re-rated switches, “strain bus” conductors, jumpers, down leads, bus jumpers, and “heavy duty bus” in Bulk Electric System (BES) substations; 5) conducted a field inspection to confirm the switch rating and conductor elements match the Element Rating utilized in the Facility Rating database for 100% of previously re-rated switches, “strain bus” conductors, jumpers, down leads, bus jumpers, and “heavy duty bus” in BES substations; and 6) completed all required engineering analyses of field audit results. Notified FRCC of additional occurrences. To prevent recurrence, TEC: 1) revised the "Tampa Electric Material Specifications (TEMS) for Gang Operated Air Break Switches for Substation Use" to request unique identifiers (i.e. serial numbers) on switch nameplates from the manufacturers going forward; 2) added a procedure to the "Substation Engineering Technical Manual (SETM)" for conducting re-rates of Facility Elements that includes field visits to verify the installed rating type; 3) revised the as-built Q/A procedure in the SETM to ensure as-built drawings match the files and drawings that the facility ratings are based on before equipment is energized; and 4) conducted a training session with applicable Substation Engineering and Operations personnel to review the revisions/additions to the "TEMS for Gang Operated Air Break Switches for Substation Use" and the "SETM." | 2017-03-31 | 2017-05-12 | Neither Admits nor Denies | On September 3, 2015, FRCC and TEC leadership met to discuss concerns regarding TEC's root cause analysis and how it contributed to trends and repeats. Since the meeting, FRCC has seen a significant culture of compliance change whereby TEC has conducted comprehensive root cause analysis when issues have arisen. Additionally, when there have been issues, an in-depth extent of condition review has been conducted to provide reasonable assurance the reliability and security of the BES is maintained. In this instance, TEC discovered and reported issues found during the extent of condition review that FRCC believes would have been difficult to discover through normal monitoring activities. Furthermore, TEC has demonstrated a commitment to developing and enhancing internal controls to improve their operations. Throughout the process, TEC cooperated fully and worked collaboratively with FRCC. FRCC reviewed TEC's Internal Compliance Program (ICP) and considered it to be a a mitigating factor in the penalty determination. In 2016, the FRCC Risk Assessment and Mitigation team reviewed TEC's ICP and found it to be very strong. TEC Self-Reported this issue and FRCC believes the quality of the ICP allowed for this finding. This is a demonstration of TEC's stronger culture of compliance and their commitment to continual improvement. Based on these activities, and to encourage continued self-monitoring, FRCC has chosen a zero-dollar penalty for this issue. FRCC considered TEC's compliance history in determining the penalty. TEC's relevant prior noncompliance with FAC-009 R1 includes: FRCC2011008741 and FRCC2015015178. FRCC2011008741: In this prior instance, mitigating activities were restricted to identifying weak link inventory, and as a result would not have identified the incorrectly rated items discovered in this Self-Report. Although this prior issue was related to Facility Ratings, FRCC determined it should not be an aggravating factor in the penalty determination. The facts and circumstances varied greatly and the mitigating activities were not designed to discover the items now reported. FRCC2015015178: In this prior instance, mitigating activities included field inspections of all TEC BES Substations to ensure that all substation elements of existing Facilities had been included in the Facilities Ratings Database and implement any changes to Facility Ratings. Neither a cross-comparison of the nameplates for re-rated switches, nor a verification of conductor types were conducted as part of the field inspections. The Elements that did not have a nameplate, specifically any conductor or bus, were only visually reviewed. This activity did not catch the items now being reported in this Self-Report. While this instance is considered a repeat violation, it was not considered an aggravating factor because the facts and circumstances varied and the mitigating activities were not designed to discover the items now reported. In addition, the work that TEC has done to improve their compliance program, including the improvements and commitment to root cause analysis, should be recognized as the kind of behavior we would like to see continued.