## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Minnkota Power Cooperative, Inc. (MPC) | NCR01013 | MRO2016016401 | Settlement Agreement | On June 2, 2016, MPC submitted a Self-Report stating that, as a Transmission Owner, it was in violation of FAC-009-1 R1. MPC had Facility Ratings that were not consistent with MPC's Facility Rating methodology. During a 2015 annual review, MPC reviewed five Bulk Electric System (BES) Facilities and revealed errors affecting equipment and BES Facility Ratings at three of the Facilities. Because the error seemed to be more than just an isolated occurrence, MPC decided to initiate a comprehensive review of all ratings to determine the depth of the error as well as ensure that other Facilities did not experience errors similar in nature. During the review, MPC found, aside from the current transformer (CT) emergency rating error for summer and winter seasons, a number of other mistakes were made as well. Specifically, MPC had 77 Facilities that contained 2,753 pieces of rated equipment; 47 of MPC's 77 Facilities contained at least one equipment rating errors (11 of 77 overall Facility Ratings were affected by the equipment rating errors). In 11 instances, these errors resulted in a change to the overall Facility Rating. Seven of these 11 Facilities had a change that represented a decrease in the Facility's overall rating. Five of these seven were Transmission Lines that operated above 200 kV. MRO reviewed the historical data for the five Transmission Lines. One of these five Transmission Lines is a radial line that had a maximum loading of 88% of the corrected rating. For each of the remaining four Transmission Lines, MRO determined that the maximum loading was less than 50% of the corrected rating. MPC had a prior FAC-009-1 R1 violation (MRO2012010744) that was completed on May 27, 2014. However, many of the errors detected in the 2016 review existed prior to the implementation of the previous Mitigation Plan. As part of the Mitigation Plan for the prior violation, MPC committed to performing a comprehensive assessment of its Facility Ratings. In addition, after the prior violation, MPC implemented an internal control that consisted of an annual review of a sample of its Facility Ratings. MPC detected the current violation in the first execution of this annual review. There are three primary causes to the violation: 1) a significant number of the Facility Ratings methodology errors were the result of not including all applicable equipment into the applicable Facility Rating; 2) MPC determined that it does not correctly apply its Facility Rating methodology to CT ratings and line conductor temperature assumptions, and this was not previously detected because the application of its Facility Rating methodology was not a subject of the prior Mitigation Plan; and 3) the Facility Ratings data repository and associated spreadsheets used during the prior Mitigation Plan did not have any features to mitigate against data entry errors or omissions when entering equipment ratings. | FAC-009-1 | R1 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, the risk was not minimal because seven Facilities had a Facility Rating that was higher than its actual/corrected Facility Rating. Five of these seven were Transmission Lines that operate above 200 kV, and one of those five Transmission Lines had a Facility Rating decrease of 33% after it was corrected. Further, the scope and duration of the noncompliance was significant, as 47 of MPC's 77 Facilities had associated equipment ratings errors, and some of these errors have existed since the enforceability of FAC-009-1 R1. However, the risk of the noncompliance was not serious or substantial, as a review of historical loading data confirmed that of the five Transmission Lines that operated above 200 kV that had a Facility Ratings decrease, the maximum loading of the radial line was 88% of the corrected rating and the maximum loading for each of the remaining four Transmission Lines was less than 50% of the corrected rating. Additionally, none of the six Facilities whose Facility Ratings were decreased are associated with an Interconnection Reliability Operating Limit or Cranking Path. Finally, the issue was identified through a functioning detective control. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable on MPC) | 9/30/2016 (when MPC completed a comprehensive review of all BES Facilities and Facility Ratings) | $29,000 | Self-Report | To mitigate this violation, MPC: 1) performed a comprehensive review of all BES Facilities and Facility Ratings; 2) performed a peer review validation of all the Facility Ratings; 3) revised its Facility Rating Procedure to allow for professional judgment of minor discrepancies; 4) developed an enhanced Facility Ratings spreadsheet; 5) transferred old equipment ratings into the new enhanced Facility Ratings spreadsheet; 6) performed final review of new spreadsheets and loaded the new Facility Ratings spreadsheets into a compliance software tool; 7) committed to continued annual sampling of 10% of its Facility Ratings; 8) shifted responsibility for maintaining Facility Ratings away from a general Compliance Engineer and to the Project Engineer; and 9) is in the process of implementing a corporate objective aimed at improving Project Management and job planning. MPC's NERC Compliance obligations, including FAC-008/009, are embedded in these procedures. | 2/28/2017 | 2017-12-22 | Admits | MRO reviewed MPC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MPC has a strong self-audit program. Additionally, MPC has worked to operationalize compliance in its ICP by designating an operations employee to be the standard owner for ensuring compliance with a NERC Reliability Standard, assigning another employee to assist the standard owner, and also requiring compliance staff and the standard owner work together on all Self-Reports as well as the development and implementation of any mitigating activities. MRO considered the nature and quality of MPC's cooperation to be a mitigating factor in the penalty determination. MRO considered MPC's Self-Report of the violation to be a mitigating factor in the penalty determination. MRO considered MPC’s FAC-009-1 R1 compliance history in determining the penalty. MPC’s relevant prior noncompliance with FAC-009-1 R1 includes: NERC Violation ID MRO2012010744 (FAC-009-1 R1). The prior violation was discovered during in preparation of MPC's 2012 Compliance Audit. As part of its Mitigation Plan, MPC committed, among other actions, to perform a detailed review of all of its Facility Ratings. Additionally, MPC implemented an internal control to self-audit a sample of existing Facility Ratings on an annual basis. However, the prior mitigation did not, nor could have, included a review of equipment ratings that were missing from the Facility Rating Data and associated spreadsheets. When MRO sampled equipment ratings during the first Mitigation Plan, it found no outstanding issues. However, through the course of this second violation, it was discovered that some of MPC’s equipment was not included in the database and therefore not subject to the mitigation verification activities that MRO performed in 2014. Additionally, the prior mitigation did not focus on the application of MPC’s Facility Rating Methodology to CT ratings and line conductor temperature assumptions, and the ratings database used during prior mitigation did not have any features to mitigate data entry errors. MRO considered MPC's compliance history to be an aggravating factor in the penalty determination. While the Mitigation Plan corrected many of its Facility Ratings, and the scope and severity of the Facility Rating errors were reduced, MPC's implementation of the prior Mitigation Plan did not detect and correct a significant number of Facility Ratings as evidenced by the current noncompliance, although some of the current noncompliance was caused by factors not addressed in the prior mitigation plan. Finally, MRO recognizes that MPC did successfully implement an annual Facility Ratings review that detected the current noncompliance during the first annual review, and aggravated the penalty to a lesser degree due to that internal control. Based on the above and beyond activity, MRO applied credit to the penalty. MPC has committed to developing a tool that assists in calculating and managing BES Facility Ratings. The database will enhance reliability by enforcing data quality by validating equipment and facility information entered to ensure the required data is entered and that the data values meet pre-defined conditions, automating monitoring, and enforcing MPC's Facility Ratings, in addition to other reliability benefits. MPC has stated that the database will be fully implemented by year-end 2019. The cost of fully implementing the database is estimated at approximately $131,000.