## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017140 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Generator Owner and Transmission Owner, was in violation of FAC-008-3 R6. LWU failed to establish Facility Ratings that were consistent with the associated Facility Ratings Methodology. LWU did not identify the most limiting Element for one of seven (14 percent) Facilities. When determining the Facility Rating for the Hypoluxo substation to Main substation 138 kV line, the current transformers (CTs) at Hypoluxo substation were not considered when the Facility Ratings were determined. Therefore, LWU did not have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Rating Methodology or documentation for determining its Facility Ratings. LWU owns seven Facilities consisting of 81 components. The audit team reviewed all 81 and found one (.012%) with an incorrect Facility Rating. The root cause for this violation was insufficient documentation of the ratings for individual components. Additionally, the nameplate data in the field was misinterpreted due to age, corrosion, and general condition. | FAC-008-3 | R6. | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to include all Bulk Electric System (BES) components of a Facility when establishing a Facility Rating could have led to inadvertently overloading one BES component (i.e., the CTs) by approximately 200 percent. The incorrect Facility Rating could have led to misoperations, equipment damage, or catastrophic failure of one LWU-owned CT. Importantly, such a failure could impact the local area but would not adversely impact broader BPS reliability. LWU did not exceed the corrected facility ratings during the violation timeframe. LWU’s peak load of 100 MW represents only .0022 percent of the total load within the FRCC Region. The lack of, or inaccuracies in, documenting Facility Ratings appear to be systemic issues that exist within LWU’s Facility Rating Methodology, as previously disclosed under the Full Notice of Penalty in FRCC2014013685 and FRCC200900252. No harm is known to have occurred. | 9/5/2016 (when LWU failed to identify the most limiting Element for one Facility) | 3/2/2017 (when LWU updated all Facility Rating documents) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) completed a system wide inventory of BES equipment and verified that all applicable Facility Ratings documents are in agreement; and 2) updated all applicable Facility Ratings documents. To prevent recurrence, LWU: 1) purchased an asset management software; 2) hired a third-party vendor to assist in development and implementation of a systematic tracking of the NERC standards; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators and third-party representatives to: a. discuss the list of applicable NERC standards and the deadlines for each standard implementation; b. review any potential or current equipment modifications that could potentially impact BES Facility Ratings or System Operating Limit. | 2017-03-17 | 2018-02-26 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. FRCC reviewed LWU's compliance history and determined there was a relevant instance of noncompliance, which was considered to be aggravating. FRCC2014013685 mitigation was validated based on evidence supplied by the entity. The mitigation plan was verified without field inspection. The new violation was discovered during a Spot Check field inspection.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017139 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Generator Owner, was in violation of MOD-025-2 R1.2. LWU did not verify at least 40 percent of its applicable Facilities by July 1, 2016 as required by the MOD-025-2 Implementation Plan. LWU did not submit the required testing information for the Real Power capability of its applicable Facilities to the Transmission Planner within the required 90 days of completing the Real Power capability test of its applicable Facilities (GT2 and S-5) in accordance with MOD-025-2, R1.2 The root cause for this violation was lack of management oversight. The previous management responsible for compliance oversight failed to properly monitor implementation plans related to new standards and did not provide their employees with the proper direction. | MOD-025-2 | R1., R1.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to notify their Transmission Planner within the required timeframe created a risk that could have impacted the Region’s capability model. The model inaccuracies could have impacted the Region’s ability to identify and resolve localized emergencies. The risk is increased as inaccuracies within the Transmission Planner’s and Region’s models could misrepresent the real power resources available during localized capacity emergencies, thus exacerbating the issue. The risk was reduced as testing to determine the units’ real power capability was performed as required per Attachment 1 of the Standard. However, the notification to the Transmission Planner did not occur; and the total generation output of 77 MW represents only .0014 percent of the Region. No harm is known to have occurred because there were no capacity emergency events that occurred during this timeframe. | 9/28/2016 (when LWU did not submit the required testing information to the Transmission Planner within the required 90 days) | 2/13/2017 (when the Transmission Planner was notified) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) submitted required test results to the Transmission Planner. To prevent recurrence, LWU: 1) purchased an asset management software; 2) hired a third-party vendor to assist in development and implementation of a systematic tracking of the NERC standards; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators and third-party representatives to discuss the list of applicable NERC standards and the deadlines for each standard implementation and any approaching deadlines and assure redundancy in personnel. | 2017-03-17 | 2018-02-26 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. Accordingly, FRCC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to a settlement with penalty. FRCC reviewed LWU's compliance history and determined there were no relevant instances of noncompliance.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017106 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Generator Owner, was in violation of MOD-025-2 R2.2. LWU did not verify at least 40 percent of its applicable Facilities by July 1, 2016 as required by the MOD-025-2 Implementation Plan. LWU did not submit the required testing information for the Reactive Power Capability of its applicable Facilities to the Transmission Planner within the required 90 days of completing the Reactive Power capability test of its applicable Facilities (GT2 and S-5) in accordance with MOD-025-2, R2.2. The root cause for this violation was lack of management oversight. The previous management responsible for compliance oversight failed to properly monitor implementation plans related to new standards and did not provide their employees with the proper direction. | MOD-025-2 | R2., R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to notify their Transmission Planner within the required timeframe created a risk that could have impacted the Region’s capability model. The model inaccuracies could have also impacted the Region’s ability to identify and resolve localized emergencies. The risk is increased as inaccuracies within the Transmission Planner’s and Region’s models could misrepresent the reactive resources available during localized capacity/voltage emergencies, thus exacerbating the issue. The risk was reduced as testing to determine the units’ reactive power capability was performed as required per Attachment 1 of the Standard; and the total generation output of 77 MW represents only .0014 percent of the Region. No harm is known to have occurred because no capacity/voltage emergency events that occurred during this timeframe. | 9/28/2016 (when LWU did not submit the required testing information the Transmission Planner within the required 90 days) | 2/13/2017 (when the Transmission Planner was notified) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) submitted required test results to the Transmission Planner; To prevent recurrence, LWU: 1) purchased an asset management software; 2) hired a third-party vendor to assist in development and implementation of a systematic tracking of the NERC standards; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators and third-party representatives to discuss the list of applicable NERC standards and the deadlines for each standard implementation and any approaching deadlines and assure redundancy in personnel. | 2017-03-17 | 2018-02-26 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. Accordingly, FRCC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to a settlement with penalty. FRCC reviewed LWU's compliance history and determined there were no relevant instances of noncompliance.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017142 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Transmission Owner (TO), was in violation of PER-005-2 R2. LWU did not develop and implement a training program for its personnel. The FRCC team expanded the Spot Check scope to include R2 when they were unable to determine if LWU verified, at least once, the capabilities of its personnel, as required by R3. The FRCC team determined that LWU did not use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of the Standard. Without having a training program, LWU did not: 1) create a list of Bulk Electric System (BES) company-specific Real-time reliability related tasks based on a defined and documented methodology (R2.1.) 2) design and develop training materials according to its training program (R2.2.) 3) deliver training to its identified personnel (R2.3.) 4) evaluate its training program (R2.4.) 5) verify, at least once, the capabilities of its personnel (R3.) The root cause for this violation was lack of management oversight. The previous management responsible for compliance oversight failed to properly monitor implementation plans related to new standards and did not provide their employees with the proper direction. | PER-005-2 | R2. | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to implement a training program and provide a list of BES company-specific Real-time reliability tasks created a potential risk that could have allowed untrained personnel to make decisions in situations for which they were not qualified, thus endangering reliability, equipment, and safety. The failure to have a training program may result in the lack of knowledge necessary for the operator to make appropriate real-time decisions The risk was increased due to LWU’s unfamiliarity with tasks related to TO activities, which could have impacted the localized area. The risk was reduced due to LWU’s peak load of 100 MW representing only .0022 percent of the total load within the FRCC Region. Also, LWU utilized NERC-certified operators who received annual training related to their job duties. Over the pendency of the violation there were no incidents indicating a lack of training on the reliability related tasks, therefore, no harm is known to have occurred. | 7/1/2016 (when LWU did not develop and implement a training program for its personnel) | 2/27/2018 (when LWU implemented a training program) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) developed a training document using the Analysis, Design, Development, Implementation, and Evaluation (ADDIE) model (initial and continuous) that: a. developed a list of company-specific Real-time reliability-related tasks, b. identified operations staff that perform those tasks, c. reviewed existing policies, procedures, and training processes to incorporate into the development of the Operator Training Program, and d. identified trainers and defined requirements for certification 2) assured qualified trainers have satisfied trainer requirements; and 3) verified all required operators have completed the PER-005 initial training course; and verified, at least once, the capabilities of its personnel assigned to perform each of the BES company-specific Real-time reliability-related tasks;. To prevent recurrence, LWU: 1) contracted a vendor to assist with tracking of NERC standards and implementation of new and newly revised standards; 2) purchased an asset management software to track requirements; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators, and third-party representatives with the following agenda: a. Discuss the list of applicable NERC standards and the deadlines for each standard implementation; b. Discuss any approaching deadlines and assure redundancy in personnel; and c. Perform any applicable training required to bring personnel up to required credentials. | 2018-02-27 | 2018-03-01 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. FRCC reviewed LWU's compliance history and determined there were no relevant instances of noncompliance.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017143 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Generator Owner, was in violation of PRC-019-2 R1. LWU did not verify coordination of at least 40 percent of its applicable facilities by July 1, 2016 as required by the PRC-019-2 Implementation Plan. LWU did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for LWU's three generating facilities: GT1 (26 MW), GT2 (21 MW) and S-5 (10 MW). Relay settings for the voltage regulator system controls were verified on 2/9/17 for GT2 and 2/23/17 for S-5 and found to be set such that in service limiters were set to operate before the protection system and the protection system devices were set to operate in accordance with PRC-019 requirements. The root cause for this violation was lack of management oversight. The previous management responsible for compliance oversight failed to properly monitor implementation plans related to new standards and did not provide their employees with the proper direction. | PRC-019-2 | R1. | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to coordinate its voltage regulating system controls for its three generating units could have caused their generating units to not isolate properly or deenergize unnecessarily that may result in damage to LWU’s generators. The risk is increased as lack of coordination could have caused inadvertent tripping of other generators on the LWU system. The risk was reduced because the total generation output of 77 MW represents only .0014 percent of the Region. No harm is known to have occurred. | 7/1/2016 (when LWU did not verify coordination of at least 40 percent of its applicable facilities by July 1, 2016) | 3/2/2017 (when LWU verified that all applicable generator systems have correct settings and coordination) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) performed an engineering study to verify that all applicable generators voltage regulating system controls and settings of the applicable Protection System devices are properly coordinated; and 2) verified that all applicable generator systems have correct settings and coordination; To prevent recurrence, LWU: 1) purchased an asset management software; 2) hired a third-party vendor to assist in development and implementation of a systematic tracking of the NERC standards; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators, and third-party representatives to discuss the list of applicable NERC standards and the deadlines for each standard implementation and any approaching deadlines and assure redundancy in personnel. | 2017-03-17 | 2018-02-26 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. Accordingly, FRCC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to a settlement with penalty. FRCC reviewed LWU's compliance history and determined there were no relevant instances of noncompliance.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2017017141 | Settlement Agreement | During a Compliance Spot Check conducted from February 27, 2017 through March 2, 2017, the FRCC determined that LWU, as a Generator Owner, was in violation of PRC-024-2 R1. LWU had not verified 40 percent of its applicable Facilities by July 1, 2016, as required by the PRC-024-2 Implementation Plan. LWU did not verify it had set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024-2 Attachment 1 for LWU's three generating facilities: GT1 (26 MW), GT2 (21 MW) and S-5 (10 MW). The root cause for this violation was lack of management oversight. The previous management responsible for compliance oversight failed to properly monitor implementation plans related to new standards and did not provide their employees with the proper direction. | PRC-024-2 | R1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LWU’s failure to set its generator frequency protective relays to not trip within the “no trip zone” could have caused their generating units to not isolate properly during a frequency event. Since LWU relays were set within the “no trip zone,” their generators would have tripped too soon exacerbating the frequency event. LWU verified that the existing generating units and associated equipment did not have any limitations that would have required settings changes. The risk is increased as lack of proper protective relay settings could cause inadvertently tripping other generators on the LWU system. The risk was reduced due to the total generation output of 77 MW represents only .0014 percent of the Region. No harm is known to have occurred as no frequency events occurred during this time frame. | 7/1/2016 (when LWU did not verify coordination of at least 40 percent of its applicable facilities by July 1, 2016) | 6/21/2017 (when LWU verified that it set its protective relaying within the “no trip zone” of PRC-024 Attachment 1 and submitted reports to the Transmission Planner) | $60,000 ((for FRCC2017017140, FRCC2017017139, FRCC2017017106, FRCC2017017142, FRCC2017017143, and FRCC2017017141) | Spot Check | To mitigate this violation, LWU: 1) set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1 and submitted reports to the Transmission Planner; To prevent recurrence, LWU: 1) purchased an asset management software; 2) hired a third-party vendor to assist in development and implementation of a systematic tracking of the NERC standards; and 3) set up quarterly meetings, attended by engineers, engineering manager, system operators, and third-party representatives to discuss the list of applicable NERC standards and the deadlines for each standard implementation and any approaching deadlines and assure redundancy in personnel. | 2017-06-21 | 2018-02-26 | Admits | The Spot Check performed in 2017 was a result of the Notice of Penalty filed in November 2016 in response to LWU defaulting on the settlement related to three violations from 2014. During the Spot Check, FRCC found that LWU's internal compliance program (ICP) continued to be deficient and was a contributing factor to the additional violations discovered. The deficiencies with the ICP included a lack of effective management oversight of compliance personnel, which contributed to the number of issues found during the Spot Check and the general issues LWU experienced in providing accurate and timely responses to FRCC. As a result, FRCC did not apply mitigating credit for LWU's ICP. Additionally, five of the six violations included in this SNOP began on the same date, due to a lack of awareness, which is indicative of a systemic failure of the program. After the Spot Check, LWU began taking steps to improve their ICP. As detailed in the mitigating activities, LWU retained a third-party consultant with extensive NERC experience to support LWU's overall NERC compliance program. To support the overall compliance enhancement process, LWU is developing and implementing a compliance tracking system for ongoing NERC compliance activities. FRCC and LWU have agreed to several actions to address these concerns. First, FRCC and LWU have agreed that LWU's City Manager will execute this Settlement Agreement. This action will ensure that LWU's executive leadership is fully aware of these issues and is committed to driving continuous improvement in LWU's posture across its organization. Second, FRCC will perform additional monitoring related to PER-005-2 in 2019. Third, LWU will continue to contract for outside compliance support over a multi-year timeframe. This will add additional support to LWU’s compliance program. Accordingly, FRCC disqualified this minimal risk violation for Compliance Exception treatment, and escalated this disposition to a settlement with penalty. FRCC reviewed LWU's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2016016699 | Settlement Agreement | On December 22, 2016, ERCOT submitted a Self-Report stating that, as a Reliability Coordinator (RC), it was in violation of IRO-002-2 R7. Specifically, ERCOT failed to continuously monitor its RC Area for approximately 47 minutes during an issue with its Energy Management System (EMS) on July 7, 2016. This was a category 1.h.i event, loss of monitoring or control at a Control Center such that it significantly affects the entity's ability to make operating decisions for 30 continuous minutes or more, specifically, this was a loss of operator ability to remotely monitor or control Bulk Electric System (BES) elements. In order to monitor its RC Area, ERCOT possesses four EMS servers, with one operating as the primary EMS server and three operating as backups. ERCOT uses two primary tools to monitor its RC Area, including monitoring System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs) for pre- and post-Contingency exceedances. First, ERCOT uses a Real-Time Monitoring Contingency Analysis (RTCA) tool. Second, ERCOT uses a Real-Time Network Analysis (RTNET) tool to perform state estimation functions. In addition to its ongoing RC Area monitoring activities, ERCOT uses data snapshots from the active EMS server to develop system recovery and planning models. On July 7, 2016, an ERCOT system analyst was performing a weekly model verification upload and inadvertently loaded the previous week’s model into the EMS server’s active production environment. As a result, the active EMS server attempted to use this bad data and lost the ability to monitor the RC Area at 11:41:31. The data from the active EMS server replicated to the three standby EMS servers as designed. At 11:43:15, ERCOT personnel attempted to failover to the backup EMS servers, but this failover was unsuccessful because the corrupt data had already replicated on all of ERCOT’s EMS servers. As these EMS troubleshooting activities occurred, ERCOT personnel began implementing its established emergency procedures to address its loss of direct monitoring capability. Specifically, at 12:00:12, ERCOT issued a hotline call to all Transmission Operators (TOPs) to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. At 12:02:42, ERCOT issued a hotline call to Qualified Scheduling Entities (QSEs) regarding its EMS monitoring issues. Finally, at 12:05:25, ERCOT issued a second hotline call to all TOPs to update them regarding its ongoing EMS monitoring issues. As ERCOT personnel implemented its established emergency procedures, they likewise continued troubleshooting activities. Specifically, ERCOT personnel successfully reloaded a previous model save case and restored the EMS system’s production environment. ERCOT personnel then disabled a feature for archiving RTCA results and modified several excessive data mismatches within RTNET. With these steps, both the RTNET and RTCA ran successfully at 12:28:48. As a result, ERCOT regained the ability to continuously monitor its RC Area, ending the noncompliance. The root cause of this violation was that ERCOT lacked adequate controls to prevent the introduction of corrupt data into its EMS production environment. In particular, ERCOT did not technically preclude its personnel from inadvertently loading model cases into the EMS production environment or include cautionary messages or other prompts to prevent such actions. | IRO-002-2 | R7 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system. Specifically, ERCOT’s inability to directly monitor its RC Area potentially increased the risk that it would be unable to identify and respond to a potential contingency in a timely manner. However, a number of factors reduced the risks presented by ERCOT’s monitoring issue in the current circumstances. First, ERCOT possessed emergency procedures for responding to this type of monitoring capability loss, including instructions to issue hotline calls to TOPs to ensure the system was monitored by additional entities for previously identified critical reliability elements. These emergency procedures also include detailed steps for detecting and addressing any exceedances such as identifying the area of concern, viewing one-line displays, and directing generation to adjust output. During the issue in question, ERCOT personnel successfully implemented these emergency procedures to coordinate with RC Area TOPs. Specifically, within 20 minutes of the loss of its monitoring capability, ERCOT issued hotline calls and emergency notices to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances during the issue duration. In addition, ERCOT notified all QSEs regarding its EMS issues and remained in communication with two QSEs for large GOPs in the RC Area to maintain frequency and secure additional generation resources as necessary to address issues. Texas RE also considered ERCOT’s troubleshooting efforts to reduce the duration of the monitoring issue. In particular, these efforts limited the issue duration to 47 minutes, less than the 73 minute average duration for EMS outages across the Electric Reliability Organization (ERO) between October 2013 and April 2017. Finally, ERCOT possesses a number of enhanced system restoration plans and conducts routine drills on their implementation, reducing the likelihood that it would not adequately respond to a contingency if one had occurred during the issue. | 7/7/2016 (when ERCOT lost the ability to monitor the RC Area) | 7/7/2016 (when ERCOT successfully activated its RTNET and RTCA tools, restoring its direct RC Area monitoring capability) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) executed emergency operations procedures during the emergency and directed the TOPs to monitor their own service area and notify ERCOT if they observed any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations; 2) restored its ability to continuously monitor its RC Area; 3) revised the database loading script to remove the capability to load model cases into the active EMS Server; 4) added a banner to the database scripts to clearly label them as “Production Servers”; 5) removed the snapshot creation option from the model load process to prevent accidental loading of the model case to the online production environment; 6) implemented a change to automatically save four days of RTCA solutions in a more accessible location to enable quicker resolution should another EMS outage occur; 7) conducted operator and shift engineer training on loss of EMS, including a review of the event in question; and 8) completed operator and shift engineer training on the new IRO and TOP requirements, which specifically require a real time assessment to be performed every 30 minutes. | 2016-11-14 | 2017-05-25 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. ERCOT was subject to event reporting requirements for a complete loss of Supervisory Control and Data Acquisition (SCADA) EMS and submitted such EOP-004 reports to identify these issues. Accordingly, Texas RE did not award self-reporting credit. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its Real-Time Analysis (RTA) capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2016016700 | Settlement Agreement | On December 22, 2016, ERCOT submitted a Self-Report stating that, as a Reliability Coordinator (RC), it was in violation of IRO-003-2 R1. Specifically, ERCOT failed to monitor all Bulk Electric System (BES) facilities within its RC Area to ensure that, at any time, regardless of prior planned or unplanned events, it was able to determine any potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) violations within its RC Area for approximately 47 minutes on July 7, 2016. This was a category 1.h.i event, loss of monitoring or control at a Control Center such that it significantly affects the entity's ability to make operating decisions for 30 continuous minutes or more, specifically, this was a loss of operator ability to remotely monitor or control BES elements. In order to monitor its RC Area, ERCOT possesses four EMS servers, with one operating as the primary EMS server and three operating as backups. ERCOT uses two primary tools to monitor its RC Area, including monitoring SOLs and IROLs for pre- and post-Contingency exceedances. First, ERCOT uses a Real-Time Monitoring Contingency Analysis (RTCA) tool. Second, ERCOT uses a Real-Time Network Analysis (RTNET) tool to perform state estimation functions. In addition to its ongoing RC Area monitoring activities, ERCOT uses data snapshots from the active EMS server to develop system recovery and planning models. On July 7, 2016, an ERCOT system analyst was performing a weekly model verification upload and inadvertently loaded the previous week’s model into the EMS server’s active production environment. As a result, the active EMS server attempted to use this bad data and lost the ability to monitor the RC Area at 11:41:31. The data from the active EMS server replicated to the three standby EMS servers as designed. At 11:43:15, ERCOT personnel attempted to failover to the backup EMS servers, but this failover was unsuccessful because the corrupt data had already replicated on all of ERCOT’s EMS servers. As these EMS troubleshooting activities occurred, ERCOT personnel began implementing its established emergency procedures to address its loss of direct monitoring capability. Specifically, at 12:00:12, ERCOT issued a hotline call to all Transmission Operators (TOPs) to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. At 12:02:42, ERCOT issued a hotline call to Qualified Scheduling Entities (QSEs) regarding its EMS monitoring issues. Finally, at 12:05:25, ERCOT issued a second hotline call to all TOPs to update them regarding its ongoing EMS monitoring issues. As ERCOT personnel implemented its established emergency procedures, they likewise continued troubleshooting activities. Specifically, ERCOT personnel successfully reloaded a previous model save case and restored the EMS system’s production environment. ERCOT personnel then disabled a feature for archiving RTCA results and modified several excessive data mismatches within RTNET. With these steps, both the RTNET and RTCA ran successfully at 12:28:48. As a result, ERCOT regained the ability to continuously monitor its RC Area, ending the noncompliance. The root cause of this violation was that ERCOT lacked adequate controls to prevent the introduction of corrupt data into its EMS production environment. In particular, ERCOT did not technically preclude its personnel from inadvertently loading model cases into the EMS production environment or include cautionary messages or other prompts to prevent such actions. | IRO-003-2 | R1 | High | High | This violation posed a moderate risk to the reliability of the bulk power system. Specifically, ERCOT’s inability to directly monitor its RC Area potentially increased the risk that it would be unable to identify and respond to a potential contingency in a timely manner. However, a number of factors reduced the risks presented by ERCOT’s monitoring issue in the current circumstances. First, ERCOT possessed emergency procedures for responding to this type of monitoring capability loss, including instructions to issue hotline calls to TOPs to ensure the system was monitored by additional entities for previously identified critical reliability elements. These emergency procedures also include detailed steps for detecting and addressing any exceedances such as identifying the area of concern, viewing one-line displays, and directing generation to adjust output. During the issue in question, ERCOT personnel successfully implemented these emergency procedures to coordinate with RC Area TOPs. Specifically, within 20 minutes of the loss of its monitoring capability, ERCOT issued hotline calls and emergency notices to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances during the issue duration. In addition, ERCOT notified all QSEs regarding its EMS issues and remained in communication with two QSEs for large GOPs in the RC Area to maintain frequency and secure additional generation resources as necessary to address issues. Texas RE also considered ERCOT’s troubleshooting efforts to reduce the duration of the monitoring issue. In particular, these efforts limited the issue duration to 47 minutes, less than the 73 minute average duration for EMS outages across the Electric Reliability Organization (ERO) between October 2013 and April 2017. Finally, ERCOT possesses a number of enhanced system restoration plans and conducts routine drills on their implementation, reducing the likelihood that it would not adequately respond to a contingency if one had occurred during the issue. | 7/7/2016 (when ERCOT lost the ability to monitor the RC Area) | 7/7/2016 (when ERCOT successfully activated its RTNET and RTCA tools, restoring its direct RC Area monitoring capability) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) executed emergency operations procedures during the emergency and directed the TOPs to monitor their own service area and notify ERCOT if they observed any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations; 2) restored its ability to continuously monitor its RC Area; 3) revised the database loading script to remove the capability to load model cases into the active EMS Server; 4) added a banner to the database scripts to clearly label them as “Production Servers”; 5) removed the snapshot creation option from the model load process to prevent accidental loading of the model case to the online production environment; 6) implemented a change to automatically save four days of RTCA solutions in a more accessible location to enable quicker resolution should another EMS outage occur; 7) conducted operator and shift engineer training on loss of EMS, including a review of the event in question; and 8) completed operator and shift engineer training on the new IRO and TOP requirements, which specifically require a real time assessment to be performed every 30 minutes. | 2016-11-14 | 2017-05-25 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. ERCOT was subject to event reporting requirements for a complete loss of Supervisory Control and Data Acquisition (SCADA) EMS and submitted such EOP-004 reports to identify these issues. Accordingly, Texas RE did not award self-reporting credit. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its Real-Time Analysis (RTA) capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2016016701 | Settlement Agreement | On December 22, 2016, ERCOT submitted a Self-Report stating that, as a Reliability Coordinator (RC), it was in violation of IRO-003-2 R2. Specifically, ERCOT failed to know the current status of all critical facilities whose failure, degradation or disconnection could result in a System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) violation, as well as the status of any facilities that may be required to assist area restoration objectives for approximately 47 minutes on July 7, 2016. This was a category 1.h.i event, loss of monitoring or control at a Control Center such that it significantly affects the entity's ability to make operating decisions for 30 continuous minutes or more, specifically, this was a loss of operator ability to remotely monitor or control Bulk Electric System (BES) elements. In order to monitor its RC Area, ERCOT possesses four Energy Management System (EMS) servers, with one operating as the primary EMS server and three operating as backups. ERCOT uses two primary tools to monitor its RC Area, including monitoring SOLs and IROLs for pre- and post-Contingency exceedances. First, ERCOT uses a Real-Time Monitoring Contingency Analysis (RTCA) tool. Second, ERCOT uses a Real-Time Network Analysis (RTNET) tool to perform state estimation functions. In addition to its ongoing RC Area monitoring activities, ERCOT uses data snapshots from the active EMS server to develop system recovery and planning models. On July 7, 2016, an ERCOT system analyst was performing a weekly model verification upload and inadvertently loaded the previous week’s model into the EMS server’s active production environment. As a result, the active EMS server attempted to use this bad data and lost the ability to monitor the RC Area at 11:41:31. The data from the active EMS server replicated to the three standby EMS servers as designed. At 11:43:15, ERCOT personnel attempted to failover to the backup EMS servers, but this failover was unsuccessful because the corrupt data had already replicated on all of ERCOT’s EMS servers. As these EMS troubleshooting activities occurred, ERCOT personnel began implementing its established emergency procedures to address its loss of direct monitoring capability. Specifically, at 12:00:12, ERCOT issued a hotline call to all Transmission Operators (TOPs) to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. At 12:02:42, ERCOT issued a hotline call to Qualified Scheduling Entities (QSEs) regarding its EMS monitoring issues. Finally, at 12:05:25, ERCOT issued a second hotline call to all TOPs to update them regarding its ongoing EMS monitoring issues. As ERCOT personnel implemented its established emergency procedures, they likewise continued troubleshooting activities. Specifically, ERCOT personnel successfully reloaded a previous model save case and restored the EMS system’s production environment. ERCOT personnel then disabled a feature for archiving RTCA results and modified several excessive data mismatches within RTNET. With these steps, both the RTNET and RTCA ran successfully at 12:28:48. As a result, ERCOT regained the ability to continuously monitor its RC Area, ending the noncompliance. The root cause of this violation was that ERCOT lacked adequate controls to prevent the introduction of corrupt data into its EMS production environment. In particular, ERCOT did not technically preclude its personnel from inadvertently loading model cases into the EMS production environment or include cautionary messages or other prompts to prevent such actions. | IRO-003-2 | R2 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system as ERCOT successfully followed emergency procedures in coordination with other entities and there was no loss of Load and no SOL or IROL exceedances. Specifically, ERCOT’s failure to know the current status of all critical facilities for 47 minutes increased the risk that it would be unable to identify and/or properly respond to a potential contingency in a timely manner. However, a number of factors reduced the risks presented by ERCOT’s monitoring issue in the current circumstances. First, ERCOT possessed emergency procedures for responding to this type of monitoring capability loss, including instructions to issue hotline calls to TOPs to ensure the system was monitored by additional entities for previously identified critical reliability elements. These emergency procedures also include detailed steps for detecting and addressing any exceedances such as identifying the area of concern, viewing one-line displays, and directing generation to adjust output. During the issue in question, ERCOT personnel successfully implemented these emergency procedures to coordinate with RC Area TOPs. Specifically, within 20 minutes of the loss of its monitoring capability, ERCOT issued hotline calls and emergency notices to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances during the issue duration. In addition, ERCOT notified all QSEs regarding its EMS issues and remained in communication with two QSEs for large GOPs in the RC Area to maintain frequency and secure additional generation resources as necessary to address issues. Texas RE also considered ERCOT’s troubleshooting efforts to reduce the duration of the monitoring issue. In particular, these efforts limited the issue duration to 47 minutes, less than the 73 minute average duration for EMS outages across the Electric Reliability Organization (ERO) between October 2013 and April 2017. Finally, ERCOT possesses a number of enhanced system restoration plans and conducts routine drills on their implementation, reducing the likelihood that it would not adequately respond to a contingency if one had occurred during the issue. | 7/7/2016 (when ERCOT lost the ability to monitor the RC Area) | 7/7/2016 (when ERCOT successfully activated its RTNET and RTCA tools, restoring its direct RC Area monitoring capability) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) executed emergency operations procedures during the emergency and directed the TOPs to monitor their own service area and notify ERCOT if they observed any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations; 2) restored its ability to continuously monitor its RC Area; 3) revised the database loading script to remove the capability to load model cases into the active EMS Server; 4) added a banner to the database scripts to clearly label them as “Production Servers” 5) removed the snapshot creation option from the model load process to prevent accidental loading of the model case to the online production environment; 6) implemented a change to automatically save four days of RTCA solutions in a more accessible location to enable quicker resolution should another EMS outage occur; 8) conducted operator and shift engineer training on loss of EMS, including a review of the event in question; and 9) completed operator and shift engineer training on the new IRO and TOP requirements, which specifically require a real time assessment to be performed every 30 minutes. | 2016-11-14 | 2017-05-25 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. ERCOT was subject to event reporting requirements for a complete loss of Supervisory Control and Data Acquisition (SCADA) EMS and submitted such EOP-004 reports to identify these issues. Accordingly, Texas RE did not award self-reporting credit. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its Real-Time Analysis (RTA) capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2016016702 | Settlement Agreement | On December 22, 2016, ERCOT submitted a Self-Report stating that, as a Reliability Coordinator (RC), it was in violation of IRO-005-3.1a R1. Specifically, ERCOT failed to monitor its RC Area parameters for approximately 47 minutes on July 7, 2016. This was a category 1.h.i event, loss of monitoring or control at a Control Center such that it significantly affects the entity's ability to make operating decisions for 30 continuous minutes or more, specifically, this was a loss of operator ability to remotely monitor or control Bulk Electric System (BES) elements. In order to know the status of critical facilities in its RC Area, ERCOT possesses four Energy Management System (EMS) servers, with one operating as the primary EMS server and three operating as backups. ERCOT uses two primary tools to monitor its RC Area, including monitoring System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs) for pre- and post-Contingency exceedances. First, ERCOT uses a Real-Time Monitoring Contingency Analysis (RTCA) tool. Second, ERCOT uses a Real-Time Network Analysis (RTNET) tool to perform state estimation functions. In addition to its ongoing RC Area monitoring activities, ERCOT uses data snapshots from the active EMS server to develop system recovery and planning models. On July 7, 2016, an ERCOT system analyst was performing a weekly model verification upload and inadvertently loaded the previous week’s model into the EMS server’s active production environment. As a result, the active EMS server attempted to use this bad data and lost the ability to monitor the RC Area at 11:41:31. The data from the active EMS server replicated to the three standby EMS servers as designed. At 11:43:15, ERCOT personnel attempted to failover to the backup EMS servers, but this failover was unsuccessful because the corrupt data had already replicated on all of ERCOT’s EMS servers. As these EMS troubleshooting activities occurred, ERCOT personnel began implementing its established emergency procedures to address its loss of direct monitoring capability. Specifically, at 12:00:12, ERCOT issued a hotline call to all Transmission Operators (TOPs) to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. At 12:02:42, ERCOT issued a hotline call to Qualified Scheduling Entities (QSEs) regarding its EMS monitoring issues. Finally, at 12:05:25, ERCOT issued a second hotline call to all TOPs to update them regarding its ongoing EMS monitoring issues. As ERCOT personnel implemented its established emergency procedures, they likewise continued troubleshooting activities. Specifically, ERCOT personnel successfully reloaded a previous model save case and restored the EMS system’s production environment. ERCOT personnel then disabled a feature for archiving RTCA results and modified several excessive data mismatches within RTNET. With these steps, both the RTNET and RTCA ran successfully at 12:28:48. As a result, ERCOT regained the ability to continuously monitor its RC Area, ending the noncompliance. The root cause of this violation was that ERCOT lacked adequate controls to prevent the introduction of corrupt data into its EMS production environment. In particular, ERCOT did not technically preclude its personnel from inadvertently loading model cases into the EMS production environment or include cautionary messages or other prompts to prevent such actions. | IRO-005-3.1a | R1 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system as ERCOT successfully followed emergency procedures in coordinating with other entities and there was no loss of Load and no SOL or IROL exceedances. Specifically, ERCOT’s failure to monitor its designated RC Area parameters for 47 minutes increased the risk that it would be unable to identify and/or properly respond to a potential contingency in a timely manner. However, a number of factors reduced the risks presented by ERCOT’s monitoring issue in the current circumstances. First, ERCOT possessed emergency procedures for responding to this type of monitoring capability loss, including instructions to issue hotline calls to TOPs to ensure the system was monitored by additional entities for previously identified critical reliability elements. These emergency procedures also include detailed steps for detecting and addressing any exceedances such as identifying the area of concern, viewing one-line displays, and directing generation to adjust output. During the issue in question, ERCOT personnel successfully implemented these emergency procedures to coordinate with RC Area TOPs. Specifically, within 20 minutes of the loss of its monitoring capability, ERCOT issued hotline calls and emergency notices to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances during the issue duration. In addition, ERCOT notified all QSEs regarding its EMS issues and remained in communication with two QSEs for large GOPs in the RC Area to maintain frequency and secure additional generation resources as necessary to address issues. Texas RE also considered ERCOT’s troubleshooting efforts to reduce the duration of the monitoring issue. In particular, these efforts limited the issue duration to 47 minutes, less than the 73 minute average duration for EMS outages across the Electric Reliability Organization (ERO) between October 2013 and April 2017. Finally, ERCOT possesses a number of enhanced system restoration plans and conducts routine drills on their implementation, reducing the likelihood that it would not adequately respond to a contingency if one had occurred during the issue. | 7/7/2016 (when ERCOT lost the ability to monitor the RC Area) | 7/7/2016 (when ERCOT successfully activated its RTNET and RTCA tools, restoring its direct RC Area monitoring capability) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) executed emergency operations procedures during the emergency and directed the TOPs to monitor their own service area and notify ERCOT if they observed any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations; 2) restored its ability to continuously monitor its RC Area; 3) revised the database loading script to remove the capability to load model cases into the active EMS Server; 4) added a banner to the database scripts to clearly label them as “Production Servers”; 5) removed the snapshot creation option from the model load process to prevent accidental loading of the model case to the online production environment; 6) implemented a change to automatically save four days of RTCA solutions in a more accessible location to enable quicker resolution should another EMS outage occur; 7) conducted operator and shift engineer training on loss of EMS, including a review of the event in question; and 8) completed operator and shift engineer training on the new IRO and TOP requirements, which specifically require a real time assessment to be performed every 30 minutes. | 2016-11-14 | 2017-05-25 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. ERCOT was subject to event reporting requirements for a complete loss of Supervisory Control and Data Acquisition (SCADA) EMS and submitted such EOP-004 reports to identify these issues. Accordingly, Texas RE did not award self-reporting credit. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its Real-Time Analysis (RTA) capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2017017719 | Settlement Agreement | On June 9, 2017, ERCOT submitted a Self-Report stating that, as a Reliability Coordinator (RC), it was in violation of IRO-008-2 R4. Specifically, ERCOT failed to ensure that a Real-time Assessment (RTA) was performed at least once every 30 minutes in one instance on May 4, 2017. At 18:53, ERCOT’s Energy Management System (EMS) performed an RTA using its Real-Time Contingency Analysis (RTCA) and Real-Time Network Analysis (RTNET) tools. Four minutes after successfully completing this RTA, analogue telemetry data flags in ERCOT’s EMS identified issues with telemetered data points from a large Transmission Operator (TOP) and ERCOT’s RTNET failed to successfully solve. ERCOT system analysts immediately began troubleshooting activities, including manually replacing bad telemetry data points with the goal of achieving a converged solution by correcting transformer tap measurements, capability limits, analog and status telemetry, model errors such as topology or impedance parameters, and/or adjusting accuracy classes. At 19:17, ERCOT personnel began implementing its established emergency procedures by issuing hotline calls to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. Following these steps, ERCOT personnel then completed an initial manual RTA at 19:30, 37 minutes after ERCOT performed the previous RTA. ERCOT personnel then continued to perform manual RTAs at least once every 30 minutes until ERCOT regained its RTNET and RTCA capabilities at 23:07. The root cause of this violation was that ERCOT lacked detailed instructions regarding when during the system troubleshooting process to begin manually performing an RTA to meet the required 30-minute deadline. In particular, ERCOT personnel focused on troubleshooting activities in an attempt to recover monitoring capability and did not transition to performing the initial manual RTA in sufficient time to meet the 30-minute requirement. | IRO-008-2 | R4 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ERCOT’s failure to perform an RTA for seven minutes could have potentially reduced ERCOT’s situational awareness. However, during the 7-minute timeframe in which ERCOT exceeded the period for completing the execution of its RTA tools, ERCOT was receiving data and was able to communicate with TOPs and other market participants. These data and communications assisted ERCOT in maintaining situational awareness. Second, ERCOT personnel successfully implemented established emergency procedures designed to maintain situational awareness during monitoring capability issues. In particular, ERCOT System Operators issued hotline calls and emergency notices within the 30-minute RTA window to all TOPs to monitor their service areas and notify ERCOT of Transmission Facilities that exceeded their normal Facility Ratings, monitor all power flows to their last posted limits, report if power flows reached 85% of any Transmission Facility’s applicable limits, and notify ERCOT if there was a topology change that could affect any interface. This again bolstered ERCOT’s situational awareness and its ability to respond to any contingencies. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances or Frequency Measurable Events during the short issue duration. No harm is known to have occurred. | 5/4/2017 (30 minutes after ERCOT performed the last RTA) | 5/4/2017 (when ERCOT performed a manual RTA) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) performed an initial manual RTA; 2) continued to perform manual RTAs at least every 30 minutes until the analysis tools were restored; 3) updated its Shift Engineer Procedure to explicitly clarify the process for performing a manual RTA during analysis tool outages; 4) updated its Transmission and Security Desk Procedure to include corrective actions to take once a manual RTA is performed; 5) provided training to applicable ERCOT personnel regarding the need to perform RTAs every 30 minutes; and 6) created options to “replace/remove replace” status points for an entire company from a single display with a minimum number of actions and to restore the telemetered measurements for a specific company from a snapshot to enhance EMS system recovery efforts. | 2017-10-10 | 2017-12-04 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its RTA capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.
Texas Reliability Entity, Inc. (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2017017720 | Settlement Agreement | On June 9, 2017, ERCOT submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-001-3 R13. Specifically, ERCOT failed to ensure that a Real-time Assessment (RTA) was performed at least once every 30 minutes in one instance on May 4, 2017. At 18:53, ERCOT’s Energy Management System (EMS) performed an RTA using its Real-Time Contingency Analysis (RTCA) and Real-Time Network Analysis (RTNET) tools. Four minutes after successfully completing this RTA, analogue telemetry data flags in ERCOT’s EMS identified issues with telemetered data points from a large Transmission Operator (TOP) and ERCOT’s RTNET failed to successfully solve. ERCOT system analysts immediately began troubleshooting activities, including manually replacing bad telemetry data points with the goal of achieving a converged solution by correcting transformer tap measurements, capability limits, analog and status telemetry, model errors such as topology or impedance parameters, and/or adjusting accuracy classes. At 19:17, ERCOT personnel began implementing its established emergency procedures by issuing hotline calls to all TOPs to monitor their service areas and notify ERCOT of any Transmission Facilities that exceeded their normal Facility Ratings, any power flows that reached 85% of a Transmission Facility’s applicable limits, and any forced line operations. ERCOT personnel then completed an initial manual RTA at 19:30, 37 minutes after ERCOT performed the previous RTA. ERCOT personnel then continued to perform manual RTAs at least once every 30 minutes until ERCOT regained its RTNET and RTCA capabilities at 23:07. The root cause of this violation was that ERCOT lacked detailed instructions regarding when during the system troubleshooting process to begin manually performing an RTA to meet the required 30-minute deadline. In particular, ERCOT personnel focused on troubleshooting activities in an attempt to recover monitoring capability and did not transition to performing the initial manual RTA in sufficient time to meet the 30-minute requirement. | TOP-001-3 | R13 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ERCOT’s failure to perform an RTA for seven minutes could have potentially reduced ERCOT’s situational awareness. However, during the 7-minute timeframe in which ERCOT exceeded the period for completing the execution of its RTA tools, ERCOT was receiving data and was able to communicate with TOPs and other market participants. These data and communications assisted ERCOT in maintaining situational awareness. Second, ERCOT personnel successfully implemented established emergency procedures designed to maintain situational awareness during monitoring capability issues. In particular, ERCOT System Operators issued hotline calls and emergency notices within the 30-minute RTA window to all TOPs to monitor their service areas and notify ERCOT of Transmission Facilities that exceeded their normal Facility Ratings, monitor all power flows to their last posted limits, report if power flows reached 85% of any Transmission Facility’s applicable limits, and notify ERCOT if there was a topology change that could affect any interface. This again bolstered ERCOT’s situational awareness and its ability to respond to any contingencies. No entities within the ERCOT RC Area notified ERCOT that they were experiencing such problems. Further, there were no SOL exceedances or Frequency Measurable Events during the short issue duration. Finally, there was overlapping coverage of situational awareness, as each TOP continued to monitor Facilities and the status of Special Protection Systems within its local control areas. No harm is known to have occurred. | 5/4/2017 (30 minutes after ERCOT performed the last RTA) | 5/4/2017 (when ERCOT performed a manual RTA) | $140,000 (for TRE2016016699, TRE2016016700, TRE2016016701, TRE2016016702, TRE2017017719, and TRE2017017720) | Self-Report | To mitigate this violation, ERCOT: 1) performed an initial manual RTA; 2) continued to perform manual RTAs at least every 30 minutes until the analysis tools were restored; 3) updated its Shift Engineer Procedures to explicitly clarify the process for performing a manual RTA during analysis tool outages; 4) updated its Transmission and Security Desk Procedure to include corrective actions to take once a manual RTA is performed; 5) provided training to applicable ERCOT personnel regarding the need to perform RTAs every 30 minutes; and 6) created options to “replace/remove replace” status points for an entire company from a single display with a minimum number of actions and to restore the telemetered measurements for a specific company from a snapshot to enhance EMS system recovery efforts. | 2017-10-10 | 2017-12-04 | Neither Admits nor Denies | Texas RE reviewed ERCOT's internal compliance program and considered it to be a neutral factor in the penalty determination. Texas RE also considered ERCOT’s ongoing efforts to invest resources and project funding to strengthen its RTA capabilities for other scenarios. Although the issues identified have been fully mitigated, ERCOT is implementing system design changes to use other approaches to support RTA, including creating the ability to bypass the EMS system to connect to SCADA data directly in the case of a corrupt EMS. ERCOT has participated in NERC workshops sharing these types of technical alternatives across the industry. The project is presently scheduled for implementation in 2018 with a cost of approximately $160,000. Texas RE considered ERCOT's compliance history and determined there were no relevant instances of noncompliance.