## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Southwest Power Pool Regional Entity (SPP RE) | Board Of Public Utilities (Kansas City KS) (BPU) | NCR01061 | SPP2016015824 | Settlement Agreement | During a Compliance Audit conducted from June 6 to June 9, 2016, SPP RE determined that BPU, as a Transmission Operator (TOP), was in violation of FAC-014-2 R5.2 and as a Transmission Planner (TP), was in violation of FAC-014-2 R5.4. BPU’s Facility Ratings Methodology (FRM) provides that the emergency ratings for its transmission lines are equal to the normal ratings. Accordingly, the System Operating Limits (SOLs) for BPU’s transmission lines are based upon the normal Facility Ratings. Nevertheless, for five of the BPU 161 kV transmission lines examined by the SPP RE Audit Team, BPU submitted emergency SOLs that were higher than the normal Facility Ratings to its Reliability Coordinator (RC) and Planning Authority, the Southwest Power Pool (SPP). The root cause for this noncompliance was a lack of coordination between the BPU TOP and TP functional groups. Although both BPU functional groups utilize the Facility Ratings developed by the BPU Electric Engineering department as the foundation for SOLs and Facility Ratings, the emergency ratings submitted by the TO and TP to SPP were inconsistent with the BPU FRM. | FAC-014-2 | R5; R5.2; and R5.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to provide BPS entities that have a reliability-related need with accurate SOLs causes such entities to develop planning and operational models that do not reflect system equipment capabilities and limitations. When planning and operational models contain such errors, the potential exists for operational problems to go unidentified and/or the development of incorrect responses to operational issues. Here, the risk to the BPS is minimal because: 1) the BPU transmission system operates at a lower transmission voltage (161 kV); 2) the inaccurate SOLs were limited to the emergency ratings in planning models; and 3) BPU is a small municipal electric utility with only 61 miles of 161 kV transmission line and a peak load of 529 MW. No actual harm is known to have occurred as a result of the violation. | 9/23/2013 (the beginning of the audit period) | 3/2/2017 (when BPU provided its SOLs to those entities that have a reliability-related need) | $27,000 (for SPP2016015824 and SPP2016015826) | Compliance Audit | To mitigate this violation, BPU: 1. Verified and/or corrected ratings in the BPU Supervisory Control and Data Acquisition (SCADA) system; 2. Provided updated SOLs to the BPU TP for inclusion in SPP Planning Models; 3. Submitted SOLs to the RC (SPP) and to the Transmission Service Providers that share its portion of the RC Area. Received verification from the RC for BPU SOLs; 4. Submitted SOLs to the Planning Authority, TOPs, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners; and 5. Completed BPU SOL Methodology. | 3/2/2017 | 2017-03-16 | Admits | SPP RE reviewed BPU's internal compliance program and considered it to be a neutral factor in the penalty determination. A Settlement Agreement covering a violation of FAC-009-1 R2 (SPP2013012702) was filed with FERC under NP16-6-000 on December 30, 2015. On January 29, 2016, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The prior violation of FAC-009-1 R2 included, inter alia, BPU’s failure to follow its FRM by not establishing transmission facility emergency ratings equal to the normal ratings. Additionally, the prior violation of FAC-009-1 R2 cited BPU’s failure to provide facility ratings consistent with its FRM to its RC and Planning Coordinator. SPP RE has determined that the prior violation of FAC-009-1 R2 is a basis for aggravating the penalty for the instant violation because the underlying facts and circumstances of the prior violation of FAC-009-1 R2 and the instant violation are the same.
Southwest Power Pool Regional Entity (SPP RE) | Board Of Public Utilities (Kansas City KS) (BPU) | NCR01061 | SPP2016015826 | Settlement Agreement | During a Compliance Audit conducted from June 6 to June 9, 2016, SPP RE determined that BPU, as a Transmission Owner, was in violation of FAC-008-3 R6. The SPP RE Audit Team identified multiple issues with BPU’s Facility Ratings in finding that BPU did not have Facility Ratings for its solely and jointly owned Facilities that were consistent with its Facility Ratings Methodology (FRM). Issue #1. The Facility Ratings documentation utilized by BPU to document its substation Facility Ratings contained errors and omissions material to the determination of the BPU Facility Ratings. BPU failed to identify all the equipment in its substations necessary for the determination of the substation Facility Ratings and utilized incorrect ratings for the equipment in its substations. These errors were present in the Facility Ratings for 15 of BPU’s 17 substations and resulted in material changes to the Facility Ratings for 7 of the 17 substations. Issue #2. The Facility Ratings documentation utilized by BPU to document its transmission line Facility Ratings contained errors and omissions material to the determination of the BPU Facility Ratings. BPU failed to accurately document the Facility Ratings for transmission lines owned by or jointly owned with Kansas City Power & Light (KCPL). The Facility Ratings for four of the eight KCPL transmission lines were either omitted completely from the BPU documentation or incorrectly rated. The Maywood – Maywood South, Maywood South – Metropolitan and Woolcott – Maywood 161 kV transmission lines were omitted from the BPU documentation. The Metropolitan – Shawnee Mission 161 kV tie line was included in the BPU Documentation, however, the Facility Rating was incorrectly identified as 224 MVA and not 293 MVA. The root cause of this noncompliance was a lack of internal controls to ensure the accuracy and availability of documentation used in the development of BPU’s Facility Ratings. | FAC-008-3 | R6 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The failure to utilize accurate transmission facility ratings has the potential to: 1) compromise planning and operational models; 2) result in inaccurate protection system settings and Energy Management System alarm set points; and 3) cause operators to respond inappropriately to system events. Here, the risk to the BPS is mitigated because the BPU transmission system operates at a lower transmission voltage (161 kV) and BPU is a small municipal electric utility with only 61 miles of 161 kV transmission line and a peak load of 529 MW. Additionally, there are no Interconnection Reliability Operating Limits or flowgates for any of BPU’s transmission facilities. No actual harm is known to have occurred as a result of the violation. | 9/23/2013 (the beginning of the audit period) | 06/12/2017 (the date BPU completed its mitigation plan) | $27,000 (for SPP2016015824 and SPP2016015826) | Compliance Audit | To mitigate this violation, BPU: 1. Revised the BPU FRM to address the procedural and documentation issues identified during the audit; 2. Acquired evidence to support device ratings for the BPU transmission facilities; 3. Updated the BPU Facility Ratings consistent with the BPU FRM; and 4. Reviewed, verified ,and updated the BPU 161 kV One-Line drawing. | 6/12/2017 | 2017-07-13 | Admits | SPP RE reviewed BPU's internal compliance program and considered it to be a neutral factor in the penalty determination. A Settlement Agreement covering a violation of FAC-009-1 R1 (SPP2013012989) was filed with FERC under NP16-6-000 on December 30, 2015. On January 29, 2016, FERC issued an order stating it would not engage in further review of the Notice of Penalty. BPU’s prior violation of FAC-009-1 R1 included, inter alia, its failure to establish generation facility ratings that were consistent with its FRM and the development of incorrect transmission circuit ratings due to BPU incorrectly identifying the transmission conductor as the most limiting element for its transmission circuits. SPP RE has determined that the prior violation of FAC-009-1 R1 is a basis for aggravating the penalty for the instant violation because the facts and circumstances of the prior violation of FAC-009-1 R1 and the instant violation are similar. A Settlement Agreement covering a violation of FAC-008-3 R3 (SPP2013013001) was filed with FERC under NP16-6-000 on December 30, 2015. On January 29, 2016, FERC issued an order stating it would not engage in further review of the Notice of Penalty. BPU failed to include Protection Systems devices and substation buses, as required by FAC-008-3 R3.4.1 in its FRM. SPP RE has determined that the prior violation of FAC-008-3 R3 is a basis for aggravating the penalty for the instant violation because the prior and instant violations include BPU’s omission of equipment material to the determination of the BPU Facility Ratings.