## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Homestead, City of (HST) | NCR00037 | FRCC2017016812 | Settlement Agreement | On January 17, 2017, HST submitted a Self-Report stating that, as a Balancing Authority, it was in violation of BAL-001-1 R2. This violation began on April 6, 2016, when the NERC-assigned L10 calculation value was reduced from 7.47 to 4.58, and HST failed to update the Energy Management System (EMS) during the annual implementation period as specified by the ERO (values to be updated by April 5, 2016 as specified in BAL-003-1 Frequency Bias Setting and L10 Values for 2016). The violation ended on August 25, 2016 when the EMS was updated with the correct value. The root cause for this violation was inadequate management oversight and the failure of the Senior Load Dispatcher to understand that both the frequency response and the L10 values were to be checked and, if necessary, change one or both, and then validate the change. | BAL-001-1 | R2. | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk is that HST could have operated outside of the NERC established limits for ACE, thus exacerbating possible frequency excursions. HST's total footprint of 107 MW and L10 of only 4.58 MW would have minimal impact on the BPS. HST recalculated the Control Performance Standard 2 with the new L10 and determined they operated within the performance requirement for the duration of the violation. No harm is known to have occurred. | 4/6/2016 (when HST failed to update the EMS during the implementation period as specified) | 8/25/2016 (when the EMS was updated with the correct value) | $22,000 (for FRCC2017016812, FRCC2016015952, FRCC2017018469, FRCC2017017318, and FRCC2017017317) | Self-Report | To mitigate this violation, HST: 1) corrected the L10 value; 2) developed an internal control for Outlook Calendar reminders on the compliance calendar, the calendar of the manager of system operations and the calendar of the Senior Load dispatcher for March 31; 3) completed root cause analysis; 4) revised the BAAL procedure to include specific steps on how to change the L10, epsilon and frequency bias settings; and 5) provided training to all System Operators on the updated procedure. | 2017-10-24 | 2018-05-02 | Neither Admits nor Denies | FRCC reviewed HST's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. HST’s ICP was evaluated and deficiencies were identified including a lack of effective management oversight, which contributed to the number of Balancing Authority issues.
Florida Reliability Coordinating Council, Inc. (FRCC) | Homestead, City of (HST) | NCR00037 | FRCC2016015952 | Settlement Agreement | On July 27, 2016, HST submitted a Self-Report stating that, as a Balancing Authority (BA), it was in violation of BAL-001-2 R2. The violation started on July 1, 2016, when HST exceeded the BA Area Control Error (ACE) Limit (BAAL) high limit for 5 consecutive minutes (5 minutes beyond the 30 minutes allowed by the Requirement). The noncompliance ended when system conditions changed bringing HST’s ACE back to within the required limits. On July 1, 2016, a storm hit the HST area causing a drop in load. At 18:32 HST was allowing up to 14 MWs to flow into the Interconnection at a time when the Interconnection frequency was above 60 Hz. The 14 MWs is outside of HST's BAAL. In preparation for BAL-001-2 becoming effective on July 1, 2016, HST created BAAL alarms that come in at five (5) minute intervals while either the BAAL high or low limit is exceeded. The alarms were not enabled on July 1, 2016 and have since been activated. During the first instance, since HST had less than four (4) MWs of generation on line, the only way to mitigate the situation within 30 minutes was to curtail an Interchange transaction. The System Operator (SO) cut the Interchange schedule for the next hour, and the BAAL high limit exceedance cleared at 19:07. During HST's extent of condition review, HST determined there had been a second instance. At 06:15 on July 22, 2016, the BAAL high five minute alarm came in due to over-scheduling of Interchange. The SO did not curtail any transactions but merely adjusted the next hour schedule lower. The BAAL high limit exceedance cleared at 07:02, after a total of 52 minutes. HST was in violation for 22 minutes. The causes of this violation were determined to be: 1) insufficient training prior to the standard becoming enforceable 2) SO lack of understanding of how to properly cut and/or curtail a schedule and 3) alarms not being active on the effective date. | BAL-001-2 | R2. | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS is that HST could operate outside of the NERC-established limits for ACE, thus exacerbating possible frequency excursions. The loss of load due to storms or outages could trigger the BAAL high alarm depending on the system frequency and the amount of load lost. The loss of a generating resource could trigger the BAAL low alarm depending on the system frequency and the amount of generation lost. However, there is minimal risk to the BPS if HST exceeds the BAAL high frequency trigger due to the relatively small size of HST's 107 MW system, which equals 0.2% of the FRCC summer load. No harm is known to have occurred. | 7/1/2016 (when HST exceeded the BAAL) | 7/22/2016 (when the BAAL came back within limits) | $22,000 (for FRCC2017016812, FRCC2016015952, FRCC2017018469, FRCC2017017318, and FRCC2017017317) | Self-Report | To mitigate this violation, HST: 1) developed an internal procedure and check sheet which lists the steps the System Operator (SO) should take for either a BAAL high alarm or a BAAL low alarm; 2) trained each SO on the BAAL procedure and check sheet; and 3) completed an extent of condition review. | 2016-08-26 | 2017-10-26 | Neither Admits nor Denies | FRCC reviewed HST's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. HST’s Compliance Program was evaluated and deficiencies were identified including a lack of effective management oversight, which contributed to the number of Balancing Authority issues. FRCC reviewed HST's compliance history and determined the previous instance of noncompliance was not relevant and should not serve as a basis for aggravating the penalty. In FRCC2017016812 (also included in this SNOP filing) for BAL-001-1, the language of the requirement R2 addressed CPS2 performance. Under BAL-001-2, meeting CPS2 performance criteria was removed and replaced with meeting BAAL performance criteria for requirement R2.
Florida Reliability Coordinating Council, Inc. (FRCC) | Homestead, City of (HST) | NCR00037 | FRCC2017018469 | Settlement Agreement | On October 13, 2017 HST submitted a Self-Report stating that, as a Balancing Authority (BA) it was in violation with BAL-001-2 R2. The initial violation started on September 3, 2017, when HST exceeded the BA Area Control Error (ACE) Limit (BAAL) low limit for 40 consecutive minutes (10 minutes beyond the 30 minutes allowed by the Requirement) dragging more than 5 MWs. The noncompliance ended when system conditions changed, bringing HST’s ACE back to within the required limits. HST conducted an extent of condition review which revealed a violation of the BAAL high limit for 40 consecutive minutes (10 minutes beyond the 30 minutes allowed by the Requirement) on January 24, 2018. HST reviewed the alarm summary and verified 11 BAAL high alarms were received. The root cause was an insufficient BAAL procedure for forecasting the next day's load, resulting in a mismatch of power being scheduled to meet the required load and unclear SO expectations. Additionally, a contributing cause was the System Operator was not in the control center at the time the alarms occurred for the second instance. | BAL-001-2 | R2. | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS is that HST operated outside of the NERC-established limits for ACE, thus exacerbating possible frequency excursions. The loss of load due to storms or outages could trigger the BAAL high alarm depending on the system frequency and the amount of load lost. The loss of a generating resource could trigger the BAAL low alarm depending on the system frequency and the amount of generation lost. This is a repeat violation of BAL-001-2 R2, which occurred within the last year and increases the risk of recurrence given the prior Mitigation Plan did not prevent this occurrence. However, there is minimal risk to the BPS if HST exceeds the BAAL high frequency trigger due to the relatively small size of HST's 107 MW system, which equals 0.2% of the FRCC summer load. No harm is known to have occurred. | 9/3/2017 (when HST exceeded the BAAL) | 1/24/2018 (when the BAAL came back within limits) | $22,000 (for FRCC2017016812, FRCC2016015952, FRCC2017018469, FRCC2017017318, and FRCC2017017317) | Self-Report | To mitigate this violation, HST: 1) came back into the BAAL limits; 2) completed root cause analysis; 3) developed an internal control to use forecasted temperatures when determining the next day's schedule; 4) completed training of all System Operators on the use of the forecasted temperatures in the next day's schedule; 5) conducted extent of condition review; 6) reviewed the alarm summary to verify if the BAAL alarms came in; 7) completed a second root cause analysis; 8) reviewed the BAAL alarms protocol; and 9) created an "Expectations of the System Operator" document and reviewed with each System Operator. | 2018-03-19 | 2018-05-02 | Neither Admits nor Denies | FRCC reviewed HST's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. HST’s ICP was evaluated and deficiencies were identified including a lack of effective management oversight, which contributed to the number of Balancing Authority issues. FRCC reviewed HST's compliance history and determined there was a relevant instance of noncompliance, which was considered to be aggravating. The mitigation plan for FRCC2016015952 (also included in this SNOP filing) had been closed prior to the first instance of this violation.
Florida Reliability Coordinating Council, Inc. (FRCC) | Homestead, City of (HST) | NCR00037 | FRCC2017017318 | Settlement Agreement | During a Compliance Audit conducted from March 27, 2017 to March 29, 2017, FRCC determined that HST, as a Balancing Authority, was in violation of BAL-003-1.1 R2. As of April 6, 2016, HST had not implemented the updated Frequency Bias Setting (FBS) into its Area Control Error (ACE) calculation during the implementation period specified by the ERO (values to be updated by April 5, 2016 as specified in the BAL-003-1 FBS and L10 Values for 2016). HST did not implement the correct FBS until February 27, 2017. HST discovered the error on August 25, 2016 and attempted to change the FBS from -1.0 to -0.45, however EMS would not allow a setting above -1.0. Making the correct adjustment required working with the Energy Management System (EMS) vendor, and the FBS was updated to -0.50 due to system restriction. The root cause for this violation was the failure of the Senior Load Dispatcher to understand that both the frequency response and the L10 values should be validated and if necessary change one or both, and then validate. | BAL-003-1.1 | R2. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By not implementing the correct frequency bias settings into the ACE equation, HST would not provide its appropriate share of the Frequency Response needed to maintain Interconnection Frequency within predefined bounds by arresting frequency deviations and supporting frequency. The risk was increased as the FBS was incorrect for 328 days. The risk was reduced due to HST's FBS changing from 7.47 (FBS = -0.75 Mw/0.1Hz) to 4.58 (FBS= -0.45/0.1Hz); therefore by not updating the HST FBS, it created an over-biased impact as a Balancing Authority where HST was contributing more than required to arrest frequency deviations. Furthermore, HST's total footprint is 107 MW which equals 0.2% of the FRCC summer load. No harm is known to have occurred. | 4/6/2016 (when HST did not implement the updated Frequency Bias Setting (FBS) into its Area Control Error (ACE) calculation) | 2/28/2017 (when the calculation was updated) | $22,000 (for FRCC2017016812, FRCC2016015952, FRCC2017018469, FRCC2017017318, and FRCC2017017317) | Compliance Audit | To mitigate this violation, HST: 1) entered the correct Frequency Bias Settings into its EMS; 2) performed a root cause analysis and cause and effect analysis; 3) revised the BAAL procedure to include specific steps on how to change the L10, epsilon and frequency bias settings; and 4) trained each system operator on the new procedure. | 2017-09-27 | 2018-05-02 | Neither Admits nor Denies | FRCC reviewed HST's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. HST’s ICP was evaluated and deficiencies were identified including a lack of effective management oversight, which contributed to the number of Balancing Authority issues.
Florida Reliability Coordinating Council, Inc. (FRCC) | Homestead, City of (HST) | NCR00037 | FRCC2017017317 | Settlement Agreement | During a Compliance Audit conducted from March 27, 2017, to March 29, 2017, FRCC determined that HST, as a Distribution Provider and Transmission Owner was in violation of PRC-006-2 R9. The issue started on October 1, 2015, the effective date of the Standard, as nine of HST’s 11 underfrequency load shedding (UFLS) relays were not set in accordance with the FRCC UFLS program, and ended on March 15, 2017 when the re-calibration was complete. The UFLS relays had Time Delays that allowed greater than the required 0.28 seconds, which would exceed the maximum timing requirement criteria (Time Delay = Intentional Delay + Relay Delay + Breaker Delay) defined in the FRCC UFLS program. The technician did not include the Breaker Delay in the Time Delay calculation and used a +/- 3% of 0.28 which resulted in a Time Delay greater than 0.28 seconds. This was demonstrated by their test records, which showed the nine relays operated with an opening time of greater than 0.28 seconds. The root cause for this violation was a lack of instruction by the supervisor and a misinterpretation by the P&C Technician. | PRC-006-2 | R9. | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk is that during a UFLS event, the UFLS load shedding on the HST system would have been slower to operate than was designed and planned for by the Planning Coordinator (FRCC), which could have allowed an increased frequency decay by not shedding all the load properly. The risk was reduced because the HST UFLS program included the correct amount of load (40 MWs), in accordance with the FRCC UFLS program. Of the nine relays that were set incorrectly, the slowest reaction time before a relay would have activated was 0.03 seconds late. Additionally, HST’s total summer peak load is 107 MW or .2% of the FRCC summer load of 45,350 MW. No harm is known to have occurred. | 10/1/2015 (when the relays were not set in accordance with the UFLS program) | 3/15/2017 (when the re-calibration was complete) | $22,000 (for FRCC2017016812, FRCC2016015952, FRCC2017018469, FRCC2017017318, and FRCC2017017317) | Compliance Audit | To mitigate this violation, HST: 1) the P&C Supervisor instructed his staff to set the UFLS relays with a time delay less than 0.28 seconds; 2) recalibrated the UFLS relays to comply with the FRCC UFLS program; 3) performed cause and effect analysis to determine the root cause; and 4) completed root cause analysis actions. | 2017-09-30 | 2018-05-02 | Neither Admits nor Denies | FRCC reviewed HST's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. HST’s ICP was evaluated and deficiencies were identified including a lack of effective management oversight, which contributed to the number of Balancing Authority issues. FRCC considered HST's compliance history to be an aggravating factor in the penalty determination. FRCC2014013458 includes a violation of PRC-006 where two circuits were counted twice in the calculation for its installed automatic UFLS which would result in the shedding of only 46% of its load when 55% was required per the FRCC UFLS program.
The North American Electric Reliability Corporation (NERC) as Compliance Enforcement Authority (CEA) | Peak Reliability (Peak) | NCR10289 | NCEA201717867 | Settlement Agreement | During a Spot Check conducted from May 23, 2017 through May 24, 2017, NERC determined that Peak, as a Reliability Coordinator (RC), was in violation of COM-002-4 R1. Peak did not develop documented communication protocols for its operating personnel that issue Operating Instructions as required by R1. Although documented protocols existed in various versions and revisions, instances of noncompliance remained until Version 11 became effective. Specifically, Version 9 and Version 10 of Peak’s documented communication protocols failed to specify: (1) that operators should take an alternate action if a response is not received or if the Operating Instruction was not understood by the receiver in accordance with part 1.2; and (2) the format for time identification in accordance with part 1.5. Version 9 of Peak’s communication protocols went into effect on July 1, 2016. Version 11 of Peak’s documented communication protocols, which became effective on April 24, 2017, included all components of three-part communication identified in part 1.2 and clarified the format for time identification in accordance with part 1.5. The cause of this violation was that Peak incorrectly relied on a technical justification document written by the COM-002-4 standard drafting team, when the draft was posted for comment, in deciding to instruct its operating personnel to continue issuing directives as a type of Operating Instruction. Peak also inaccurately placed inordinate emphasis on the word “command” in the definition of Operating Instruction as related to its daily operating communications and, thus, failed to apply all of the R1 protocols to its oral, person-to-person, Operating Instructions. | COM-002-4 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Throughout the duration of this violation, Peak’s operating personnel utilized communications that did not meet the minimum set of protocols that must be included in documented communication protocols. This increased the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the BPS. However, this risk was mitigated here based on the following factors. Peak's documented communication protocols in effect throughout the time of the issue specified that three-part communication was to be used when issuing or receiving Operating Instructions and when issuing Reliability Directives. So, while Peak's documented communication protocols did not specify that an alternative action was to be taken if the communication was not understood or not received, they did specify that the RC System Operator should reissue the communication until the information was repeated back correctly. Accordingly, the issuer would be aware that the Operating Instruction or Reliability Directive was not received or understood. No harm is known to have occurred. | 7/1/2016 (when the Standard became mandatory and enforceable on Peak) | 4/24/2017 (when Version 11 of Peak RC’s communication protocols was put into effect) | $0 (for NCEA201717867, NCEA201717868, and NCEA201717866) | Spot Check | To mitigate this violation, Peak: 1) refined SOP-230 Communication Protocol v12.0 to include reduction of duplicative language and expectations for communication protocols when resynchronizing islands; 2) updated standard operating practice document identifying basic communication protocol requirements for RC System Operators; and 3) trained operating personnel on the updated communications protocols. | 2018-01-11 | 2018-06-11 | Neither Admits nor Denies | NERC did not afford penalty credit for Peak's internal compliance program in the penalty determination. Each violation, in isolation, was determined to be minimal or moderate risk. However, NERC decided to file them in combination as a Spreadsheet Notice of Penalty as the violations resulted in a more moderate risk exposure overall. In assessing a zero-dollar penalty, NERC took into account Peak's prompt mitigating activities to remediate the violation. Further, this violation was not related to the mitigation associated with the 2011 Southwest Blackout.
The North American Electric Reliability Corporation (NERC) as Compliance Enforcement Authority (CEA) | Peak Reliability (Peak) | NCR10289 | NCEA201717868 | Settlement Agreement | During a Spot Check conducted from May 23, 2017 through May 24, 2017, NERC determined that Peak, as a Reliability Coordinator (RC), was in violation of COM-002-4 R2. System Operators responsible for the Real-time operation of the interconnected bulk power system (BPS) at Peak issued Operating Instructions, including during an Emergency, prior to being trained on the documented communications protocols developed in R1. The documented communication protocols developed for COM-002-4 R1, Version 9, had not been released at the time the training course ID “PEAKRC_009_Operating_Instructions_and_Reliability_Directives” was developed and implemented. As such, the training focused on the COM-002-4 Standard and Requirements and Version 8 of Peak's documented communication protocols. The cause of the violation was Peak's failure to provide initial training for its System Operators that adequately addressed communication protocols required by R1 prior to the System Operators issuing an Operating Instruction. | COM-002-4 | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. Peak's operating personnel's failure to utilize communications that did not comport with the required minimum set of protocols increased the possibility of miscommunication that could (1) lead to action or inaction harmful to the reliability of the BPS, and (2) lead to confusion with external entities with whom they communicated. However, this risk was mitigated here based on the following factors. First, Peak provided training course ID "PEAKRC_009_Operating_Instructions_and_Reliability_Directives" to all of its System Operators prior to the effective date of COM-002-4 or prior to them issuing an Operating Instruction. Second, while the "PEAKRC_009_Operating_Instructions_and_Reliability_Directives" training course focused on Version 8 of the documented protocols, it did include a review of COM-002-4, the NERC definition of Operating Instruction, and Version 9 of the documented communication protocols, which were not yet effective but were specifically developed for COM-002-4 R1. Finally, while Peak continued to the use the term "Reliability Directives," it was considered equivalent to an Operating Instruction, and the use of three-part communication was required for all Reliability Directives, reducing the likelihood that a Reliability Directive would be misunderstood. No harm is known to have occurred. | 11/9/2016 (when the operator first issued an operating instruction after the effective date of the Standard) | 4/19/2017 (when Peak provided its System Operators with initial training on its documented communication protocols developed for COM-002-4) | $0 (for NCEA201717867, NCEA201717868, and NCEA201717866) | Spot Check | To mitigate this violation, Peak: 1) provides continuous training on its documented Communication Protocols and has included a session in each of the four (4) cycle trainings for 2018; 2) provided Communication Protocol training focusing on defining Operating Instructions and detailing the requirements of Peak’s Communication Protocol v11.0 during the spring 2017 training cycle; 3) provided Communication Protocol training focusing on developing and expanding communication skills during the issuance of Operating Instructions, as well as identifying when an Operating Instruction is to be implemented during the winter 2017-2018 off-cycle training; 4) provided Communication Starboard training focusing on defining and practicing effective Three-Part Communication during the spring 2018 cycle training; and 5) developed a 2.5 hour course on Operating Instructions and communication training for the cycle 2 training session beginning spring 2018. | 2018-04-25 | 2018-06-11 | Neither Admits nor Denies | NERC did not afford penalty credit for Peak's internal compliance program in the penalty determination. Each violation, in isolation, was determined to be minimal or moderate risk. However, NERC decided to file them in combination as a Spreadsheet Notice of Penalty as the violations resulted in a more moderate risk exposure overall. Peak has six prior instances of noncompliance with COM-002-2 R2. Although the prior noncompliance involved the same standard, the root cause and conduct differed. The prior noncompliance involved failures to issue directives and the use of three-part communication, while the violation here involved failure to update procedures to account for changes in the Standard language. The prior mitigating activities would not have prevented the current violation. In assessing a zero-dollar penalty, NERC took into account Peak's prompt mitigating activities to remediate the violation. Further, this violation was not related to the mitigation associated with the 2011 Southwest Blackout.
The North American Electric Reliability Corporation (NERC) as Compliance Enforcement Authority (CEA) | Peak Reliability (Peak) | NCR10289 | NCEA201717866 | Settlement Agreement | During a Spot Check conducted from May 23, 2017 through May 24, 2017, NERC determined that Peak, as a Reliability Coordinator (RC), violated PER-005-2 R1. Peak failed to apply the systematic approach to training to identify the change in expectations for the RC System Operators based on the new definition of Operating Instruction and COM-002-4 and, thus, provide training to the System Operators accordingly. Peak has a documented process to determine if a new Reliability Related Task (RRT) needs to be created or if a modification to an existing RRT is warranted. However, Peak did not recognize changes to the competency needed to perform its company-specific RRTs based on changes to COM-002-4 and the suite of revisions to TOP/IRO standards applicable to the RC. The cause of this violation was that Peak failed in its use of a systematic approach to training to address the common competency of "communicate / advise / direct" embedded in many RRTs related to issuing Operating Instructions. | PER-005-2 | R1 | Medium | High | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was aggravated because Peak’s protocols and training focused on Reliability Directives, but did not provide guidance or training to System Operators on using Operating Instructions which, unlike Reliability Directives, are not limited to being used during Emergencies or Adverse Reliability Impacts. This could result in RC System Operators not being aware of the ability to issue or not issuing an Operating Instruction to proactively maintain reliability in situations that are not Emergencies. However, this risk was mitigated by the following factors. First, Peak had communication protocols that mandated three-part communication for all Operating Instructions, including Reliability Directives. Second, Peak provided the System Operators training on Reliability Directives and using the communication protocols, including three-part communication. No harm is known to have occurred. | 7/1/2016 (when the Standard became mandatory and enforceable on Peak) | 4/19/2017 (when Peak provided its operators with training on its revised communication protocols that eliminated the term "Reliability Directive" and recognized the broader impacts of Operating Instructions) | $0 (for NCEA201717867, NCEA201717868, and NCEA201717866) | Spot Check | To mitigate this violation, Peak: 1) revised the Reliability Related Tasks embedded step language from communicate/advise/direct to communicate/instruct to align with the IRO/TOP 4/1/2017 Reliability Standard effective dates; 2) provided Communication Protocol training focusing on defining Operating Instructions and detail the requirements of Peak’s Communication Protocol v11.0 during the Spring 2017 training cycle; 3) provided Communication Protocol training focusing on developing and expanding communication skills during the issuance of Operating Instructions, as well as identifying when an Operating Instruction is to be implemented during the Winter 2017-2018 off-cycle training; and 4) provided Communication Starboard training focusing on defining and practicing effective Three-Part Communication during the Spring 2018 cycle training. | 2018-04-25 | 2018-06-11 | Neither Admits nor Denies | NERC did not afford penalty credit for Peak's internal compliance program in the penalty determination. Each violation, in isolation, was determined to be minimal or moderate risk. However, NERC decided to file them in combination as a Spreadsheet Notice of Penalty as the violations resulted in a more moderate risk exposure overall. Peak has one prior instance of noncompliance with PER-005-1 R1. The prior violation is distinguishable from the instant violation because the prior violation arose from Peak’s failure to have an established process for making changes to the training program. In contrast, Peak has a documented systematic approach to training in the instant violation, but failed to identify the change in expectations for the RC system operators based on the new definition of Operating Instruction and COM-002-4 and provide training to the system operators accordingly. In assessing a zero-dollar penalty, NERC took into account Peak's prompt mitigating activities to remediate the violation. Further, this violation was not related to the mitigation associated with the 2011 Southwest Blackout.