## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Public Service Company of New Mexico (PNM) | NCR05333 | WECC2017016932 | Settlement Agreement | On February 6, 2017, PNM submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-008-0 R2. Specifically, PNM reported that during an internal investigation for an unrelated issue, it discovered that it failed to implement its maintenance and testing program for 14 of its 75 (18.7%) Under Frequency Load Shedding (UFLS) devices, as required by PRC-008-0 R2. Three of the UFLS devices had completed work orders but were missing the associated test record for the prior maintenance activities. The remaining 10 UFLS devices did not have a completed work order or an associated test record for either a last or prior test. One relay missed its maintenance interval. None of the UFLS devices had been transitioned to PRC-005-6 at the time the violation was identified, so each UFLS system was still subject to PRC-008-0 at the time the issue was discovered. After reviewing all relevant information, WECC determined that PNM failed to implement its UFLS equipment maintenance and testing program for 13 (not 14 as originally self-reported) of its 75 (17.3%) UFLS devices as required by PRC-008-0 R2. The root cause of the noncompliance was due to management guidance or expectations not being well-defined, understood, or enforced. Specifically, PNM management did not require that a formal process be in place to ensure test records for each maintenance activity were uploaded upon completion of the maintenance and testing task, which resulted in gaps in the records of PNM’s maintenance and testing activities. WECC determined that this violation began on June 18, 2007 when the Standard and Requirement became mandatory and enforceable to PNM, and ended on June 6, 2017, when the last of the UFLS devices in scope was tested and documented as being tested. | PRC-008-0 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). PNM failed to implement its UFLS equipment maintenance and testing program for 13 of its 75 (17.3%) UFLS devices as required by PRC-008-0 R2. Such failure could potentially result in degradation of equipment, or cause a misoperation to occur that could result in unforeseen load shedding, or prevent planned load shedding from occurring. Of the 13 devices identified in this Self-Report, 3 (or 3/13 = 23.1% of self-reported UFLS devices) do not currently support WECC's Southern Island Under-Frequency Load Tripping Plan (SILTP). As such, failure of these devices to operate to shed load during an under-frequency condition would have had no impact to the BPS and no impact to the SILTP. The remaining 10 devices represent approximately 4% of PNM's total load. As a worst-case scenario, failure of these devices to operate during an extreme under-frequency event equates to approximately 81 MW of load out of 714 MW included in the UFLS. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. The UFLS devices in scope for this self-report were part of different 'Groups' within WECC's UFLS program. Each 'Group' was designed to operate at different levels of frequency drop. Group 1 devices, for example, comprise 5.3% of the armed load and are set to shed load at 59.5 Hz. Group 2 devices, which comprise 5.9% of the armed load, do not shed load until the frequency drops again to 58.9 Hz. The devices in scope for thisSelf-Report were spread across 5 separate 'Groups' in the UFLS program. Additionally, PNM’s system operators were trained and authorized to immediately shed firm load as necessary to address any system condition that threatened the reliability of the BPS, including manually shedding load to address extreme system conditions. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. | 6/18/2007 (when the Standard and Requirement became mandatory and enforceable) | 6/6/2017 (when the last of the UFLS devices in scope was tested and documented as being tested) | $0 (for WECC2017016932, WECC201701933, and WECC2017016934) | Self-Report | To mitigate this violation, PNM: 1) performed maintenance and testing on the devices in scope; 2) documented the maintenance and testing of the devices in scope; 3) performed a formal reconciliation of the devices associated with PRC-006 and PRC-008 to ensure the Cascade database matches its tracking sheet of relays; 4) perform an annual reconciliation to ensure that the Cascade data base remains consistent with the field inventory and establish an annual DocMinder, automated reminder, to trigger completion of the annual reconciliation; 5) implemented a formal procedure to include the collection, evidence review, and packaging and storage of evidence that maintenance had occurred to meet NERC compliance requirements; 6) conducted training to craft supervisors, engineers from the Technical Maintenance Management Department, and management from all departments on the new procedure; and 7) generated an automated reminder in its work management system to perform an annual reconciliation of the UFLS devices. | 2017-06-15 | 2018-01-31 | Admits | WECC reviewed PNM's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC applied an aggravating factor and escalated the disposition treatment from Compliance Exceptions to a Settlement Agreement without a penalty. The violation duration for PRC-008-0 R2 was 3,651 days; for PRC-011-0 R1 it was 3,606 days; and for PRC-017-0 R1 it was 3,629 days. PNM did not have any detective controls in place that could have helped identify the issues sooner to lessen the violation duration and thereby lessen the risk. WECC considered PNM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Public Service Company of New Mexico (PNM) | NCR05333 | WECC2017016933 | Settlement Agreement | On February 6, 2017, PNM submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-011-0 R1. Specifically, PNM reported that during an internal investigation for an unrelated issue, it discovered that it did not track and document the dates for the last or prior maintenance and testing for two of its three (66.7%) Undervoltage Load Shedding (UVLS) schemes--specifically, 12 of 30 (40%) UVLS devices, which included one UVLS Transformer CVT, eight UVLS batteries, and three UVLS relays. For two of the three UVLS relays, PNM had located completed work orders but was unable to locate the associated test record for the prior maintenance activity. The third relay had a completed work order, but the associated test record for the last maintenance activity was missing; also, there was no work order and associated test record for the prior maintenance activity. The one UVLS transformer CVT and the eight UVLS batteries were never maintained. None of the UVLS systems had begun transitioning to PRC-005-6 at the time the issue was identified, so each UVLS system was still subject to PRC-011-0 at the time the issue was discovered. After reviewing all relevant information, WECC determined that PNM failed to appropriately maintain its maintenance and testing records for 12 of 30 (40%) UVLS devices, as required by PRC-011-0 R1. The root cause of the violation was due to management guidance or expectations not being well-defined, understood, or enforced. Specifically, PNM management did not require that a formal process be in place to ensure test records for each maintenance activity were uploaded upon completion of the maintenance and testing task, which resulted in gaps in the records of PNM’s maintenance and testing activities. WECC determined that the start of this violation is June 18, 2007, when the Standard and Requirement became mandatory and enforceable to PNM, and ended on May 1, 2017, when the last of the UVLS devices in scope was tested and documented. | PRC-011-0 | R1; R1.6 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. PNM failed to appropriately maintain its maintenance and testing records for 12 of 30 (40%) UVLS devices, as required by PRC-011-0 R1. Such failure could potentially result in degradation of equipment, or a misoperation that could result in planned load shedding not occurring or unforeseen load shedding. However, if the UVLS devices did not operate properly during sustained low voltages in the local area where the UVLS was installed, failure of the scheme to operate as designed would not necessarily have a broader impact of the surrounding transmission system. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. There was no actual impact to the system as both the schemes in scope have operated correctly for under-voltage conditions during the violation period. The one UVLS scheme operated correctly for an under-voltage condition on October 3, 2016. The other UVLS scheme operated correctly on December 8, 2016 and January 21, 2017 for low voltage conditions. Additionally, the devices that comprised the UVLS schemes and identified in the issue were designed to take independent actions, meaning failure of one device in the scheme would not impact the ability of the other devices to operate properly. The scheme was designed to mitigate low voltages in a local area and has not been identified as needed for broader protection of the BPS. Two of PNM's neighboring Transmission Owners/Operators also have UVLS schemes to address low voltages in the affected area and the likelihood of these adjacent schemes failing simultaneously with PNM's UVLS Scheme is low. Lastly, PNM’s system operators were trained and authorized to immediately shed firm load as necessary to address any system condition that threatened the reliability of the BPS. Based on this, WECC determined that there was a remote likelihood of causing minor harm to the BPS. No harm is known to have occurred. | 6/18/2007 (when the Standard and Requirement became mandatory and enforceable) | 5/1/2017 (Mitigation Plan completion) | $0 (for WECC2017016932, WECC201701933, and WECC2017016934) | Self-Report | To mitigate this violation, PNM: 1) performed and documented the maintenance and testing on the devices in scope; 2) performed a formal reconciliation of its PRC-006 and PRC-011 devices to ensure the Cascade database matches its tracking sheet of UVLS devices; 3) implemented a formal documentation procedure to include the collection, evidence review, and packaging and storage of evidence that maintenance had occurred to meet NERC compliance requirements; and 4) conducted training to craft supervisors, engineers from the Technical Maintenance Management Department, and management of all departments, on the new procedure. | 2017-05-01 | 2018-01-31 | Admits | WECC reviewed PNM's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC applied an aggravating factor and escalated the disposition treatment from Compliance Exceptions to a Settlement Agreement without a penalty. The violation duration for PRC-008-0 R2 was 3,651 days; for PRC-011-0 R1 it was 3,606 days; and for PRC-017-0 R1 it was 3,629 days. PNM did not have any detective controls in place that could have helped identify the issues sooner to lessen the violation duration and thereby lessen the risk. WECC considered PNM's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Public Service Company of New Mexico (PNM) | NCR05333 | WECC2017016934 | Settlement Agreement | On February 6, 2017, PNM submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-017-0 R1. Specifically, PNM reported that during an internal investigation for an unrelated issue, it discovered that it failed to implement its maintenance and testing program for eight of its 45 (17.8%) Special Protection System (SPS) devices that were incorporated into three of its four remedial action schemes. Specifically, five of the SPS devices had a completed work order, but were missing the associated test record for either the last or prior maintenance activities. One SPS device had no work order and was missing a test record for the prior maintenance activity. The remaining two SPS devices had never been maintained or tested in accordance with PNM’s maintenance and testing program. After reviewing all relevant information, WECC determined that PNM failed to implement its SPS maintenance and testing program for eight SPS devices, as required by PRC-017-0 R1. The root cause of the noncompliance was due to management guidance or expectations not being well-defined, understood, or enforced. Specifically, PNM management did not require that a formal process be in place to ensure test records for each maintenance activity were uploaded upon completion of the maintenance and testing task, which resulted in gaps in the records of PNM’s maintenance and testing activities. WECC determined that the start of this violation is June 18, 2007, when the Standard and Requirement became mandatory and enforceable to PNM, and ended on May 24, 2017, when PNM recorded either the last, prior, or both test dates for the devices in scope. | PRC-017-0 | R1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. PNM failed to implement its SPS maintenance and testing program for eight SPS devices, as required by PRC-017-0 R1. Such failure could potentially result in degradation of equipment, or cause a misoperation to occur that could result in unforeseen load shedding, or prevent planned load shedding from occurring. The potential impact to the BPS resulting from failure to either test or maintain PNM’s SPS would be that the devices in the scheme would not operate properly when the system experiences sustained low voltages in the local area where the UVLS is installed. In this case, there is no increased risk of impact to the broader BES as the low voltage conditions would not propagate beyond the local area for failure of either one of these schemes. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. There was no actual impact to the BPS as the Import Contingency Load Shedding Scheme (ICLSS) SPS correctly initiated during a Category 1a event on August 7, 2016. Further, the ICLSS successfully passed a full functional test of the SPS scheme following the August 7, 2016 event. There was no actual impact to the two other SPS schemes in scope as there has been no known operation or failure to operate. Two of PNM's neighboring Transmission Owners/Operators also have UVLS schemes to address low voltages in the affected area and the likelihood of these adjacent schemes failing simultaneously with PNM's ICLSS scheme is low. Additionally, the SPS scheme is comprised of a central logic controller and multiple UVLS relays. The central logic controller was tested and maintained. The UVLS relays detect local voltage but can only operate if an enabling signal is sent from the central logic controller. As a result, the relays were treated as part of the SPS scheme instead of UVLS which keys off of only local voltage. The SPS is designed to arm more load for shedding than is necessary to mitigate the system conditions for which the scheme was designed. Therefore, failure of one or more of the devices was unlikely to reduce the overall effectiveness of the scheme. The ICLSS SPS devices take independent actions, meaning that failure of one relay or other protection system component in the SPS would not have an impact on operation of any of the other devices in the system. Lastly, PNM’s system operators were trained and authorized to immediately shed firm load as necessary to address any system condition that threatened the reliability of the BPS. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. | 6/18/2007 (when the Standard and Requirement became mandatory and enforceable) | 5/24/2017 (when PNM recorded either the last, prior, or both test dates for the devices in scope) | $0 (for WECC2017016932, WECC201701933, and WECC2017016934) | Self-Report | To mitigate this violation, PNM: 1) performed and documented maintenance and testing on the devices in scope; 2) performed a formal reconciliation of its PRC-006 and PRC-017 to ensure the Cascade database matches its tracking sheet of Remedial Action Scheme (RAS) devices; 3) implemented a formal documentation procedure to include the collection, evidence review, and packaging and storage of evidence that maintenance had occurred to meet NERC compliance requirements; and 4) conducted training to craft supervisors, engineers from the Technical Maintenance Management Department, and management of all departments, on the new procedure. | 2017-03-31 | 2018-01-31 | Admits | WECC reviewed PNM's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC applied an aggravating factor and escalated the disposition treatment from Compliance Exceptions to a Settlement Agreement without a penalty. The violation duration for PRC-008-0 R2 was 3,651 days; for PRC-011-0 R1 it was 3,606 days; and for PRC-017-0 R1 it was 3,629 days. PNM did not have any detective controls in place that could have helped identify the issues sooner to lessen the violation duration and thereby lessen the risk. WECC considered PNM's compliance history and determined there were no relevant instances of noncompliance.