## Public Non-CIP SNOP Posting
Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015939 | Settlement Agreement | On July 15, 2016, PJM submitted a Self-Report stating that, as a Transmission Operator, it was in violation of TOP-004-2 R2. The Self-Report relates to an incident that occurred on May 5, 2016 in which FirstEnergy Utilities, as agent for Monongahela Power Company (FirstEnergy), did not fully arm a Special Protection Scheme (SPS) pursuant to PJM’s instruction. There was no outage or loss of load. Even if a loss of load occurred, the incident would not have qualified as a reportable event under EOP-004-2. On May 5, 2016, the Belmont - Harrison 500 kV line, owned by FirstEnergy, tripped and locked out at 16:59 due to storms in the area of Parkersburg, WV. Shortly after the Belmont-Harrison line tripped, FirstEnergy’s contingency analysis tool showed that there were two unsolved contingencies. As a result, the FE South operator immediately informed the entity about the unsolved contingencies, and in response, the entity operator instructed FE South operators to arm the Belmont SPS. Arming this SPS requires selecting the condition (loss of the Belmont-Harrison 500 kV line) and selecting a generating unit at Pleasants Generation Station (Pleasants) to trip. The SPS acts by tripping the selected Pleasants unit if the Belmont T5 765/500kV transformer trips, thereby preventing instability at Pleasants. FE South operators called the Generator Operator to determine which unit to designate to trip in the SPS. However, when arming the SPS, the FE South operators did not select a unit to trip and thus did not fully arm the SPS. As a result, there was the potential for generator unit instability at Pleasants Generation Station and localized overloads on the 138 kV lines in the Parkersburg, WV area. Shortly thereafter, at 17:15, the FE South operator informed the entity that they believed the SPS was in service. When properly put in service, the SPS logic would remove the non-solving contingencies from FirstEnergy’s contingency list. However, the entity responded that its system was showing that the SPS was not armed. FirstEnergy immediately began investigating the discrepancy, and determined that it skipped a manual step required to arm the SPS. At 18:54, the SPS was properly put in service. The root cause of this miscommunication was the FE South Operator not effectively following the procedure for arming the SPS combined with lack of a clear indication on FirstEnergy’s SPS energy management system screen as to the status of the SPS. These causes involve the management practice of verification, which includes ensuring changes to assets are completed as intended according to the relevant process. Pursuant to Section 5.11 of the Compliance Monitoring and Enforcement Program, ReliabilityFirst determined that FirstEnergy was wholly responsible for the actions or omissions that caused or contributed to the violation. | TOP-004-2 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. By not fully arming the SPS, there was the potential for generator unit instability at Pleasants Generation Station, which could have caused units at Pleasants (approximately 1,050 MW) to trip off, and the potential for a localized outage in the Parkersburg, WV area, with the total consequential loss of load limited to 145 MW. Thus, an event, had it occurred, would not have constituted a reportable event under Reliability Standard EOP-004-2. ReliabilityFirst determined that the loss of the Pleasants units would not have caused a cascading event to the Bulk Electric System. The risk to the system was also mitigated because the entity had sufficient spinning reserves (1,800 MW) to offset any potential loss. This was confirmed through a Dynamic Stability Cascade Analysis study performed by FirstEnergy. ReliabilityFirst reviewed this study, verified the inputs, and agreed with FirstEnergy’s conclusion. No harm is known to have occurred. | 5/5/2016 At 17:14, when FirstEnergy believed it fully armed the SPS | 5/5/2016 At 18:54, when FirstEnergy properly armed the SPS | 34000 | Self-Report | To mitigate this violation, FirstEnergy : 1) reviewed and updated their Belmont SPS EMS screen to be more intuitive and provide a positive indication of SPS status; 2) revised its procedure “FE-SOUTH-NOP-226 FE-South Special Protection System Operation” with updated instructions for the Belmont SPS; and 3) retrained its operators on the process to place the Belmont SPS in service. While the parties disagreed as to whether the facts and circumstances at issue involved the “single most severe contingency” and “instability” as used in TOP-004-2 R2, FirstEnergy nonetheless mitigated the issue and implemented preventive measures, thus significantly reducing the likelihood of recurrence. | 2016-10-19 | 2017-02-07 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity’s and FirstEnergy’s internal compliance programs (ICPs) and considered them to be mitigating factors in the penalty determination. For example, entity senior management, including the entity executive team and the entity Board of Managers for the corporate compliance program, is involved in compliance matters. The entity has also established a formal compliance review committee, known as the Regulatory Oversight and Compliance Committee, which is charged with evaluating identified compliance issues and recommended actions from entity senior management and, ultimately, the entity Board of Managers. Furthermore, the entity established compliance with NERC and Regional Reliability Standards as a corporate goal. FirstEnergy's ICP is managed by its FERC & State Regulatory Compliance Department (FERC Compliance), which has corporate oversight responsibilities and is independent from FirstEnergy business units that are responsible for complying with the NERC Reliability Standards. Business Unit “Compliance Champions” assist FERC Compliance with monitoring activities that encourage opportunities to increase reliability. FE’s compliance program has strong support and participation of senior management who drive a culture that promotes continuous improvement with compliance. The FERC Compliance Department is under the VP, Compliance & Regulated Services and Chief FERC Compliance Officer (VP/Chief FERC CO), who reports directly to the President, FirstEnergy Utilities, who reports to the CEO. The VP/Chief FERC CO also has direct access to the CEO and leads the Executive Reliability Steering Committee. ReliabilityFirst considered the entity’s and FirstEnergy’s TOP-004 R2 compliance history and determined there were no relevant instances of noncompliance. PJM and FirstEnergy have been highly cooperative throughout the enforcement process. They voluntarily provided ReliabilityFirst with an abundance of information regarding the incident in a manner that was detailed, well-organized, and timely. They have been open with the ReliabilityFirst regarding this incident, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the facts. ReliabilityFirst awarded credit to encourage this sort of interaction in the future.
Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016016710 | Settlement Agreement | On December 23, 2016, BPA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1.1b R2. Specifically, BPA reported that on November 22, 2016, it discovered that a transfer trip analog device was installed at its Control Center, without indicating in the Asset Management System, critical information necessary to trigger priority and maintenance intervals for the device. Within the Asset Management System, the window for asset intake contained a system indicator designed to identify when a device is subject to the requirements of PRC-005-1.1b R2. In this case, the system indicator was not applied to the device, therefore the maintenance interval trigger did not operate as intended. The transfer trip analog device was installed in January 2008, and Protection System maintenance and testing should have been completed in March 2014 as defined by BPA’s Protection System Maintenance and Testing Program. After reviewing all the relevant information, WECC determined that BPA failed to implement its Protection System maintenance and testing program for one transfer trip analog device within its maximum maintenance interval as required by PRC-005-1.1b R2. The root cause of the violation was a lack of controls for new Protection System devices added to BPA’s Asset Management System, to verify accuracy and completeness. WECC determined that this violation began on March 1, 2014, when the Protection System maintenance and testing was due for the transfer trip analog device and ended on March 28, 2016, when maintenance and testing were completed for the transfer trip analog device, for a total of 759 days of noncompliance. | PRC-005-1.1b | R2. | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, BPA failed to implement its Protection System maintenance and testing program for one transfer trip analog device within its maximum maintenance interval as required by PRC-005-1.1b R2. Such failure could result in a device misoperation leading to a loss of generation or damage to the associated 230 kV transmission elements if the device failed to send the signal to trip. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as intermediate. However, BPA had good compensating controls. If the transfer trip had failed to operate, BPA would have dropped generation. BPA has many generation drop contingencies in place to address a failed transfer trip. Based on this, WECC determined that there was a low likelihood of causing intermediate harm to the BPS. No harm is known to have occurred. | 3/1/2014 (when the Protection System maintenance and testing were due for the transfer trip analog device) | 3/28/2016 (when maintenance and testing were completed for the transfer trip analog device) | No penalty | Self-Report | To mitigate this violation, BPA: 1) completed testing of equipment maintenance for its transfer trip analog device; 2) established a process document to complete an equipment visibility assessment for new device installs; and 3) reviewed system wide Transfer Trip equipment in the Asset Management System to ensure equipment had appropriate indicators and maintenance trigger applications.; | 2017-03-23 | 2017-04-20 | Does Not Contest | On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. BPA is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation. WECC would have assessed a financial penalty of $39,000 for the violation described herein if such penalties could be levied against BPA. WECC considered BPA's PRC-005 R2 compliance history in determining the disposition track. WECC considered BPA's PRC-005 R2 compliance history to be an aggravating factor in the disposition determination.