## Public CIP Oct. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010722 | CIP-007-3 | R6; R6.2 | MRO_URE1 self-reported noncompliance with CIP-007-3 R6 because it did not have automatic alerting enabled on several Critical Cyber Assets (CCAs) for 129 days. More specifically, two physical servers and nine virtual servers were deployed with improper configuration; therefore automatic alerts for detected cybersecurity incidents would not have been sent, as required by R6.2. When implementing new devices, MRO_URE1 executes a compliance readiness checklist. The checklist contains each configuration task for setting up controls used for achieving compliance. The checklists for these devices were completed successfully. However, the script used to configure alerting had a typo, so the alerts were not being received. The misconfiguration was identified and corrected after 129 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were protected by several layers of cybersecurity controls including: anti-virus/anti-malware software; up-to-date security patches; and authentication controls such as complex passwords. The CCAs were also located in an Electronic Security Perimeter and a Physical Security Perimeter as required. Finally, logs covering the entire period were available, and a review of the logs confirmed that no cybersecurity incidents had occurred. | Upon discovery, MRO_URE1 immediately corrected the alerting and monitoring functionality. Additionally, logs were reviewed to verify that no events occurred during the lapse in alerting. Lastly, the compliance readiness process has been updated to include a test verifying the functionality of alerting at the time of implementation. This should result in the immediate detection of any configuration errors before any lapse in alerting occurs. MRO verified that MRO_URE1 completed its mitigating activities.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010723 | CIP-004-3 | R4 | MRO_URE1 self-reported noncompliance with CIP-004-3 R4 because it failed to maintain its list of individuals authorized for unescorted physical and/or cyber access to Critical Cyber Assets (CCAs). Specifically, one employee was granted cyber access accidentally outside of the standard process, so the access was not properly documented in the list. The issue was identified during a quarterly review process and was mitigated within 55 days, outside the 7 calendar days of any change of personnel with access, as required by R4.1. The quarterly review encompassed all individuals with CCA access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the access granted to the employee was read-only, and was appropriate for the employee’s role. Additionally, the employee in question was already approved for other CCA access and had a proper personnel risk assessment and cybersecurity training as required by the Standards. | Upon discovery, the access approval was documented in the NERC CIP access management tool, which recorded the business need as determined by the designated approver and synched up the authorized and configured access lists. Because controls are already implemented for access management, the processes for obtaining access were not changed. Instead, additional reminders were sent to management via letter regarding following established procedures, and a quick reference card was distributed to all personnel responsible for NERC CIP access configuration. MRO verified that MRO_URE1 completed its mitigating activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010669 | CIP-005-1 | R1; R1.6 | NPCC_URE1 self-reported an issue with CIP-005-1 R1.6. Specifically, two servers that are Cyber Assets used to support systems within the Electronic Security Perimeter (ESP) were connected to a switch using a virtual LAN that was not documented as a non-critical Cyber Asset. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because BPS operations would not be impacted if the systems at issue sustained an outage. Additionally, the devices are non-critical Cyber Assets, and accordingly are afforded the protections of CIP-002 through CIP-009 applicable to non-critical Cyber Assets. Lastly, the undocumented switch was contained in the same Physical Security Perimeter (PSP). | NPCC_URE1 mitigated this issue by disconnecting the devices at issue and the undocumented switch and re-connecting it to switches that were documented. NPCC_URE1 reviewed the logs on the devices and found no evidence that there was any unauthorized access to the system via the undocumented switch.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009847 | CIP-005-1 | R1.5 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-005-1 R1.5. Specifically, four NPCC_URE2 Cyber Assets that control or monitor access to the Electronic Security Perimeter (ESP) were not running anti-virus and anti-malware tools, as required by CIP-007-1 R4. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the four devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. Specifically, the Critical Cyber Assets (CCAs) within the ESP had mitigating measures in place to minimize the impact of a virus. Specifically, NPCC_URE2 utilizes a service contractor to monitor the ESP, and any intrusions or attempts to breach the ESP are immediately detected and reported to properly mitigate any risk. This is an open-ended TFE and the compensating measures have been in place since 2010. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009849 | CIP-007-1 | R4 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-007-1 R4. Specifically, three devices inside the Electronic Security Perimeter (ESP) were not running anti-virus and anti-malware tools, as required by the Standard. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the three Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. Specifically, NPCC_URE2 had firewalls in place and the devices at issue did not have access to the Internet. These devices are all located within the NPCC_URE2 ESP. The devices are only connected through a VPN router. NPCC_URE2 utilizes a procedure that disables the VPN router when not needed to reduce the risk of intrusions. The VPN router is only enabled when updates are necessary. When the updates are completed, the VPN router is again disabled. This process is logged. This procedure was identified by the NPCC auditors as a Best Practice during the on-site CIP Audit. This is an open-ended TFE and the compensating measures have been in place since 2010. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009850 | CIP-007-1 | R5 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-007-1 R5. Specifically, three NPCC_URE2 devices inside the Electronic Security Perimeter (ESP) are not capable of technically enforcing strong passwords. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the three devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. NPCC_URE2 utilizes a procedural control for passwords for the devices at issue. The administrator for these devices ensures that strong passwords are used and that the password is changed annually or whenever there is a change in authorized personnel. The administrator is the person who sets the shared password for these devices, and changes the password when required. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010134 | CIP-006-3a | R1; R1.1; R1.2 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-006-3 R1. Specifically, NPCC_URE2's control room Physical Security Perimeter (PSP) had a dropped ceiling that did not have a solid wall extending up to the ceiling, as required by R1.1 and R1.2. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the control room was manned 24 hours a day, seven days a week. The control room also has an alarm system, physical access system, cameras and defense in depth, meaning that there are several security systems that monitor the PSP. Additionally, any visitors are escorted and signed in and out per NPCC_URE2's cybersecurity policy. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010135 | CIP-006-3a | R2 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-006-3 R2. Specifically, two NPCC_URE2 physical access control devices were not running anti-virus or anti-malware software, as required by CIP-007-3 R4.1. Specifically, certain parts of the devices do not support the installation of anti-virus software, as they do not contain an operating system with this capability. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the two devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the physical security systems at issue are not used to monitor or control Critical Cyber Assets and would have no impact on NPCC_URE2's Critical Cyber Assets if compromised. NPCC_URE2's Cyber Assets that authorize or log access to Physical Security Perimeters (PSPs) are afforded the protections specified in CIP-006-3a R2, with the exception of the parts of the devices described herein. These parts are located within the PSP. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010440 | CIP-006-3c | R8 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-006-3c R8. RFC_URE1 produced an inspection report stating that it must replace a door contact pursuant to its maintenance and testing program for physical security systems. The contractor who could fix the door was onsite at RFC_URE1 that day, so RFC_URE1 requested the contractor to repair the door. As a result, RFC_URE1 repaired the door the same day it discovered the issue. RFC_URE1, however, did not create a formal work order for the repair, and therefore failed to retain the record for the maintenance, as required by CIP-006-3c R8.2. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated because RFC_URE1 repaired the door contact the same day it discovered the issue and had just failed to document the maintenance work. The CIP-006 R8 issue discovered during the Audit began nine days prior to the discovery date. The problem with the door was that a contact was misaligned. The misaligned contact did not affect the magnetic lock on the door, so there was never unimpeded access. The door would only operate when an authorized individual swiped a badge. The bad contact only affected the transmission of the status of the door (“open” or “closed”) to the central monitoring system. The door in question is on a specific floor of RFC_URE1’s corporate headquarters. In order to access that door, there are two other sets of security protections. In order to gain unescorted access to the corporate headquarters an individual must pass through one of four turnstiles which are opened using a corporate ID card. Visitors must be escorted in order to gain access. Additionally, access to the entire floor is restricted by sliding glass doors on either end of the elevator bank access corridor. The remainder of the floor is only accessible to employees who have associated access privileges. Visitors must call someone and be met at one of the doors to gain access to the floor. The door in question resides behind both of these physical protections. | RFC_URE1 reinforced the requirement of documenting maintenance, with appropriate personnel including minor repairs completed when a technician is already on-site for other work. In addition, RFC_URE1 revised its maintenance and testing form to include two additional categories: "Follow Up/Date" and "Service Ticket Number" to document the work performed. Furthermore, RFC_URE1 now includes invoices documenting repairs in the maintenance and testing form.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010434 | CIP-005-3a | R5 | RFC_URE2 self-reported an issue with CIP-005-3a R5 to ReliabilityFirst. Typically, RFC_URE2’s electronic access logs are automatically transferred daily from routers to a central log repository. Two issues occurred that prevented logging from these routers. First, the routers ran out of virtual memory which caused subsequent log records to overwrite previous log records. Second, the vendor’s technical issue prevented the automatic backup and storage of the logs on the central log repository. As a result, a portion of the log data that includes logging for attempts at or actual unauthorized access for these routers were not captured in the central log repository for over four months. RFC_URE2 began employing an alternate source on for one router and, 22 days later, for the remaining two routers, which successfully captured and retained logs for these three routers. As a result, there was a net loss of logs of 55 days for two routers and 35 days for the remaining router. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because the logging issue did not affect alerting for attempts at or actual unauthorized access as RFC_URE2's system issues alerts in real time. These alerts do not rely on the storage of log files in the central log repository. In addition, RFC_URE2 subsequently retrieved and retained log files resulting in the recovery of log files for one router and 22 days later for the other two routers. | RFC_URE2 committed to take certain actions to mitigate the issue. RFC_URE2 implemented an alternate logging source, which began capturing and retaining logs. In addition, RFC_URE2 ensured that the vendor resolved the technical issue on the centralized log repository.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009866 | CIP-004-3 | R4 | RFC_URE3 self-reported an issue with CIP-004-3 R4. A RFC_URE3 contract security officer resigned from the RFC_URE3 contractor. RFC_URE3 previously granted the contract security officer authorized unescorted physical access to areas containing Critical Cyber Assets (CCAs). RFC_URE3, however, failed to update its list of personnel who have physical access to (CCAs) until about 5 months after the contract security officer resigned which was not within seven calendar days of this change in access rights of personnel, as required by CIP-004-3 R4.1. In addition, RFC_URE3 failed to disable the contract security officer’s physical access badge within seven calendar days, as required by CIP-004-3 R4.2. RFC_URE3 disabled the contract security officer’s physical access badge; however, the contract security officer still had the physical access badge when RFC_URE3 discovered the issue. 15 days after RFC_URE3 disabled the physical access badge, the contract security officer voluntarily surrendered the badge. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because prior to the time period of the issue, the contract security officer had cybersecurity training and a valid personnel risk assessment, which included an extensive background check similar to that required for unescorted access to nuclear power plants, a driving record review and stringent fitness for duty testing. In addition, the contract security officer never had authorized cyber access to CCAs, and operations personnel occupy the areas to which the contract security officer had access 24 hours a day. As a result of the foregoing, it was less likely that the contract security officer could gain access unnoticed and cause harm to the integrity of the CCAs. Furthermore, the contract security officer did not physically access the areas containing CCAs during the time period of the issue. | RFC_URE3 committed to take certain actions to mitigate the issue. RFC_URE3 disabled the contract security officer’s physical access badge. In addition, RFC_URE3 established an internal process whereby the security contractor will communicate employee status changes to appropriate RFC_URE3 management personnel regarding security personnel that is distinct from the pre-existing weekly roster updates. Furthermore, the security contractor will follow up within 24 hours of that out-of-service effective date to verify that RFC_URE3 has removed access within 24 hours. If RFC_URE3 has not removed access, the system will send a second notification. In addition, RFC_URE3 began generating weekly automated emails that provide to its contractors and vendors lists of its employees who have authorized unescorted physical access to CCAs. The contractors and vendors are directed to review the lists to determine whether access is still required and to reply whether any require cancellation. If there is no reply during the same week, RFC_URE3 will cancel access for those individuals.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2012009705 | CIP-007-1 | R5.3 | SPP RE_URE1 submitted two Self-Reports to SPP RE stating that it was noncompliant with CIP-007-1 R5.3.2 and R5.3.3. Because CIP-007-1 R5.3.2 and R5.3.3 are closely related, SPP RE consolidated the two Self-Reports into one Self-Report. Regarding R5.3.2, SPP RE_URE1 reported that during an internal compliance audit, SPP RE_URE1 identified 23 accounts with access to its Energy Management System (EMS) that had passwords that did not consist of a combination of the three required character types (alpha, numeric and "special" characters). The passwords did consist of at least seven characters, and contained alpha and numeric characters, but failed to include a “special” character, as prescribed by R5.3.2. Regarding R5.3.3, SPP RE_URE1 identified three devices that had not had their passwords changed annually. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE1 had accounts that did not fully conform to the CIP-007-1 R5.3.2 requirement, these accounts did conform to two out of the three criteria listed in the subrequirement. Furthermore, all of the accounts that were not compliant with CIP-007-1 R5.3 were under continuous monitoring via an automated event and monitoring solution that provided unauthorized access detection. There were no incidents or events of unauthorized access detected during SPP RE_URE1's period of noncompliance. | SPP RE_URE1 changed passwords on its EMS Critical Cyber Assets (CCAs), Protected Cyber Assets (PCAs), and electronic access control systems (EACSs) to meet the following requirements: 1) Length: Passwords shall be a minimum of 8 characters. 2) Complexity: Passwords shall consist of a combination of upper and lower alpha, numeric, and “special” characters. 3) Frequency: Passwords, at a minimum, shall be changed on an annual basis. SPP RE_URE1 also notified users of the requirement to select and use passwords that meet the complexity requirements as detailed in its passwords requirement document. Finally, SPP RE_URE1 changed passwords on every EMS CCA, PCA and EACS to comply with the CIP-007-1 R5.3 Requirements.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2012009924 | CIP-004-1 | R4.1 | During a CIP Compliance Audit of SPP RE_URE2, the SPP RE CIP Audit Team identified noncompliance with CIP-004-1 R4.1 related to the quarterly reviews of SPP RE_URE2's list of personnel with access to Critical Cyber Assets (CCAs). Specifically, the audit team determined that SPP RE_URE2 could not demonstrate that it had reviewed its lists of personnel with electronic access to CCAs on a quarterly basis during the audit period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE2 could not show that it had reviewed the list of personnel with electronic access to CCAs quarterly, it did demonstrate that it reviewed the list of personnel with physical access to CCAs quarterly, as required by this Standard. Furthermore, SPP RE_URE2 demonstrated that it had conducted an annual review of access privileges, including electronic access, to CCA information, as required by CIP-003-3 R5. Finally, SPP RE_URE2 has a small number of employees with electronic access, and a low employee turn-over rate. Accordingly, changes to these employees' electronic access privileges would have been noticed by SPP RE_URE2 IT staff, despite the lack of a quarterly review. | SPP RE_URE2 conducted quarterly reviews of electronic access rights, transferring the responsibility to perform these reviews to the CIP compliance specialist, who is knowledgeable about electronic access rights. Additionally, SPP RE_URE2 updated its list to more efficiently identify those individuals with electronic access.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2012009929 | CIP-006-1 | R1 | During a CIP Compliance Audit of SPP RE_URE2, the SPP RE CIP Audit Team identified SPP RE_URE2's noncompliance with CIP-006-1 R1. A SPP RE_URE2 employee inappropriately gave itself physical access to a Physical Security Perimeter (PSP), the control room (SPP RE_URE2's backup control center), without following the procedures established in the SPP RE_URE2 Physical Security Plan. SPP RE_URE2's Physical Security Plan requires employees to get permission from the appropriate manager or supervisor and to complete the authorized access procedures before being granted access. The employee accessed the control room PSP in order to perform testing of the security door contact. The PSP in which the employee granted itself access to was a recently re-designated PSP. The re-designation had split one PSP into two PSPs. The SPP RE_URE2 employee lacked permission to access the re-designated PSPs. However, prior to the re-designation, the SPP RE_URE2 employee did have access to the one PSP. The SPP RE_URE2 employee granted itself access at 12:23 p.m., and terminated access at 12:25 p.m., after testing the door devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the SPP RE_URE2 employee inappropriately gave itself physical access to the control room, the employee had access to the control room prior to its re-designation from one PSP, to two PSPs. Additionally, records show that the employee's access to the control room existed only for a total of two minutes for the purpose of testing the doors. The employee had the necessary training and Personnel Risk Assessment (PRA). | SPP RE_URE2 took disciplinary action against the SPP RE_URE2 employee and counseled the employee on the correct process to follow to gain access to PSPs. SPP RE_URE2 granted the employee authorized access to the control room PSP.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2012009931 | CIP-006-1 | R3 | During an SPP RE CIP Compliance Audit of SPP RE_URE2, the SPP RE CIP Audit Team discovered a remediated issue of CIP-006-3 R5. The Audit Team observed that SPP RE_URE2 had not implemented technical controls for monitoring physical access at an access point between two Physical Security Perimeters (PSP), SPP RE_URE2's control room and SPP RE_URE2's computer room. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE2 did not have monitoring measures in place for the access point between its control room and computer room, the access point did have a keyed lock securing SPP RE_URE2's control room from any entry from the computer room. The keyed lock at the access point did not secure SPP RE_URE2 computer room from entry from the control room. Individuals with approved access to SPP RE_URE2's control room also have approved access to the computer room. Besides having a physical access control for the access point between the two PSPs, SPP RE_URE2 also had security measures in place at the access point to the building that housed the two PSPs. The building housing the PSPs has security guards, a barbed-wire fence surrounding the building, two steel doors, which were alarmed and a magnetically locked access door. | SPP RE_URE2 combined the two PSPs thereby negating the need to monitor the door connecting them.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2012009932 | CIP-006-3c | R6 | During a CIP Compliance Audit of SPP RE_URE2, the SPP RE CIP Audit Team identified SPP RE_URE2's noncompliance with CIP-006-3c R6. Specifically, the Audit Team identified three instances in which SPP RE_URE2 did not adhere to its Physical Security Plan when logging the escorted physical access of three visitors to SPP RE_URE2's control room Physical Security Perimeter (PSP). This remediated issue involved one SPP RE_URE2 employee and two outside visitors. According to SPP RE_URE2's Physical Security Plan, visitors must fill out a visitor’s log in order to gain access to certain areas within SPP RE_URE2's facilities. The visitor logs identify the name of the visitor, the entry/exit date and time, and the name of the accompanying SPP RE_URE2 escort. In one instance, a SPP RE_URE2 employee visitor failed to record the PSP exit time, and in the second instance SPP RE_URE2 failed to record the PSP exit time of one outside visitor as well as the PSP exit time and name of the SPP RE_URE2 escort for another outside visitor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE2 did not follow its procedures by recording the times that the three individuals exited a SPP RE_URE2 PSP, all three individuals went through multiple layers of security to gain access to the PSP. The additional security measures included: a check-in with SPP RE_URE2 security, issuance of a visitor’s badge, and escorted access to enter the PSP. Additionally, the one SPP RE_URE2 employee that failed to record the SPP RE_URE2 PSP exit time, had been in the SPP RE_URE2 control center before, and had appropriately and completely filled out the visitor logs during those times. None of the outside visitors had the capability to enter the PSP without an escort. Finally, SPP RE_URE2's control room is manned 24/7 and has 24-hour visual security monitoring. | SPP RE_URE2 circulated a company-wide e-mail to all personnel reminding them of the need to follow the company procedures related to logging physical access to the PSPs. Furthermore, SPP RE_URE2 held training for employees regarding the procedures for entering and leaving its PSPs.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100242 | CIP-005-1 | R3.2 | TRE_URE1 self-reported that it failed to submit a technical feasibility exception (TFE) on a device CIP-005-1 R3.2 requirements. The device is not a Critical Cyber Assets (CCA) nor is it essential to the operation of any Cyber Assets. Previously, TRE_URE1 had filed a TFE for this device but for a different Standard. Therefore, Texas RE determined that the device is not a new device that was overlooked. The oversight occurred when filling out the TFEs because TRE_URE1 failed to file a TFE for this Standard. The mitigating measures put in place in accordance with the previously filed TFE for this device served as a mitigating measure during the period of this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the device is not a CCA nor is it essential to the operation of any Cyber Assets. Further, Texas RE determined that the risk was mitigated by the fact that during the pendency of this issue, there were no means to gain cyber access this device. Additionally, this device had been included in a previously filed TFE and all mitigating measures put in place in accordance with the previous TFE were also in place during the pendency of this issue. Furthermore, the device is always protected by the surrounding protective systems on the PSPs and ESPs. This device is inside an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). | Because the device was covered by a previous TFE, the mitigation measures put in place for the previous TFE also serve to mitigate the risk of this instance of noncompliance.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100269 | CIP-005-1 | R3.2 | TRE_URE1 self-reported that it failed to submit a technical feasibility exception (TFE) on a device. The device is not a Critical Cyber Assets (CCA) nor is it essential to the operation of any Cyber Assets. Previously, TRE_URE1 had filed a TFE for this device but for a different Standard and Texas RE approved the TFE. Therefore, Texas RE determined that the device is not a new device that was overlooked. The oversight occurred when filling out the TFEs because TRE_URE1 failed to file a TFE for this Standard. The mitigating measures put in place in accordance with the previously filed TFE for this device served as a mitigating measure during the period of this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the device is not a CCA nor is it essential to the operation of any Cyber Assets. Further, Texas RE determined that the risk was mitigated by the fact that during the pendency of this issue, there were no means to gain cyber access this device. Additionally, this device had been included in a previously filed TFE and all mitigating measures put in place in accordance with the previous TFE were also in place during the pendency of this issue. Furthermore, the device is always protected by the surrounding protective systems on the PSPs and ESPs. This device is inside an ESP and PSP. | Because the device was covered by a previous TFE, the mitigation measures put in place for the previous TFE also serve to mitigate the risk of this instance of noncompliance.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009765 | CIP-004-2 | R2 | During an Audit it was discovered that TRE_URE1 did not update its cyber security training program at least annually. TRE_URE1's annual training stated that updating of its cyber security incident response plan as per CIP 008-1 R1.4 is required within ninety calendar days of any changes made. However, when Version 2 of the CIP Standards became effective on April 1, 2010, TRE_URE1 failed to update its annual training materials that reference CIP 008-1 R1.4. TRE_URE1 failed to provide a reference to the new Version of the Standard- CIP-008-2 R1.4, which requires any changes to be made within thirty calendar days instead of 90 calendar days. As a result, TRE_URE1 included incorrect information into its training materials. This issue existed from April 1, 2010 to January 11, 2012. Furthermore, Texas RE found an additional remediated issue during the Compliance Audit. Seven TRE_URE1 contractors with access to Critical Cyber Assets (CCAs) were not trained as required by CIP-004-2 R2.3. However, TRE_URE1 failed to train them by that date and did not revoke their access until four days after training should have been completed. As a result, Texas RE determined that TRE_URE1 had a remediated issue with CIP-004-2 R2.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE1 employees were being trained with training material that did not fully reflect a change in the Reliability Standards Versions, the employees received a timely training on all other aspects of the Standard. Also, all trained employees at issue had Personnel Risk Assessment (PRAs) performed and were knowledgeable about TRE_URE1's CCAs' security practices. For sub requirements R2.3, the contractors having access to these CCAs had previously had cyber security training, and their PRAs were current. Therefore, Texas RE determined that these contractors were familiar with TRE_URE1's security practices. Finally, TRE_URE1 was noncompliant with R2.3 for a period of four days, which reduced the risk to the BPS to minimal. | To mitigate this issue TRE_URE1 has provided an updated training program document, which reflects the change from Version 1 to Version 2 of this CIP Standard. TRE_URE1 also trained the contractors at issue.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009766 | CIP-002-1 | R3 | During a Compliance Audit Texas RE discovered that TRE_URE1 did not develop a list of Critical Cyber Assets (CCAs) using the list of Critical Assets determined through an application of TRE_URE1's risk-based assessment methodology (RBAM). Specifically, Texas RE determined that one device was incorrectly excluded from the list of CCAs because TRE_URE1 failed to follow its RBAM for developing a list of CCAs. An inaccurate filtering criteria was assigned to the device that caused it to be marked as not being a CCA. However, TRE_URE1 was aware that the device was a CCA and afforded all the security measures required by the Reliability Standards to it. No other instances of incorrect filtering were discovered during the Compliance Audit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The CCA at issue was located inside a Physical Security Perimeter (PSP), was monitored by an electronic entrance, and was firewalled. In addition, the CCA was subject to staff oversight at TRE_URE1's Electronic Security Perimeters (ESPs) and the PSP, and it was accessible only to designated staff members with Personnel Risk Assessments (PRAs). Documents show that the CCA at issue was considered as part of the CCA list. The security of the CCA was not compromised during the three-month period of TRE_URE1's noncompliance. | To mitigate this issue TRE_URE1 has provided a CCA list document, showing that marketing PC1 been documented as a CCA. The document was signed by the Senior Manager.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009773 | CIP-008-2 | R1.4 | During a Compliance Audit, Texas RE discovered that TRE_URE1's Cyber Security Incident response plan (Versions 2009 and 2011) stated that changes to the plan are to be incorporated into the plan within 90 days, not within 30 days, as required by Version 2 of this Standard -CIP-008-2 R1.4. Version 1 of this Standard required that any change be incorporated within 90 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE determined that this remediated issue is documentation- related and administrative in nature because there were no changes to the plan during the period of noncompliance. Further, any changes to the plan would still have been incorporated within 90 days, thereby further reducing the risk to the BPS. | TRE_URE1 updated its Cyber Security Incident response plan, which is part of its training program, to require that any changes are incorporated within 30 days.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100155 | CIP-006-1 | R1.8 | TRE_URE2 self-reported noncompliance with CIP-006-1 R1.8. As part of the annual cyber vulnerability assessment (CVA), TRE_URE2 identified noncompliance. Texas RE determined that the system was not afforded the protective measured required by this Standards, a process to grant access was not used, not all accounts have been changed because the vendor has indicated that there may be negative impacts, the documented process for granting access to the device and associated hardware was not used to grant access, shared accounts that did not meet the password complexity and annual change frequency requirement, physical security monitoring alarm processes were not correctly followed by one employee per documented procedures, the devices were configured to enable all users with a network account to log on locally, employees were given system access to the badging servers prior to completion of background check, and responsibility for patch management for the badging servers was not defined or automated, and patches were not installed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2 badging servers are completely separate from TRE_URE2’s Supervisory Control and Data Acquisition (SCADA) and Distributed Control Systems (DCS). Exposure was limited by the fact that the devices were in Physical Security Perimeters (PSPs) with controlled access, essentially limiting access to only people with the appropriate Personnel Risk Assessment (PRAs). Texas RE determined that in the worst case scenario would result in TRE_URE2 PSP doors unlocking. Even if this occurred, TRE_URE2 facilities are protected 24/7. Also, the device quadruple (4X) is redundant. TRE_URE2's assessed the other security layers and determined that no actual intrusion or criminal activity occurred as a result of this failure to follow procedure. The servers had up to date monitored antivirus. | TRE_URE2 stated that the following mitigation activities have been completed: 1) CIP-005-3 R2: This was corrected and validated by TRE_URE2's gap analysis team. Access authorization documentation and procedures have been reviewed. 2) CIP-007-3 R5.1: Local logon service has been reduced to allow only personnel with a business need to logon to the system. 3) CIP-007-3 R3: device was updated with current security patches and verified by a vulnerability assessment scanning tool. Responsibility for patch installation has been clearly defined. 4) CIP-007-3 R5, R5.2, R5.3: The process has been documented and implemented. As a future improvement, all access control and verification will be performed with a single access control tool. Not all of the accounts have been changed because the vendor has indicated that there may be negative impacts. TRE_URE2 worked with the vendor to resolve this issue. 5) CIP-006-3 R5: The employee received corrective training to ensure documented procedures will be followed, along with monitoring of compliance for this specific physical security monitoring function.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100400 | CIP-005-1 | R1.5 | TRE_URE2 self-reported noncompliance with CIP-005-1 R1.5 for a failure to afford the protective measures specified in Standards CIP-007 R1 and R3 through R9. TRE_URE2 utilizes several applications and servers to administer firewalls, to provide logs, and to produce email alerts and reports for malicious activities for its Electronic Security Perimeter (ESP). As part of the CIP gap analysis, TRE_URE2 identified and self-reported noncompliance with CIP-005-1 R1.5 because it failed to afford all of the protective measures required by this Standard for two applications and two servers. The servers are physically located inside the PSP, but outside the Electronic Security Perimeter (ESP). For an application, TRE_URE2 failed to implement an acceptable use banner on one instance, the application did not log user activity, server access was not reviewed on annual basis, and three shared accounts did not identify and document individual users for the servers. For another application, TRE_URE2 identified three shared accounts with default passwords that allow access, and two of the accounts did not meet the password complexity requirement. TRE_URE2 failed to implement a patch management process for other servers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Remote access to the servers at issue is limited. The default account can only be accessed locally, within a protected physical area. Individuals that can logon to the microcontrollers have a current and valid Personnel Risk Assessment (PRA) and cyber security training. Interactive login was limited to specific workstations with static IP addresses. These workstations were assigned to employees who already had authorized access, and who had PRAs and had completed cyber security training. 2) The systems at issue are not directly accessible from the Internet, reside in a PSP with limited access, are physically and electronically segregated from TRE_URE2's Supervisory Control and Data Acquisition (SCADA) and Distributed Control Systems (DCS), and run anti-virus scans. No virus detections have occurred during the pendency of this remediated issue. | TRE_URE2 completed all mitigating activities related to this issue, including the following measures: 1) Acceptable use banners on the application and servers were installed; 2) Logging capability for the application and servers were enabled; 3) TRE_URE2 expanded its existing cyber security procedures; 4) The passwords complexities were identified on the accounts at issue; and 5) System patches and security updates were completed and verified by a vulnerability assessment scan.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012009733 | CIP-007-1 | R5.2 | TRE_URE2 self-reported an issue with CIP-007-1 R5.2 for a failure to implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factor default accounts. TRE_URE2 utilizes its Energy Management System (EMS) to monitor and control its Transmission Operator (TOP) area. The EMS has been identified as a Critical Cyber Asset (CCA) per TRE_URE2's methodology. As part of its CIP gap analysis, TRE_URE2 self-reported noncompliance with CIP-007-1 R5.2. For three shared accounts, TRE_URE2 could not demonstrate compliance, as specified in Requirement 5, with the documentation procedures required by its account management program. The policy requires identification of all computers with shared accounts. In addition, TRE_URE2 could not identify those individuals with access to one of the three shared accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The EMS system is located within the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). The system is only accessible to personnel with approved unescorted access to the Critical Cyber Asset. 2) TRE_URE2 demonstrated its password policy was compliant with the requirements of CIP-007-1 R5.3. TRE_URE2 implemented its policy for all three shared accounts . | The following mitigation activities have been completed: TRE_URE2 documented the computers with shared access implementing their policy to minimize and manage the use of shared account privileges.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012010289 | CIP-003-1 | R1.1 | During a Compliance Audit Texas RE found that TRE_URE3 was noncompliant with CIP-003-1 R1 because its cyber security policy failed to address the requirements in Standards CIP-002 through CIP-009. Texas RE determined that TRE_URE3 2009 and 2010 versions of its cyber security policy did not address the requirements in Standards CIP-002 through CIP-009, but its 2011 Version did address these Requirements. Specifically, TRE_URE3's policy presented failed to adequately address the following two requirements: CIP-007-2 R5 and CIP-003-2 R5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE3 was able to provide documentation on all other aspects of their NERC Cyber Security Policy document for 2010 and 2009 and the updated version for 2011 addressed the requirements of this Standard. Texas RE determined that the risk was mitigated by the fact that TRE_URE3 had a policy prior to the mandatory compliance date. TRE_URE3's Cyber Security Plan has been in place for years, annually reviewed, updated according to TRE_URE3's internal document control procedures, and adequately addressed the vast majority of the requirements in Standards CIP-002-2 thorough CIP-009-2. TRE_URE3's policies did not contain low-level, specific details and requirements related to the implementation of the policy. However, these details were contained in other processes and procedures that supported compliance with the security policy | The updated policy addresses each applicable CIP standard and requirement. Under each requirement there is a brief description of how TRE_URE3 meets that requirement. The updated policy mitigates this remediated issue.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010304 | CIP-007-1 | R4 | WECC_URE1, as a Balancing Authority, Generator Operator, Generator Owner, Load Serving Entity, Transmission Operator, Transmission Owner, and Transmission Service Provider, self-reported an issue with of CIP-007-1 R4. A WECC Subject Matter Expert (SME) contacted WECC_URE1 to discuss its Self-Report. According to the WECC SME, WECC_URE1 stated that for five devices it failed to use anti-virus software and other malicious software prevention tools. WECC_URE1 also stated that it is technically infeasible to use anti-virus or anti-malware software on these devices and intended to file a Technical Feasibility Exception (TFE). The WECC SME concluded that WECC_URE1 had an issue with CIP-007-1 R4 and referred the matter to Enforcement. Enforcement determined that WECC_URE1 had an issue with CIP-007-1 R4 because it neither installed anti-virus or anti-malware software on the CCAs described above, nor did WECC_URE1 file TFEs for the devices involved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because The CCAs are devices used as a communication link for managing serially connected devices. As compensating measures, the devices are located in an Electronic Security Perimeter and have technical and procedural mechanisms for control of electronic access at all access points. WECC_URE1 enabled only those ports and services necessary at the access points and required username and passwords to access the devices. Also, all devices are located within a Physical Security Perimeter with procedural controls to manage physical access, including 24/7 logging and monitoring of physical access. Additionally, if the devices were to lose connectivity, alarms alert staff. WECC_URE1 filed TFEs for the devices because it was technically infeasible to install anti-virus and anti-malware software on the devices. WECC approved the TFEs. | WECC_URE1 completed mitigation of this issue.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010965 | CIP-006-3c | R2.2 | WECC_URE2, as a Balancing Authority, Generator Operator, Load Serving Entity, Transmission Operator, Transmission Owner, and Transmission Service Provider, self-reported an issue with CIP-006-3c R2.2. WECC_URE2 reported that it failed to file Technical Feasibility Exceptions (TFE) for two Critical Cyber Assets (CCAs) that authorize and/or log physical access to a Physical Security Perimeter (PSP). WECC Subject Matter Experts (SMEs) reviewed WECC_URE2’s Self-Report and TFE requests. SMEs determined it is technically infeasible for WECC_URE2 to install anti-virus software on the two devices. WECC Enforcement reviewed WECC_URE2’s Self-Report, the SMEs’ findings, and TFE approvals and determined that WECC_URE2 failed to submit a TFE as required under CIP-007-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE2 had compensating measures in place to secure the devices against misuse or malicious attack. CIP-006-3 R2.2 requires entities to afford these devices protections specified in twenty-four Standard Requirements. In this case, WECC_URE2 failed to afford two devices one protection specified in CIP-007-3 R4. Specifically, WECC_URE2 failed to file TFEs for two devices on which it was technically infeasible to implement anti-virus software. WECC_URE2 secured both devices within an Electronic Security Perimeter (ESP). Electronic access was logged and monitored. Individuals with electronic access completed Personnel Risk Assessments (PRAs) and cyber security training. WECC_URE2 controlled access to the ESP with restricted user accounts, passwords, intrusion detection, and alarms. WECC_URE2 installed alarms to alert personnel of unauthorized physical access to the Physical Security Perimeter. WECC_URE2 secured the devices within a facility to which access was controlled and monitored. Individuals with physical access to the devices completed PRAs. WECC_URE2 enabled only necessary ports and services on both devices. | WECC_URE2 completed mitigation of this issue.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010468 | CIP-002-3 | R1 | During a compliance audit WECC determined that WECC_URE3 had an issue with CIP-002-3 R1. WECC discovered that WECC_URE3 implemented a revised version of its risk-based assessment methodology (RBAM). Although the document contained procedures and evaluation criteria, it failed to contain a risk-based assessment component. The WECC Audit Team referred its finding to the WECC Enforcement (Enforcement). Enforcement reviewed the Audit Team’s findings and determined that WECC_URE3 had an issue with CIP-002-3 R1, because it failed to identify and document an RBAM to identify its Critical Assets (CAs) and Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE3 does not have CAs and does not have CCAs. As compensating measures, WECC_URE3’s previous applications of its RBAMs generated null lists of CAs and CCAs. The WECC Audit Team determined that the existing null lists were accurate. | WECC_URE3 completed mitigation of the issue. WECC_URE3 proposed to revise its RBAM to document the risk-based component in detail. WECC_URE3 evaluated its Cyber Assets through an application of the updated RBAM to determine WECC_URE3’s CAs. This process yielded a null set of Critical Assets for WECC_URE3.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010763 | CIP-003-1 | R1 | WECC_URE4 self-certified an issue with CIP-003-1 R1.3. A WECC Subject Matter Expert (SME) discussed with WECC_URE4 its self-certification. WECC_URE4 stated that it did not annually review its entire cyber security policy in the calendar year. Specifically, WECC_URE4 did not review cyber security policies that were outdated and not used by WECC_URE4. The WECC SME concluded that WECC_URE4 had an issue with CIP-003-1 R1.3 and referred the matter to WECC Enforcement. WECC Enforcement determined that WECC_URE4 had an issue with CIP-003-1 R1.3 because it did not perform a complete annual review of its cyber security policy for the calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the cyber security policies were outdated and not used by WECC_URE4. As compensating measures, WECC_URE4 stated that it did annual reviews and approved the current policies in use. WECC_URE4 did a full review of the cyber security policy in other calendar years. | WECC_URE4 completed mitigation of this issue. WECC_URE4 reviewed its cyber security policy in calendar year and removed the outdated items.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010765 | CIP-006-3c | R1 | WECC_URE4 self-certified an issue with CIP-006-3c R1. A WECC SME contacted WECC_URE4 to discuss its self-certification. WECC_URE4 stated that one of its employees gained access to one of its Physical Security Perimeters (PSP) without having authorized access to the PSP. The employee involved accessed the PSP by walking through a door opened by another employee who had authorized access to the PSP. After the employee involved gained access to the PSP, alarms activated and the employee contacted WECC_URE4’s security guards from a phone located next to the PSP door. Security instructed the employee to leave the PSP, which the employee did. The employee was inside the PSP for approximately one minute and did not access any Critical Cyber Assets (CCAs). The WECC SME concluded that WECC_URE4 had an issue with CIP-006-3c R1 and referred the matter to WECC Enforcement. WECC Enforcement reviewed the WECC SME’s findings and the WECC_URE4 self-certification. Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the employees immediately contacted WECC_URE4’s security guards and left the PSP without accessing any CCAs. As compensating measures, WECC_URE4 monitored the PSP 24 hours per day and each PSP access point has an alarm to alert of unauthorized physical access. In addition, WECC_URE4 staffs security at the facility 24/7. WECC_URE4’s procedures for monitoring for unauthorized access proved effective as an alarm sounded, the employee immediately contacted WECC_URE4 security, and security instructed the employee to leave the PSP. | WECC_URE4 completed mitigation of this issue. WECC_URE4 remediated this issue when the employee who gained unauthorized access to the PSP left the PSP. WECC_URE4 trained personnel to instruct individuals who enter a WECC_URE4 PSP without an escort to immediately leave the PSP
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012010361 | CIP-004-3 | R3 | WECC_URE5 self-reported a an issue with CIP-004-3 R3. According to the Self-Report, one of WECC_URE5 employees had physical access to the a WECC_URE5 Physical Security Perimeter (PSP) for a period of 43 days after his personnel risk assessment (PRA) had expired. WECC determined that WECC_URE5 had an issue of CIP-004-3 R3 for failing to have an updated PRA for one of its employees. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because all Critical Cyber Assets (CCAs) reside within an identified PSP and Electronic Security Perimeter. Therefore, the CCAs were monitored and afforded the protections of CIP-005 and CIP-006. In addition, the employee involved had CIP-004 R2 training and is in good standing with WECC_URE5. | WECC_URE5 submitted a mitigation plan to address this issue. WECC approved the mitigation plan and certified its completion.