## Public CIP Feb. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010874 | CIP-004-3 | R4; R4.1 | NPCC_URE1 self-reported an issue with CIP-004-3 R4.1. NPCC_URE1 failed to update its list of personnel with authorized cyber access to Critical Cyber Assets (CCAs) within seven calendar days. NPCC_URE1 was informed by a vendor that one of its personnel with authorized cyber access to CCAs was no longer employed by the vendor. The employee had voluntarily resigned his position 32 days earlier and the vendor immediately revoked cyber access to all of NPCC_URE1’s CCAs for the individual on the date of his termination. Because the vendor did not inform NPCC_URE1 of the employee's access revocation until 32 days had passed, NPCC_URE1's list was not updated within seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A personnel risk assessment (PRA) had been completed on the individual at issue prior to his being granted access to NPCC_URE1’s CCAs. The PRA was still valid at the time of his resignation. The individual had also completed annual cybersecurity training, as required by NPCC_URE1’s cybersecurity training program. The individual was never issued an identification card or access card by NPCC_URE1. This individual was never granted unescorted physical access to NPCC_URE1’s CCAs. After the employee resigned, the vendor revoked all electronic access to NPCC_URE1 Cyber Assets. NPCC_URE1 has inspected the electronic access logs for NPCC_URE1’s Electronic Security Perimeter and verified that the individual did not access any of NPCC_URE1’s CCAs after the date of termination of his employment. | To mitigate this issue, NPCC_URE1 updated its protected cyber system access list to accurately reflect the status of all applicable personnel. NPCC_URE1 now requires that vendors and contractors notify NPCC_URE1 within 24 hours when the employment status changes for an individual with unescorted physical access or cyber access to NPCC_URE1’s protected Cyber Assets. NPCC_URE1 updated its CIP annual training for vendors and NPCC_URE1 managers to include the review of specific requirements for removal of access and updating of access lists at the time of termination. NPCC_URE1 also revised the PRA section of its contract service agreements to include provisions requiring the vendor to notify NPCC_URE1 within 24 hours when unescorted physical access or cyber access is no longer required or the vendor terminates an employee. Lastly, NPCC_URE1 verified that applicable vendors have procedures to notify NPCC_URE1 within 24 hours when an applicable employee is terminated or there is a relevant change in the employee's status.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010753 | CIP-004-1 | R3 | RFC_URE1 self-reported an issue with CIP-004-1 R3 to ReliabilityFirst. RFC_URE1 identified the issue as relating to CIP-006-1 R1.8. ReliabilityFirst subsequently determined that the facts and circumstances constituted an issue with CIP-004-1 R3. RFC_URE1 contracted with a consultant to conduct an annual review of its personnel risk assessment (PRA) program. As a result of that review, RFC_URE1 discovered three instances where it granted its employees authorized cyber access to Critical Cyber Assets without conducting a timely PRA. For two of the employees, RFC_URE1 granted cyber access before it completed the respective PRAs 10 months and 14 months later. For the third employee, RFC_URE1 granted cyber access seven days before the employee completed the PRA. In its Self-Report, RFC_URE1 identified seven additional instances where it granted cyber access to an employee prior to conducting a PRA. ReliabilityFirst determined, however, that these instances were not possible violations because CIP-004-1 R3 was in effect during the time period, which required RFC_URE1 to conduct a PRA within 30 days of granting cyber access. For the seven instances, RFC_URE1 conducted the PRA within 30 days of granting cyber access. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). A violation of CIP-004 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for unknown, unverified, or criminal individuals to access Critical Cyber Assets (CCAs), which could result in harm to the integrity of the CCAs. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. The individuals at issue were part of one of the following two user groups: service dispatchers and IT support. First, the service dispatchers have read-only access to the energy control system in a distribution operator capacity due to RFC_URE1’s use of the energy control system for distribution in addition to transmission. Second, the IT support personnel had cyber access to workstations that are physical access control system assets where the IT support personnel only had operating system access and not application access. Operating system access allows the user to modify only the underlying operating system including device drivers and add or upgrade applications as required for support of corporate services. These individuals had no rights to the physical access control system and could not modify any access rights or privileges within that system. Application access requires an additional level of authentication that these individuals did not have. | To mitigate the issue, RFC_URE1: 1) reviewed the status of all individuals with authorized cyber or authorized unescorted physical access to CCAs; 2) verified that all individuals have current PRAs within seven years; 3) revised its procedures to review the daily report of employee change records to ensure appropriate access grants; and 4) revised its PRA verification procedures to ensure it conducts PRAs prior to granting access.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011578 | CIP-005-1 | R1; R1.6 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 did not maintain its documentation pursuant to CIP-005-1 R1.6. Specifically, RFC_URE2 did not synchronize all Electronic Security Perimeter (ESP) related documentation, did not document all Cyber Assets, did not clearly mark all electronic access points to the ESP, and did not categorize Cyber Assets as Critical Cyber Assets or access points. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. During Compliance Audit, ReliabilityFirst confirmed during a site visit that, although documentation was lacking, RFC_URE2 was properly protecting all of its Cyber Assets within an Electronic Security Perimeter and Physical Security Perimeter. | To mitigate the issue, RFC_URE2: 1) synchronized its documentation related to its ESP; 2) included and properly categorized all Cyber Assets; and 3) ensured its documentation clearly marked electronic access points to the ESP.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011579 | CIP-007-1 | R1; R1.3 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 did not document all test results for all change requests, as required by CIP-007-1 R1.3. RFC_URE2 uses a test script worksheet to process all change requests. ReliabilityFirst discovered several instances in which RFC_URE2 did not complete, or only partially completed, test scripts for change requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. This issue was a documentation error because, although RFC_URE2 did not fully document the test results, RFC_URE2 was able to demonstrate that it followed and successfully completed each step listed on its test script worksheet for all change requests. | To mitigate the issue, RFC_URE2 reinforced the requirement that test scripts must be completed for every change request and includes instructions on its test scripts stating, “a Pass or Fail must be entered on every step before form can be closed.”
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011580 | CIP-007-1 | R3 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 had an issue with CIP-007-1 R3 as it did not document that it assessed security patches and security upgrades within 30 calendar days of availability. ReliabilityFirst also determined RFC_URE2 did not document the compensating measures it applied to mitigate risk exposure for those patches it did not install. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. During the Compliance Audit RFC_URE2 provided ReliabilityFirst with evidence demonstrating that it kept all its Cyber Assets up to date with the latest available patches even though RFC_URE2 did not document that it assessed security patches and security upgrades within 30 calendar days of availability. | To mitigate the issue, RFC_URE2 updated its security patch management procedure to help ensure it documents its assessment of security patches within 30 calendar days and documents the compensating measures it applies for those patches it does not install.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011581 | CIP-007-1 | R6; R6.5 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 had an issue with CIP-007-1 R6.5 as it could not provide documentation that demonstrated it reviewed its system event logs. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. RFC_URE2 had system event logs, but it did not document its review of those logs. RFC_URE2 reviewed the logs but was unable to demonstrate its review of the logs. Additionally, the risk was mitigated by the fact that RFC_URE2’s network is a closed network with no access to the Internet. Furthermore, RFC_URE2 generates alerts from its access points of events that could pose potential risk to the BPS. | To mitigate the issue, RFC_URE2 revised its monitoring and logging procedure to ensure that RFC_URE2 reviews and maintains records documenting the review of logs of system events related to cybersecurity at least quarterly.
ReliabilityFirst Corporation (ReliabilityFirst); Texas Reliability Entity, Inc. (Texas RE); Southwest Power Pool Regional Entity (SPP RE) (collectively, the Regional Entities) | Unidentified Registered Entity 3 (RFC_URE3, TRE_URE3, SPP RE_URE3) (Collectively, URE_3) | NCRXXXXX | RFC2012009909 TRE2012009940 SPP2012009918 | CIP-004-3 | R4 | This issue involved four incidents of noncompliance with CIP-004-3 R4 by URE_3: 1) URE3 self-reported an issue with CIP-004-3 R4 to three Regional Entities. A contractor in URE3's workplace services department, who had authorized unescorted physical access to Critical Cyber Assets (CCAs), resigned and no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days as required by the Standard, and revoked the employee’s access 30 days later; 2) URE_3 submitted a Self-Report to three Regional Entities identifying an issue with CIP-004-3 R4. The Self-Report identified one common instance of an issue among the Regional Entites and one additional instance unique only to SPP RE. Subsequently, URE_3 submitted evidence demonstrating that it did not in fact have an issue with CIP-004-3 R4 with respect to the common instance. As a result, the Regional Entities did not pursue this issue. However, the instance unique only to SPP RE was a non-compliant issue. URE3 submitted a Self-Report to SPP RE identifying an issue with CIP-004-3 R4. A building maintenance technician who had physical access to a Physical Security Perimeter resigned and no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days, and revoked the employee’s access nine days later; 3) URE_3's submitted Self-Reports to the Regional Entities identifying an issue with CIP-004-3 R4. An URE_3 employee within an operations business unit who had authorized cyber access to certain generation control supervisory control and data acquisition system CCAs no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days, and revoked the employee’s access 36 days later; and 4) URE_3 submitted Self-Reports to the Regional Entities identifying an issue with CIP-004-3 R4. An information technology service desk contractor who had authorized cyber access to CCAs no longer required such access. URE_3 failed to revoke the contractor’s access within seven calendar days and revoked the contractor’s access 18 days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-004 R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for personnel that a responsible entity determined should no longer have access to CCAs, with potential access to CCAs. Such continued access could result in harm to the integrity of the CCAs or the reliability of the BPS as a result of actions by an individual who should no longer have physical or electronic access to CCAs. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. URE_3 discovered these instances of noncompliance due to its internal controls when it performed its routine quarterly reviews of employees and contract employees. In each instance, URE_3 revoked access almost immediately after discovering it had not revoked access, and, in each instance, URE_3 discovered the issue no later than one month after access revocation was required. In addition, all of the employees and contractors in each instance were not terminated for cause and resigned except for one employee, whose manager determined that access was no longer required to perform the job function. Furthermore, the individuals who had physical access no longer had their physical access badges, reducing the likelihood the individuals could gain access to the Physical Security Perimeter. One individual did not have physical access at the time of resignation, and URE_3 collected that individual’s secure identification token at the time of resignation thereby preventing remote access. | To mitigate the issue, URE_3: 1) revoked the individuals’ access rights; 2) identified, developed, and made available awareness and training for managers who have NERC CIP contractors or employees; 3) sent a letter to managers summarizing termination responsibilities; 4) developed a pending revocation report to show all outstanding electronic access revocation requests; and 5) made appropriate clarifications on the form utilized to begin the process of terminating an individual’s electronic access.
ReliabilityFirst Corporation (ReliabilityFirst); Texas Reliability Entity, Inc. (Texas RE); Southwest Power Pool Regional Entity (SPP RE) (collectively, the Regional Entities) | Unidentified Registered Entity 3 (RFC_URE3, TRE_URE3, SPP RE_URE3) (Collectively, URE_3) | NCRXXXXX | RFC2012001311 TRE2012009732 SPP2012009559 | CIP-006-3c | R1; R1.4; R1.6 | URE3 submitted respective Self-Reports to SPP RE, Texas RE, and ReliabilityFirst identifying an issue with CIP-006-3c R1.4. An URE_3 information technology (IT) employee without authorized unescorted physical access entered a Physical Security Perimeter (PSP) by tailgating through a door. The URE_3 IT employee entered the lobby adjoining the PSP. At 13:47, an URE_3 operations employee with authorized unescorted physical access exited the PSP door, and at the same time, the URE_3 IT employee exited the elevator and walked quickly toward the PSP door, grabbing the door handle just before the door closed and locked. The URE_3 IT employee pulled the door open, walked through it, and wandered around the floor before asking for assistance from an administrative assistant. The URE_3 IT employee was escorted to the electronic logging system, received a badge, and was checked in and out as a visitor. 9 minutes later, the URE_3 IT employee was escorted out of the area. URE_3 submitted Self-Reports to ReliabilityFirst and SPP RE identifying an issue with CIP-006-3c R1.6 which stemmed from three instances of noncompliance. First, an instance occurred that impacted ReliabilityFirst and SPP RE. URE_3 staff visited the an URE3 engineer for area development discussion. The discussion occurred in an URE_3 meeting room. During the meeting, the engineer briefly exited the meeting room for 15 to 20 seconds to go to the printer. The visitors remained in the room during this unescorted period because the meeting room, which is located down the hall from the printer, is visible from the printer area and the individual was only outside of the room for a few seconds to retrieve a printout. Second, an instance occurred that impacted ReliabilityFirst and SPP RE. A security guard escorted a vending machine repairman into control center kitchen to repair a vending machine. At an unknown point, the security guard left the repairman alone in the kitchen without transferring escort responsibility to control center personnel. The repairman remained in the kitchen until requesting the control center personnel to let the repairman exit the kitchen. The control center operator escorted the repairman to the main entrance of the control center where the security guard met them and resumed escort out of the center. Third, an instance occurred that impacted SPP RE only. URE_3 received an alarm indicating that a door was forced open at a supervisory control and data acquisition (SCADA) Computer Room main door. The operations center called the room and an URE_3 electrician answered the phone. The electrician reported that when he entered the room, he set the alarm off, and he could not exit the room. The operations center discovered that the electrician did not have the correct access for this room and opened the door for the electrician so he could exit the room. The operations center relocked the door once the electrician exited the room, and asked the electrician to pull on the door to ensure that it was locked. URE_3 conducted a follow-up investigation and discovered that the door magnetic lock was not fully engaged, but the door locks met close enough to show that the door was closed. Furthermore, URE_3 discovered that it had revoked the electrician’s access to that room during quarterly access reviews when the electrician was on a leave of absence. The electrician still maintains authorized unescorted physical access to other areas. URE_3 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-006-3c R1.6. An URE_3 wireman had visitors at a substation in order to pull new cables into the substation. The wireman called the security department to request the ability to prop a door open at the substation in order to install the new cable runs in the substation. The security department granted the request and advised the wireman to swipe his badge each time he entered and exited the control house at the substation, and sign the visitors in and out each time they entered and exited the control house. The security department advised the wireman to call the security department every time the visitors entered and exited the control house as well and that the wireman should not leave the visitors unescorted in the control house. The security department received a door prop alarm from a door at the substation, as expected. A few hours later, the security department ran a badge analysis history for the wireman because the door had been propped open for several hours, and the security department had received no calls. Two hours later, the security department manager advised the security department to call the control house, at which time the wireman said that the visitors were still onsite and, at one point, the wireman went to his van leaving the visitors unescorted. As a result, URE_3 failed to provide these visitors with a continuous escort. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-006-3c R1 has the potential to affect the reliable operation of the BPS by providing the opportunity to physically access Cyber Assets that are not protected by the implementation of a physical security plan. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. The issue occurred for a short duration prior to the URE_3 IT employee being logged in and escorted. In addition, at no time was the URE_3 IT employee in proximity to Critical Cyber Assets (CCAs) without an escort. Authorized personnel were in close proximity to the CCAs and would likely have resisted any unauthorized attempts at physical access. All of the escorting employees at issue remain employees of URE_3 who are trusted with authorized unescorted physical access. Regarding the instance where URE3 left meeting attendees unescorted for 15 to 20 seconds, the meeting room has no CCAs and there are multiple layers of security access control devices between the meeting room and the CCAs including a biometric reader, proxy card reader, and man-trap doors. In addition, the engineer attested that the visitors remained in the meeting room during the unescorted period. The visitors remained in the room during this unescorted period because the meeting room, which is located down the hall from the printer, is visible from the printer area and the individual was only outside of the room for a few seconds to retrieve a printout. Regarding the instance with the vending machine repairman, there are no CCAs in the kitchen. The CCA area is isolated and far away from the kitchen. There were six operators on duty in the CCA area during the unescorted period and no one saw the repairman leave the kitchen area until he was finished with the repairs. Regarding the instance with the electrician, the electrician had a valid personnel risk assessment and cybersecurity training. Until his leave of absence, he had authorized unescorted physical access to the computer room. CCAs are protected by username and password, and the Electronic Security Perimeter is protected by an access control list that verifies access rights. URE_3 had not assigned contractors usernames and passwords, so they could not access the CCAs. | URE_3 submitted to ReliabilityFirst a Mitigation Plan to address the issue with CIP-006-3c R1.4. URE_3 enhanced its physical barriers by installing keycard restrictions in the elevators through which the tailgater entered, requiring the use of a building badge for the elevator to stop at the lobby, and modifying the door to ensure it closes more quickly. In addition, URE_3 improved signage at the relevant location by performing an assessment of the existing signage and create and implement a strategy for enhancing existing signage. Furthermore, URE_3 provided additional training for personnel who have authorized unescorted physical access to the relevant PSP on the responsibilities of having such access, including ensuring that doors close securely during ingress and egress and monitoring the activities of individuals in the lobbies outside the PSP to prevent tailgating. URE_3 submitted to ReliabilityFirst a Mitigation Plan to address the issue with CIP-006-3c R1.6. URE_3 revised its communication and operation procedures to minimize human error including security awareness training, signage regarding visitors, minimizing visitors to the control center during off-business hours, and reminding escorts and visitors of the CIP requirements upon sign in. In addition, URE_3 reconfigured the operations center to remove the office area meeting room from the PSP, updated the operations center visitor check-in process, and repaired the SCADA room security door.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010100 | CIP-006-3c | R1; R1.1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-006-3c R1.1. While conducting annual preventative maintenance on its security system, RFC_URE3 discovered approximately seven 22 by 12 inch holes with cables running through them above the main door to a telecom room. Two weeks later, RFC_URE3 repaired the holes. RFC_URE3 identified an addition instance of CIP-006-3c R1 in ReliabilityFirst. At a supervisory control and data acquisition (SCADA) computer room Physical Security Perimeter (PSP), RFC_URE3 discovered several instances where there was a 25 to 35 inch gap between the top of the walls and the concrete roof support. 2 weeks later, RFC_URE3 repaired the holes. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated because there are additional layers of security that one would have to penetrate to enter the PSP. The PSP is located in a small room within a larger room that has a separate door with a keypad lock. The holes did not lead outside the larger room. The SCADA computer room is located inside a building perimeter with partial fencing, and is secured with locks and card readers. | RFC_URE3 submitted to ReliabilityFirst a Mitigation Plan to address the first instance of the issue with CIP-006-3c R1.1. RFC_URE3 patched the gaps in the six-wall border and updated its physical security site survey checklist to remind services to: inspect rooms for potential gaps in the six-wall border; have workplace services and/or physical security personnel inspect all PSPs for any gaps in the six-wall border; review and inspect questionable gaps; and remediate any gaps discovered.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012001312 | CIP-006-3c | R5 | RFC_URE3 self-reported an issue with CIP-006-3c R5 to ReliabilityFirst. The station manager for a substation reported an issue to the security department. The station crew had permission to prop open the CIP station control building door while pulling in new control cables. At some point during their work, the crew began searching for materials in the station yard and left the control building unattended with the doors propped open for approximately 20 minutes. The station superintendent brought this to the crew’s attention and reported the issue to the security deparment. RFC_URE3 failed to monitor these physical access point during that time period. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-006 R5 has the potential to affect the reliable operation of the BPS by providing the opportunity to access the Physical Security Perimeter as failure to comply with the Standard means there are inadequate technical and procedural controls to monitor physical access points. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. RFC_URE3’s station manager identified this issue and reported it immediately as a CIP issue to the security department, illustrating that RFC_URE3’s internal controls caused RFC_URE3 to discover this issue. No unauthorized personnel were in the control house at the time the station superintendent re-entered it. The Critical Cyber Asset devices are protected by access control lists and require usernames and passwords in order to access the devices. In addition, the contractors were working outside in the yard approximately 1,000 feet from the control house. A supervisor was onsite and none of the contractors entered the building. | To mitigate the issue, RFC_URE3: 1) held a meeting with the associated station manager to discuss the mitigation options; 2) held a staff meeting with the department to review the CIP procedures for propping doors open for work; 3) developed a discussion training guide to reinforce the policy and expected conduct; 4) sent out an email reminder with the previous documents and summary; and 5) implemented a reminder script from the security department on the door prop open request for the security department to read to the station staff requesting the door prop.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011126 | CIP-002-1 | R2 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined that RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-1 R1. Therefore, RFC_URE4 could not demonstrate that it applied its RBAM annually to develop a list of Critical Assets pursuant to CIP-002-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011127 | CIP-002-1 | R4 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-3 R1. Therefore, RFC_URE4 could not demonstrate that it annually approved its RBAM pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011128 | CIP-003-3 | R2; R2.2 | During a Compliance Audit. ReliabilityFirst determined that RFC_URE4 could not provide evidence that it documented a change to its senior manager designation within 30 calendar days of the effective date. Specifically, although RFC_URE4 appointed its plant manager as the senior manager for implementation of, and adherence to, the CIP Reliability Standards, RFC_URE4 failed to document this change within 30 calendar days. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this was a documentation error. It was a documentation error because RFC_URE4 did appoint a senior CIP manager who functioned in that capacity throughout the duration of the issue. RFC_URE4 just neglected to document the change. | To mitigate the issue, RFC_URE4 appointed a senior manager and documented the change.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011129 | CIP-002-1 | R1 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined that RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-3 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900651 | CIP-004-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R2.1 because it had failed to establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCA). SERC_URE1 learned that a contractor for SERC_URE1’s agent had access to CCAs for support and maintenance purposes but was unaware of specific CIP-004 requirements. While the contractor’s firm maintained some cyber security training and awareness, these internal efforts did not cover specific entity policies and access controls, proper use of CCAs, proper handling of CCA information, plans to recover or re-establish CCAs, or documentation of training conducted. It was determined that SERC_URE1 did not have adequate procedures to monitor and ensure CIP-004 R2 compliance of personnel with access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The untrained contractor only provided technical support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented a cyber security training program that covered all aspects of CIP-004 R2.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900652 | CIP-004-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R3 because it failed to have a documented personnel risk assessment (PRA) program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). SERC_URE1 learned that a contractor for SERC_URE1’s agent had access to Critical Cyber Assets (CCAs) for support and maintenance purposes but was unaware of specific CIP-004 requirements. While the contractor’s firm performed some pre-employment background checks, these internal efforts did not meet the level required by CIP-004-1 R3. It was determined that SERC_URE1 did not have a PRA program that sufficiently addressed contractor personnel with access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The contractor only provided support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented a PRA program for contractors with access to CCAs.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900653 | CIP-004-1 | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R4 because it failed to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. SERC_URE1 learned that a contractor for SERC_URE1's agent had access to CCAs for support and maintenance purposes but was unaware of specific CIP-004 requirements. It was determined that SERC_URE1 did not include the contractor on its list of personnel with authorized cyber or authorized unescorted physical access to CCAs, including his or her specific electronic and physical access rights to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The contractor only provided support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented an automated process for tracking contractors and employees with authorized cyber or unescorted physical access to CCAs.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900654 | CIP-004-1 | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R4 because it failed to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCA), including their specific electronic and physical access rights to CCAs. It was found that 19 employees of SERC_URE1’s agent who had access to CCAs were reassigned and were not removed from the list within the allowed seven day revocation period for employees who no longer need access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the missed individuals had valid and current personnel risk assessments and CIP cyber security training. | To mitigate this issue, SERC_URE1's agent implemented an automated process for tracking contractors and employees with authorized cyber or unescorted physical access to CCAs. This automated process also includes features that enable the removal of access within the timeframes specified by CIP-004 R4 .
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900655 | CIP-005-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-005-1 R2 because the firewall of SERC_URE1’s agent was inadvertently configured to the “any-any” access rule, and was not set-up to deny access by default. It was determined that the firewall that formed the Electronic Security Perimeter (ESP) was installed prior to the date of mandatory compliance by SERC_URE1's agent and had a default access rule used for testing and trouble-shooting the pre-production system that was left intact once the system went into production. Pursuant to SERC_URE1 agent’s ESP procedure, this rule should have been removed prior to the mandatory and effective date of CIP-005-1 R2; however, this rule replacement did not occur. During an evaluation of the ESP, SERC_URE1's agent discovered the overly permissive “any-any” access rule and initiated an internal investigation of all other ESP firewalls. SERC_URE1 agent’s investigation concluded and SERC_URE1's agent removed the “any-any” rule and replaced it with a more stringent rule that denies access by default on this ESP firewall. No other instances of the permissive “any-any” rule were found on any ESP forming firewalls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's agent had a corporate firewall that had a deny-by-default access setting that had to be traversed in order to reach the ESP firewall. Only employees that had met the training and screening requirements of CIP-004 were allowed access through the corporate firewall, which is outside the ESP firewall. | To mitigate this issue, SERC_URE1's agent: 1) removed the non-compliant firewall and installed a CIP-005 R2 compliant firewall in its place; 2) determined if there were any other production ESP firewalls not in compliance with CIP-005 R2; 3) revised its procedures for ESP firewalls; and 4) notified SERC_URE1 that it completed training for the SERC_URE1 agent's employees working on CIP-005 R2.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000660 | CIP-003-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R3 because it had been unable to perform personnel risk assessments (PRAs) on some of the individuals with access to Critical Cyber Assets (CCAs) due to a collective bargaining agreement (CBA) issue. Because of this, SERC_URE1 should have taken an exception to its cyber security policy (CSP), but it failed to do so. It was determined that, as of the date of mandatory compliance, SERC_URE1’s agent had implemented a CSP but had not taken an exception to the CSP on the issue of PRAs for its union employees. SERC_URE1 agent’s management realized that the CBA with its union employees did not allow for the performance of the PRA for those employees, and recognized this issue required an exception to the CSP that was never sought. SERC_URE1's agent obtained the authority to conduct PRAs on represented employees with access to CCAs. All required PRAs for the union employees were completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The exception to the CSP was only necessary because of a CBA that prevented the performance of PRAs for union employees. CIP-004 R3 explicitly notes that the requirement to perform PRAs for personnel with authorized access to CCAs is subject to existing collective bargaining unit agreements. | To mitigate this issue, SERC_URE1's agent completed all PRAs for union employees with access to CCAs.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000661 | CIP-006-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-006-1 R1 because it had not considered the application that monitors and controls the physical access to Physical Security Perimeters (PSPs) as a Cyber Asset, and all employees who used the system did not have valid personnel risk assessments (PRAs). It was determined that the subject of this Self-Report was a physical access control system (PACS) that managed physical access to Critical Cyber Assets (CCAs) and other secure areas not covered by the CIP standards. The PACS system was designed and segmented by permissions, so employees that managed PSPs were required to have PRAs and employees and contractors who managed non-CIP secure areas were not required to have PRAs since they could not access, manage, or control the PSPs. As understanding and knowledge of the CIP requirements regarding PACS increased, SERC_URE1 became aware that all employees with access to the PACS system should have valid PRAs and training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PACS system was set-up and segmented to prevent non-CIP users from being able to access the CIP designated PSPs. The PACS system is not directly tied to the Energy Management System. | To mitigate this issue, SERC_URE1's agent: 1) assembled a list of all personnel who had access to the security application that monitors and controls physical access to PSPs and processed PRAs for these employees and notified the manager upon completion of the PRAs; 2) determined if any other Cyber Assets or CCAs were not protected at the access point similar to the security application and reported its findings; 3) modified its cyber security policy and associated procedures to ensure that it is clear that all Cyber Assets and CCAs are protected at the access point; 4) modified its cyber security policy and associated procedures to require PRAs prior to granting an employee or contractor access to a Cyber Assets subject to CIP-006 R1.8; 5) trained all personnel, as applicable, on the revised procedures developed in items 3 and 4 above; and 6) revoked the access of any personnel who did not pass the PRA.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000662 | CIP-007-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R1.1 because the test procedures did not specifically call out for tests of cyber security controls, but were instead focused on application and functional testing. It was determined that the test procedure did not address adverse effects to the production environment and were focused solely on application and functionality testing instead of also including specific instructions for testing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's agent addressed cyber security controls in its initial designs, and its change request process required a design document review in which security controls would be reviewed. Only documented and allowed traffic from outside the Electronic Security Perimeter (ESP) is permitted into the ESP. | To mitigate this issue, SERC_URE1's agent: 1) modified its testing procedures to explicitly include cyber security controls for significant changes in the test plan checklist; and 2) developed a training class on CIP-007 for all personnel responsible for the process of testing significant changes to ensure that the test plan checklist includes cyber security controls.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000663 | CIP-007-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R2 because during a review of the ports and services documentation, operator workstations (which are Cyber Assets) within the Electronic Security Perimeter (ESP) were found to be missing from that initial compliance review. It was determined that SERC_URE1 had a procedure in place that detailed how to determine and document ports and services for each type of operating system in service as Critical Cyber Assets (CCAs) or non-critical Cyber Assets within the ESP. The original investigation between SERC_URE1 and SERC_URE1’s agent determined that subparts of the procedure were violated, and ports and services for certain Cyber Assets within the ESP (the operator workstations) were not documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These missing workstations were exclusively available to operators within the Physical Security Perimeter and ESP, where only permitted traffic is allowed, and were not accessible from outside the ESP. These workstations were located within the ESP, they were protected by anti-virus and current software patches and monitored in real-time by an intrusion detection system. | To mitigate this issue, SERC_URE1's agent: 1) determined if any other Cyber Assets within the ESPs were not compliant with CIP-007 and developed a plan to bring any such assets back into compliance; 2) trained all personnel responsible for change management process on the plan; and 3) completed all outstanding tasks from the plan.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000739 | CIP-003-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R1.2 because it had failed to ensure the cyber security policy (CSP) of SERC_URE1’s agent, was readily available to all personnel who had access to, or were responsible for, Critical Cyber Assets (CCA). SERC_URE1 learned that the CSP had not been provided to all contractors who had access to or were responsible for CCAs. This issue resulted from a lack of understanding that the contractors who had access to CCAs must also have ready access to the CSP. A copy of the CSP was later provided to the affected contract employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was limited to 12 contractors with remote electronic access. The contractors were from reputable companies that supported multiple cyber systems, so they were well aware of applicable cyber security controls. | To mitigate this issue, SERC_URE1's agent installed a computer kiosk at the entrance to the Electronic Security Perimeter with a copy of the SERC_URE1's agent's CSP to facilitate availability of the CSP for escorted personnel.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000740 | CIP-002-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-002-1 R3 because it failed to identify certain workstations and laptops in its control center and back-up control center as Critical Cyber Assets (CCAs). SERC_URE1 learned that certain control centers and back-up control center workstations and laptops were not on its CCA list. The identified Cyber Assets that were deemed critical were added to the CCA list and all required CCA controls and protections were put into place. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All workstations were protected by standard company security control practices for electronic and physical access. All workstations and laptops were located within the control center, a secure area. | To mitigate this issue, SERC_URE1's agent added each newly identified CCA to its official list.
Southwest Power Pool Regional Entity | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2012009935 | CIP-007-1 | R5; R5.2.2 | During a CIP Compliance Audit, SPP RE determined that SPP RE_URE1 was noncompliant with CIP-007-3 R5.2.2. Specifically, although SPP RE_URE1 had a documented list identifying individuals with access to shared accounts, the list did not include those individuals with access to one default shared local account for a Microsoft SQL Server database default account. This account is associated with a non-critical cyber asset located within the Electronic Security Perimeter (ESP), which is used solely as a historical data warehouse. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE_URE1 only failed to document the individuals that had access to the shared local account for the Microsoft SQL Server database default account but the remaining individuals were identified correctly. Furthermore, the Microsoft SQL Server account only contained SPP RE_URE1 historical Energy Management System (EMS) data. The cyber asset did not have real-time capabilities; therefore any cyber security compromises to this asset would not have affected real-time operations. Finally, although undocumented, any individual who had access to the Microsoft SQL server would have had a documented Personal Risk Assessment (PRA) per SPP RE_URE1's access request and authorization process. | SPP RE_URE1 identified all individuals having access to the subject shared account and updated its shared user account list accordingly. SPP RE verified completion of the mitigating activities.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 1 (Texas RE_URE1) | NCRXXXXX | TRE2012009947 | CIP-002-1 | R1.2 | During a Compliance Audit of Texas RE_URE1, Texas RE discovered an issue with Reliability Standard CIP-002-1 R1.2. Texas RE discovered that Texas RE_URE1 did not consider all assets listed in R1.2 when developing its risk-based assessment methodology (RBAM). Texas RE_URE1 had delegated certain function activities to a contractor but had failed to include the contractor’s control center in its consideration of Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. After Texas RE_URE1 considered the contractor’s facilities, Texas RE_URE1's list of Critical Assets or Critical Cyber Assets (CCA) remained null because the control center was deemed not to be a Critical Asset. The contractor does not perform any of the operations related to Texas RE_URE1's generation unit. The contractor is used as a communications medium between Texas RE_URE1's generation unit and other entities. Additionally, at the time of the issue, there was communication redundancy from the contractor to the plant that included four means of communication. | Texas RE_URE1 has included the contractor’s control center as a consideration in its RBAM. The RBAM has been reviewed and signed by the current senior manager. Texas RE has verified the mitigation activities as complete.
Texas Reliability Entity, Inc (Texas RE) | Unidentified Registered Entity 2 (Texas RE_URE2) | NCRXXXXX | TRE2012011389 | CIP-002-3 | R4 | Texas RE_URE2 self-reported an issue with CIP-002-3 R4. Specifically, Texas RE_URE2 stated that it failed to follow its own procedures to have its risk-based assessment methodology (RBAM) and Critical Assets/Critical Cyber Assets (CCA) lists reviewed and signed annually by its CIP senior manager. Texas RE verified that Texas RE_URE2 did review its RBAM and Critical Assets/CCA lists in the prior year, and that the CIP senior manager responsible for signing the documents did so prior to the annual deadline. However, with the transition to a new CIP senior manager in the next year, Texas RE_URE2 failed to have these documents reviewed and signed by the annual deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Once Texas RE_URE2 did review its RBAM, and its Critical Assets and CCA lists, no changes were noted. Therefore, Texas RE_URE2 had been operating with a complete list of Critical Assets/CCAs for the 12 days that the issue occurred. | Texas RE_URE2's new delegated CIP senior manager reviewed and signed the documents. Furthermore, to prevent reoccurrence, Texas RE_URE2 has implemented an automated notification system, which sends out notices to the appropriate personnel when the time for the annual review comes up. Texas RE has verified that these activities have been completed.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011470 | CIP-006-3c | R2 | WECC_URE1 submitted a Self-Report to WECC citing an issue with CIP-006-3c R2. WECC_URE1 reported that it had been revising its risk-based assessment methodology (RBAM) and that based on the revised RBAM it was going to remove three facilities from its Critical Asset list. WECC_URE1 stated that prior to finalization of the new Critical Asset list, WECC_URE1 employees transferred certain Physical Access Control System (PACS) devices, which controlled access and logged information for the three facilities, from the PACS virtual local area networks (VLAN), which provides all of the protections required by CIP-006-3c R2.2, to the corporate security VLAN. WECC_URE1 noted that the corporate security VLAN does not provide all the requirements of CIP-006-3c R2.2. The PACS devices remained on the Corporate Security VLAN for four days until WECC_URE1’s senior manager approved the new Critical Asset list removing the three facilities. WECC_URE1 reported that the PACS devices, which protected the facilities, were not afforded all of the protections required by CIP-006-3c R2.2. Specifically, when placed on the Corporate Security VLAN, WECC_URE1 failed to apply the protections afforded by CIP-003-3 R6, CIP-005-3 R2.4 and R2.5, CIP-006-3 R5, CIP-007-3 R1, and CIP-007-3 R7.2 and R7.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risks posed by this issue were, to an extent, limited given the scope of the issue and compensating measures in place. The issue duration period is limited to four days, thus reducing vulnerabilities given the limited window of opportunity for possible intentional or unintentional misuse or intrusion. Further, the scope of the issue is limited to four PACS devices that were relocated to WECC_URE1’s Corporate VLAN. WECC_URE1’s Corporate VLAN is an isolated access network. Similar to an Electronic Security Perimeter (ESP), electronic access to the VLAN is controlled and monitored. Individuals who accessed the Corporate Security VLAN had completed Critical Infrastructure Protection training and a personnel risk assessment. Similarly, physical access to the PACS devices was controlled and monitored. Individuals with unescorted physical access completed training and were on the WECC_URE1’s unescorted access list. The PACS devices were located within a Physical Security Perimeter (PSP). Furthermore, during the four day period, WECC_URE1 continued to log access to the PSPs containing PACS devices. | To mitigate this issue, WECC_URE1: 1) approved its revised RBAM and removed the three related facilities from its Critical Asset list; and 2) WECC_URE1 senior management discussed the issue and reiterated the importance of clear communications and Standard Owner responsibilities. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010363 | CIP-004-3 | R4 | WECC_URE2 submitted a Self-Report citing an issue with CIP-004-3 R4, specifically R4.1. WECC_URE2 reported that a telecommunications agent, who had authorized unescorted physical access to Critical Cyber Assets (CCAs) within the Physical Security Perimeter (PSP) located at WECC_URE2’s system operations control center, was terminated from his position. WECC_URE2 noted that the individual did not have logical access to CCAs and was required to have physical access to the PSP as part of his job duties. WECC_URE2 reported that upon termination, the individual’s access was revoked and his badge was collected by Human Resources but the personnel access list for CCAs was not updated to reflect the termination. WECC_URE2 stated that the assistant manager of system and trading operations discovered that the terminated individual no longer needed to be on the CCA authorized personnel list. On that same day, the assistant manager informed the personnel access list manager that the terminated employee no longer needed access to CCAs and the personnel access list manager subsequently deactivated the individual’s physical access to the control system and removed the individual from the physical access list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risks posed by WECC_URE2’s issue are, to an extent, minimized by the scope of the issue as well as compensating measures in place during the issue duration. The scope of the issue is limited to one employee. WECC_URE2 has procedures that include removing access badges and keys from employees after such employees have been terminated. Additionally, WECC_URE2 removes logical access to CCAs immediately upon termination. Furthermore, WECC_URE2 has a policy of training all employees who have access to CCAs and has all employees with such access undergo a personnel risk assessment (PRA). Moreover, the system control center is monitored by human observation 24 hours a day 7 days a week. Finally, in this case, WECC_URE2 revoked the employee’s access and did collect the employee’s access card (badge), thus precluding the employee from gaining access during pendency of the remediated issue and WECC_URE2 updated its access list within 11 days of the employee’s departure. | To mitigate this issue, WECC_URE2: 1) updated the personnel access list and removed the terminated person from the list; 2) WECC_URE2’s Human Resources department updated its notification and distribution process to include the system trading operations manager, personnel access list manager, and the system administrator to update the access list for personnel who no longer require access to CCAs as a result of separation actions; and 3) WECC_URE2’s procedure for personnel access to CCAs was modified to include Human Resources and system trading operations manager notification. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011000 | CIP-002-2 | R4 | WECC performed an off-site Compliance Audit of WECC_URE3. During the Audit, the audit team concluded that WECC_URE3 had an issue with CIP-002-2 R4 for failing to have a CIP Senior Manager, or delegate thereof, sign and approve its risk-based assessment methodology (RBAM), its null list of Critical Assets, and its null list of Critical Cyber Assets (CCAs). WECC_URE3’s general manager, who designated the CIP senior manager but is not the CIP designated senior manager or a delegate thereof, did approve WECC_URE3’s RBAM, its null list of Critical Assets, and its null list of CCAs during the duration of the issue. In addition, WECC_URE3’s CIP senior manager did sign an attestation documenting the annual dates on which he approved WECC_URE3’s risk-based methodology, its null list of Critical Assets, and its null list of CCAs. The dates of the designated CIP senior manager’s annual review and approval of WECC_URE3’s risk-based methodology and the results of the assessment, which led to null lists of Critical Assets and CCAs, are identified in the attestation and align with WECC_URE3’s other compliance documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE3’s general manager had reviewed and approved its risk-based methodology, its null list of Critical Assets, and its null list of CCAs during the duration of the issue. Furthermore, there are documented emails from the CIP senior manager noting his awareness of the lists of Critical Assets and CCAs. The designated CIP senior manager reports directly or indirectly to the general manager. Accordingly, WECC_URE3 was aware that it did not have any Critical Assets or CCAs. | To mitigate this issue, WECC_URE3’s CIP senior manager signed an attestation noting the annual dates on which he reviewed and approved its risk-based methodology, its null list of Critical Assets, and its null list of CCAs.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012011468 | CIP-004-3 | R4 | WECC_URE4 submitted a Self-Report citing an issue with CIP-004-3 R4. WECC_URE4 reported that it failed to revoke physical access to Critical Cyber Assets (CCAs) within seven days for an individual who no longer required such access. An individual employed by WECC_URE4 no longer required physical access to a single Physical Security Perimeter (PSP) containing CCAs. Per CIP-004-3 R4.3, access rights should have been revoked within seven days. Access was revoked within ten days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by WECC_URE4's issue is limited given the scope of the issue and the compensating measures in place during the duration of the issue. The individual maintained physical access rights to a single PSP for a period of three days beyond the period prescribed in R4.2. The individual in scope of the issue completed a personnel risk assessment, and cyber security training. The individual in scope did not attempt to physically access the CCAs. All of the CCAs to which the individual had access were contained within a Physical Security Perimeter. Physical access thereto was controlled and monitored. Unauthorized physical access attempts would have triggered alarming. The CCAs were also electronically secured within an Electronic Security Perimeter (ESP). Electronic access was controlled and monitored. Electronic access was limited to specific staff members who required such access. Cyber security events within the ESP containing the CCAs would have triggered alarming. | To mitigate this issue, WECC_URE4: 1) revoked individual’s access to CCAs; and 2) implemented additional training and workload/resource management to prevent future instances of a similar nature.