## Public CIP June FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012009680 | CIP-007-1 | R2; R2.1 | During an on-site Compliance Audit, FRCC determined that FRCC_URE1 had an issue with CIP-007-1 R2.1. FRCC_URE1 could not provide evidence to demonstrate that only ports required for normal and emergency operations were enabled for all of its Critical Cyber Assets. For the identified Cyber Assets, scans demonstrated that one port was open which was not documented as a port required for normal and emergency operations. Although a different port was documented in the list of authorized ports for the Cyber Assets, vendor documentation did not support the need for this port and it would vary each time the application was restarted. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because the open port varied each time the application was restarted, requiring a new port scan on the system to find the port. The Cyber Asset is located within an Electronic Security Perimeter (ESP) and Physical Security Perimeter. Furthermore, access to the range of unauthorized open ports is closed at the ESP access point firewall preventing access to the Cyber Asset from outside the ESP. | To mitigate this issue, FRCC_URE1: 1) updated its authorized ports and services by asset class - application servers document, to remove the unneeded port and associated service from the list of authorized ports and services; 2) submitted a technical feasibility exception (TFE) to document implementation of the windows firewall to block the unauthorized ports that are not required for operation and cannot be disabled by the vendor supplied application; and 3) verified the TFE mitigating and compensating protections are only allowing the authorized services to listen for connections on authorized ports. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013011736 | CIP-005-3a | R3; R3.2 | FRCC_URE1 self-reported that it had an issue with CIP-005-3a R3.2. For approximately one minute, FRCC_URE1's backup logging monitoring and alerting Cyber Asset was unable to detect and alert for attempts at or actual unauthorized accesses when it had to switch from the primary to backup monitoring Cyber Asset during a scheduled maintenance update of the primary logging Cyber Asset. FRCC_URE1 did not timely submit a Technical Feasibility Exception (TFE) for the Cyber Asset. It did, however, have a manual process in place to detect and alert for attempts at or actual unauthorized accesses although not clearly documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was reduced because FRCC_URE1 had a manual procedure (although not clearly documented) in place for the backup monitoring and logging Cyber Asset to detect and alert (manually) for attempts at or unauthorized accesses. Furthermore, the duration of the issue was short, one minute, and the issue was a result of an administrative oversight in not submitting the TFE. | To mitigate this issue, FRCC_URE1: 1) submitted a TFE for the Cyber Asset's inability to detect and alert; and 2) updated documentation to sufficiently articulate manual review process. FRCC has verified the completion of all mitigation activity.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011475 | CIP-002-1 | R1; R1.2.2; R1.2.3 | During a Compliance Audit, MRO discovered that MRO_URE1 failed to have a risk-based assessment methodology (RBAM) which considered the following assets: 1) transmission substations that support the reliable operation of the bulk electric system (BES), in accordance with CIP-002-1 R1.2.2; and 2) generation resources that support the reliable operation of the BES, in accordance with CIP-002-1 R1.2.3. Specifically, MRO_URE1 failed to include criteria in order to determine criticality of substations below 230 kV, generators below 100 MW, and transmission and generation assets required for system restoration. Instead of developing criteria, MRO_URE1 relied upon a statement from its subject matter expert (SME). MRO_URE1 also relied upon a similar statement for generators under 100 MW. While engineering judgment is permissible in an RBAM, MRO determined that further documentation of this assertion was necessary. Furthermore, during mitigation, MRO discovered that preliminary asset lists, used to exercise the RBAM, had some discrepancies. However, those discrepancies were found to be assets which were not owned by MRO_URE1, and were erroneously included in its asset list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although MRO_URE1’s documentation was insufficient for its justification of excluding these assets from its assessment, MRO_URE1 asserted that its SMEs have sufficient engineering experience with other system studies in this area to make such determinations. MRO_URE1 failed to properly document its SME experience which qualified them to make such determinations. Additionally, the documentation issue with the preliminary asset lists did not impact MRO_URE1’s overall Critical Asset list. The revisions did not result in any additions to MRO_URE1’s actual list of Critical Assets. Therefore, MRO determined that this issue posed a minimal risk to the BPS. | To mitigate this issue, MRO_URE1 revised its RBAM to include more detail regarding the engineering assessment process to achieve the following: 1) clarify the criteria for including or excluding BPS assets from further detailed analysis during the application of the RBAM; 2) provide additional documentation specific to the assessment of restoration resources; and 3) clarify the assessment method for assets that are owned by other registered entities but operated by MRO_URE1.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010128 | CIP-002-1 | R1 | During a Compliance Audit, MRO discovered that MRO_URE2 failed to adequately document evaluation criteria used to assess its Critical Assets to determine the impact on the Bulk Electric System (BES). CIP-002-1 R.1.1 requires the Responsible Entity to maintain documentation describing its risk-based assessment methodology (RBAM) that includes procedures and evaluation criteria. MRO_URE2 included its procedures used to categorize assets in its RBAM, but did not include evaluation criteria. MRO_URE2's RBAM contained impacts to the BES that were conclusory and did not identify how its conclusions were derived for classifying its Critical Assets. For example, MRO_URE2's control center was identified as having a low probability of an event and minimal impact on the BES, but did not state how those conclusions were determined. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE2 does not operate generation or transmission facilities. As a result, its control center is used as a "view-only" tool. Although MRO_URE2 did not include evaluation criteria in its RBAM, MRO_URE2's previous determination regarding its list of Critical Assets remained the same after MRO_URE2 clarified its evaluation criteria. | To mitigate this issue, MRO_URE2 updated its RBAM pursuant to CIP-002 R1, which incorporated bright-line criteria from new CIP versions. Under its current RBAM, MRO_URE2's list of Critical Assets remains the same.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2012010160 | CIP-002-1 | R1; R1.1 | During a Compliance Audit, MRO discovered that MRO_URE3 failed to maintain documentation describing its risk-based assessment methodology (RBAM) that includes procedures and evaluation criteria, in accordance with CIP-002-1 R1.1. MRO_URE3 used a formula for determining criticality. Although MRO_URE3 assigned numbers for both of these scales for each asset, it failed to document how the scale entries were obtained. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although MRO_URE3’s RBAM lacked clear documentation in the use of the evaluation criteria for determining criticality, MRO_URE3 does not have any Critical Assets. Additionally, MRO_URE3 is a small entity with limited possible impact on the BPS. | To mitigate the issue, MRO_URE3 documented how each rating scale number is determined and how assets fit each rating. MRO has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012125 | CIP-005-3a | R5; R5.2 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-3a R5.2. RFC_URE1 changed the way it monitors and logs access at access points to its Electronic Security Perimeters (ESPs) when it replaced a RFC_URE1-owned and managed monitoring and logging appliance with a third-party monitoring and logging service. However, RFC_URE1 failed to update the documentation reflecting the modification of the network and controls within 90 calendar days of this change. RFC_URE1's failure to update documentation following its implementation of a new monitoring and logging service also resulted in RFC_URE1's noncompliance with Reliability Standard CIP-008-3 R1, as described in issue RFC2013012131. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's issue was a documentation deficiency related to its reference of a previous version of its monitoring and logging service, rather than the new monitoring and logging service within its CIP-005-3 documentation. RFC_URE1 did not leave its devices unprotected as a result of this documentation error. Rather, in implementing the change from one system to another system, RFC_URE1 did not deactivate its previous monitoring and logging appliance until the new monitoring and logging service was up and running, in order to ensure that there was no interruption in ESP monitoring and logging. In addition, RFC_URE1 personnel responsible for ESP monitoring and logging were directly involved in the transition from the previous monitoring and logging appliance to the new monitoring and logging service, and were therefore familiar with the changes to the monitoring infrastructure. Furthermore, the relevant personnel were continuously able to receive alerts and event data and were knowledgeable about how to customize alerts and access and review log files both during and after the transition to the new monitoring and logging service. The issue was a clerical error that had no impact on its operational capability and which did not interrupt its monitoring or logging of the ESP. | To mitigate this issue, RFC_URE1 modified its change ticket templates for its CIP-003 change control and configuration management process to require change submitter to determine whether, in each instance, RFC_URE1 should update additional documents that might be affected by a change.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012129 | CIP-007-1 | R4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R4 because it submitted its technical feasibility exception (TFE) request for its monitoring services late due to vendor delays in providing RFC_URE1 the required information. Additionally, RFC_URE1 overlooked the need to file TFEs for two switches, due to the operational functionality of these devices. For all three devices, RFC_URE1 was unable to install anti-virus software and malware prevention tools, but failed to document the compensating measures applied to mitigate risk exposure or acceptance of risk. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 provided alternate controls to protect its systems from cybersecurity breaches where anti-virus software and malware prevention tools were technically infeasible. Each implicated system and device is located behind a Physical Security Perimeter (PSP). Additionally, the two switches are located inside an Electronic Security Perimeter (ESP) and utilize a rudimentary proprietary operating system that utilizes magnetic relays to switch between routers and that is not capable of anti-virus or malware installation. RFC_URE1 follows its malware prevention program for all other devices. Furthermore, RFC_URE1 has not experienced any incidents or security breaches during the time frame of this issue. | To mitigate this issue, RFC_URE1 implemented the compensating measures, which included all equipment being inside a six-wall PSP and the switches within the ESP, described in its TFE Part B submittals to mitigate risk exposure.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010394 | CIP-007-1 | R5; R5.3.2 | RFC_URE1 submitted a Self-Certification and approximately a week later RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R5. RFC_URE1 failed to timely notify ReliabilityFirst of instances related to its operating system where, due to technical infeasibility, RFC_URE1 did not require the use of passwords consisting of a combination of alpha, numeric, and “special” characters. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although RFC_URE1 does not have technical controls regulating password complexity for its operating system, RFC_URE1 had procedural controls in place which require all system users to utilize CIP compliant passwords where possible. RFC_URE1 also submits email reminders to all system users regarding the proper password complexity. RFC_URE1 utilized technical controls to enforce the password complexity to the maximum extent capable by the operating system, which includes, at a minimum, a forced password character length of at least eight characters. Additionally, the equipment that is running the operating system is inside a Physical Security Perimeter and an Electronic Security Perimeter which RFC_URE1 monitors 24 hours a day, seven days a week. | To mitigate this issue, RFC_URE1 submitted a Technical Feasibility Exception to ReliabilityFirst and reminded operators of the CIP-007 R5.3.2 password complexity requirements.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012130 | CIP-007-1 | R6 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R6. For two Cyber Assets within the Electronic Security Perimeter, namely two switches, RFC_URE1 did not ensure that these devices implement automated tools or organizational process controls to monitor system events related to cybersecurity, nor did RFC_URE1 submit a Technical Feasibility Exception (TFE) with ReliabilityFirst to document the technical infeasibility of implementing such controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The limited operational functionality of the two switches protects RFC_URE1's system from cybersecurity breaches, since the devices are used only to switch incoming Supervisory Control and Data Acquisition (SCADA) data feeds between a redundant pair of front-end processors. A SCADA and energy management system (EMS) server controls the operation of both switches and will command an “A to B” or “B to A” switchover if it detects a loss of incoming SCADA data. The SCADA/EMS server’s detection of data loss effectively compensates for the fact that the switches themselves have no monitoring capabilities. Furthermore, the SCADA/EMS server has been given the protections as applicable from CIP-002 through CIP-009. Therefore, RFC_URE1 implemented measures to provide protection to its system from cybersecurity events. | To mitigate this issue, RFC_URE1: 1) filed a TFE with ReliabilityFirst related to the switches; and 2) modified its change ticket templates used for CIP-003 change control and configuration management to require change submitters to determine whether one or more TFEs will be required for any new Cyber Asset subject to CIP requirements. If TFE(s) are required, the submitter will be required to enter ReliabilityFirst-assigned TFE identifier(s) before change ticket can be closed out.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010395 | CIP-007-3 | R9 | RFC_URE1 submitted a Self-Certification to ReliabilityFirst stating that it had an issue with CIP-007-3 R9. RFC_URE1 failed to annually review and update all documentation specified in Standard CIP-007-3. Specifically, RFC_URE1 failed to annually review and update the following CIP-007-3 documentation in 2011: 1) system security management: ports and services procedures; 2) system security management: security patch management; 3) system security management: malicious software prevention; 4) system security management: Cyber Asset disposal or redeployment procedures; and 5) system security management: cyber vulnerability assessments. Instead, within RFC_URE1’s document management system, RFC_URE1 mislabeled the document review frequency label by inserting an incorrect document review due date and thereafter failed to annually review all CIP-007-3 documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was caused by a data entry mistake and was corrected within five months. Only minor updates to the subject document were necessary. Finally, RFC_URE1 performed the necessary reviews and updates for 2012. . | To mitigate this issue, RFC_URE1: 1) labeled documents correctly in its document management system in order to ensure that it conducts future document reviews on an annual basis; 2) created a tool to track document review dates; and 3) reviewed its documentation and added those documents that it had previously not reviewed on an annual basis to its review matrix. ReliabilityFirst has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012131 | CIP-008-3 | R1; R1.4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-008-3 R1.4. RFC_URE1 changed its system for generating automated Cyber Security Incident alerts, but failed to update its Cyber Security Incident response plan within 30 calendar days of this change. RFC_URE1's failure to update documentation following its implementation of a new monitoring and logging service also resulted in RFC_URE1's noncompliance with Reliability Standard CIP-005-3a R5.2, as described in RFC2013012125. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's issue was a documentation deficiency related to its reference of a previous version of its monitoring and logging service, rather than the new monitoring and logging service within its Cyber Security Incident response plan. RFC_URE1 did not leave its devices unprotected as a result of this documentation error. Rather, in implementing the change from one system to another system, RFC_URE1 did not deactivate its previous monitoring and logging appliance until the new monitoring and logging service was up and running, in order to ensure that there was no interruption in Electronic Security Perimeter (ESP) monitoring and logging. In addition, RFC_URE1 personnel responsible for (ESP) monitoring and logging were directly involved in the transition from the previous monitoring and logging appliance to the new monitoring and logging service, and were therefore familiar with the changes to the monitoring infrastructure. Furthermore, the relevant personnel were continuously able to receive alerts and event data and were knowledgeable about how to customize alerts and access and review log files both during and after the transition to the new monitoring and logging service. The issue was a clerical error that had no impact on its operational capability and which did not interrupt its monitoring or logging of the ESP. | To mitigate this issue, RFC_URE1: 1) updated its Cyber Security Incident response plan; and 2) modified its change ticket templates for its CIP-003 change control and configuration management process to require change submitter to determine whether, in each instance, should update additional documents that might be affected by a change.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012132 | CIP-009-3 | R1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that had an issue with CIP-009-3 R1. RFC_URE1 failed to annually review two documents: 1) the RFC_URE1 IT plan dealing with backup and recovery; and 2) the site replication and failover plan, which are incorporated by reference into RFC_URE1's recovery plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 conducted an annual review on the remainder of the recovery plan, except the two documents which were incorporated by reference. Additionally, RFC_URE1 determined that the two referenced documents that were not reviewed on an annual basis did not require any updates. | To mitigate this issue, RFC_URE1 added the two missed documents to its annual review matrix and reviewed each document.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012302 | CIP-003-1 | R2; R2.1 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-003-1 R2. RFC_URE2 could not locate a separate specific document that identified the senior manager by name, title, and date of designation for approximately 28 months. However, the senior manager who approved and signed the CIP-related documents, including the Critical Asset assessment and subsequent lists of Critical Assets and Critical Cyber Assets (CCAs) was the appropriate senior manager during that time period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This was a documentation issue only. The senior manager that approved and signed the CIP-related documents was the appropriate senior manager during that time period and is now retired. RFC_URE2 has no Critical Assets or CCAs, reducing the likelihood that this issue would cause a risk to the reliability of the BPS. | To mitigate this issue, RFC_URE2: 1) conducted a review of its CIP procedure; 2) revised its designation of senior manager letter and stored it in the electronic document management program for document retention. In addition, the electronic data tracking system will generate an annual reminder to review senior manager assignments; and 3) created a managerial transition checklist as a reminder to validate the senior manager assignment within 30 days of senior manager assignment.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012420 | CIP-003-2 | R1 | ReliabilityFirst conducted a Compliance Audit and determined that RFC_URE3 had an issue with CIP-003-2 R1. RFC_URE3 failed to ensure that its cybersecurity policy addresses all of the requirements in Standards CIP-002 through CIP-009. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3's policy generally addressed the NERC CIP Standards, even though it did not specifically address each Requirement. RFC_URE3 implemented its cybersecurity policy with limited deficiencies not attributed to the policy document. | To mitigate this issue, RFC_URE3 revised its cybersecurity policy to address the requirements of Standards CIP-002 through CIP-009.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012012427 | CIP-005-1 | R4; R4.2, R4.3, R4.4 | ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that RFC_URE3 had an issue with CIP-005-1 R4. RFC_URE3's cyber vulnerability assessment (CVA) of electronic access points did not identify all access points, such as WAN routers and gas server room modems. As a result, RFC_URE3 failed to conduct a complete review that only ports and services required for operations at access points are enabled (R4.2) and failed to discover all access points to the Electronic Security Perimeter (R4.3). RFC_URE3 conducts an automatic and a manual review of controls for default accounts, passwords, and network management community strings but, in its CVA failed to include the gas server room modems in the manual review (R4.4). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 performed CVAs for its electronic access points, although it did not document the consideration of R4.2, R4.3, and R4.4. In addition, for the access points that RFC_URE3 did not discover, RFC_URE3 classified the access points it failed to discover as Critical Cyber Assets (CCAs) and afforded them the protective measures of CCAs. | To mitigate this issue, RFC_URE3 revised its documented process for CVAs of access points to the Electronic Security Perimeter.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012428 | CIP-006-1 | R1 | ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that RFC_URE3 had an issue with CIP-006-1 R.1. ReliabilityFirst discovered an Electronic Security Perimeter cable that extended outside the Physical Security Perimeter (PSP). In addition, ReliabilityFirst discovered that RFC_URE3 failed to identify an emergency exit door as an access point on its PSP drawing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The cabling is located under a raised floor for a short distance on the floor of the corporate office, which has limited access. The door at issue is an emergency exit only and it is incapable of opening from the outside. If opened from the inside, an alarm activates and security would respond to the alarm. In addition, the door is located inside a building with limited access. | To mitigate this issue, RFC_URE3 installed conduit around the cable at issue and added the emergency exit door to the PSP drawing.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013011665 | CIP-006-3c | R1 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R1. RFC_URE4 decommissioned a Physical Security Perimeter (PSP) at a power plant because it moved two workstations into another PSP at the plant. RFC_URE4 performed a routine physical walk-down of the power plant to validate network documentation. During the walk-down, RFC_URE4 discovered that two Cyber Assets in the decommissioned PSP, one critical and one non-critical, remained connected to the Electronic Security Perimeter (ESP) through the power plant’s main site distribution switch (which was located in an active and protected PSP. As a result, two Cyber Assets remained connected to ESP after RFC_URE4 decommissioned the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue still had the protections of the ESP. In addition to the protections of the ESP, these devices utilize a non-Windows based operating system that is not as susceptible to mainstream viruses. Although lack of physical protection presents an increased risk of access, the decommissioned PSP was wholly contained on a site with restricted access and perimeter security protection, reducing the likelihood of unauthorized access. | To mitigate this issue, RFC_URE4 removed the devices from the ESP and revised its current change control process to ensure it all business units understand the process of decommissioning PSPs. ReliabilityFirst has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013011946 | CIP-005-1 | R1; R1.4 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-1 R1. During a physical walk-down of all CIP Physical Security Perimeters (PSPs), RFC_URE4 discovered an undocumented switch residing in the Electronic Security Perimeter (ESP) and PSP at a power plant. The switch was acting as a hub to connect one of RFC_URE4’s paperless chart recorders to a different switch. RFC_URE4 failed to identify and protect this switch as required by CIP-005-3a R1.4. RFC_URE4 removed the switch from the ESP. RFC_URE4 submitted another Self-Report to ReliabilityFirst identifying an additional issue with CIP-005-1 R1.4, consolidated into RFC2013011946. During its annual physical and electronic walk down of the power plant, RFC_URE4 discovered two undocumented non-critical Cyber Assets within the ESP. The devices, a wireless gateway device and a signal converter, were connected to a router in the plant’s ESP. RFC_URE4 failed to identify these devices as required by CIP-005-1 R1.4. RFC_URE4 disconnected the wireless gateway device from the router and RFC_URE4 disconnected the signal converter from the router. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the undocumented switch, the switch utilized a non-Windows operating system that is not as susceptible to mainstream viruses. The switch resided in a PSP and the paperless chart recorder was the only device to which it was connected. Both the wireless gateway device and the signal converter device were located within an ESP and PSP. Regarding the wireless gateway device, RFC_URE4 never configured it with an IP address and it was therefore unable to communicate or be discovered on the network. In addition, wireless transmission on the device was inactive. Regarding the signal converter, RFC_URE4 utilizes the device to remotely monitor data on the generating unit, which does not affect plant operation. In addition, its monitoring capability was redundant because a primary means of monitoring the asset was in place. As a result, it was less likely that unauthorized access to Critical Cyber Assets could occur through these devices. | To mitigate this issue, RFC_URE4: 1) removed the device from the ESP and PSP; and 2) removed the devices after verifying that their removal would not impact the reliability of the system.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012068 | CIP-004-4 | R2 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-4 R2. RFC_URE4 added a new contractor to the network engineering security group to enable the contractor to access a non-NERC system. This contractor did not have cybersecurity training. Adding the contractor to this group inadvertently provided the contractor with cyber access to certain routers and switches, which are Critical Cyber Assets (CCAs). During a periodic user access review, RFC_URE4 discovered this access and immediately revoked it. RFC_URE4 submitted a Self-Report to ReliabilityFirst identifying an additional issue with CIP-004-4, consolidated into RFC2013012068. As part of an internal effort to improve its reporting mechanism for physical and electronic access, RFC_URE4 discovered two contract employees and one RFC_URE4 employee that had not completed annual training but retained physical access to one or more Physical Security Perimeters. RFC_URE4’s internal policy requires employees and contractors to renew their annual training once per calendar year, not to exceed 15 months. In each instance, the employee and the supervisor of the employee were notified that the training was set to expire. Upon discovery, RFC_URE4 revoked access for all three individuals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the failure to conduct cybersecurity training prior to granting access, the contractor had a current and valid personnel risk assessment (PRA). In addition, when RFC_URE4 reviewed the logs, it determined that the contractor did not access any of the CCAs. It is unlikely that the contractor would have known about the access to such devices as the contractor’s job roles did not include accessing NERC CIP routers or switches. Regarding the failure to complete annual cybersecurity training, the individuals had physical access only, and all three individuals had current and valid PRAs. All three individuals had completed cybersecurity training prior to being granted access. | To mitigate this issue, RFC_URE4: 1) revoked the employees’ access, and implemented a system-generated nightly list of all personnel with electronic and physical access that have qualifications in jeopardy of surpassing the allotted annual review period. This list will be automatically distributed to the NERC compliance organization for review and monitoring; and 2) communicated the importance of timely access revocation to all RFC_URE4 leaders.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012099 | CIP-006-3c | R1; R1.6 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R1.6. RFC_URE5 did not log the exit and re-entry of five visitors to a physical security perimeter (PSP). Specifically, RFC_URE5 escorted the five visitors from a conference room inside a PSP to a lab area outside the PSP, but within the same facility, to participate in a demonstration. RFC_URE5 then escorted the five visitors back into the PSP to gather equipment, and then escorted them back out of the PSP to participate in the demonstration. At the close of the demonstration, RFC_URE5 escorted the five visitors back to the PSP. When escorting the visitors into and out of the PSP, RFC_URE5 neglected to log the visitors’ exit and re-entry into the PSP pursuant to CIP-006-3c R1.6.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five visitors had an escort for the duration of the issue. Additionally, the RFC_URE5 escort had successfully completed CIP training, had a valid personnel risk assessment and was authorized to have unescorted access to the PSP at issue. Finally, RFC_URE5 logged initial entry and final exit from the PSP of the five individuals, just not the exit and re-entry associated with the lab demonstration. | To mitigate this issue, RFC_URE5: 1) discussed the incident with the CIP escort and reinforced proper logging procedures; and 2) provided all department personnel with re-education on CIP escort responsibilities during a department meeting.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012098 | CIP-004-1 | R4 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-1 R4. RFC_URE5 discovered that an authentication source was configured to grant a non-CIP directory service group access to Critical Cyber Assets (CCAs). However, RFC_URE5 had not authorized cyber access to two members of the group through its regulatory access authorization database system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both members of the group who lacked cyber authorization from RFC_URE5 had valid CIP training and personnel risk assessments for the duration of the issue. The issue with CIP-004-1 R4 did not provide non-CIP personnel with CIP access; rather it provided cyber access to two CIP-qualified individuals without first formally authorizing access. Finally, the two individuals at issue were unaware they had cyber access to the CCAs at issue and at no time attempted to access the CCAs. | To mitigate this issue, RFC_URE5: 1) removed the two individuals from the group; 2) disabled the group’s ability to access CCAs; 3) created and implemented new naming conventions to delineate between CIP and non-CIP directory service groups, reducing the likelihood that RFC_URE5 will inadvertently assign a non-CIP directory service group to a CIP-controlled access list; and 4) reviewed all directory service groups for similar situations and did not discover any additional instances of possible noncompliance.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012100 | CIP-006-3c | R5 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R5. During a five-day period, RFC_URE5 did not continuously monitor an access point into a physical security perimeter (PSP) with an alarm system or human observation. RFC_URE5 initially configured an access point to a PSP with a portal mantrap and an exterior steel door with a keypad connected to its Physical Access Control System. During a renovation of the access point RFC_URE5 removed the mantrap and with it the alarm for unauthorized access. During this renovation, RFC_URE5 monitored for unauthorized access with human observation 24 hours a day, seven days a week from an office located next to the access point. However, when FE Utilities renovated that office, it relocated the individuals observing the access point for five days. The employee who decided to relocate the individuals from the office for five days incorrectly believed an alarm input was installed on the exterior steel door adjacent to the keypad. RFC_URE5 failed to monitor the access point with an alarm system or human observation during that five-day period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Access to the PSP was controlled and logged by an exterior steel door with the keypad access system for the duration of the issue. Additionally, access to the building in which the PSP is located was continuously monitored by a guard staff stationed 24 hours a day, seven days a week for the duration of the issue. | To mitigate this issue, RFC_URE5 installed an alarm on the access point of the PSP.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2013012193 | CIP-004-1 | R4 | RFC_URE6 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-1 R4. RFC_URE6 discovered that an authentication source was configured to grant a non-CIP directory service group access to Critical Cyber Assets (CCAs). However, RFC_URE6 had not authorized cyber access to two members of the group through its regulatory access authorization database system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both members of the group who lacked cyber authorization from RFC_URE6 had valid CIP training and personnel risk assessments for the duration of the issue. The issue with CIP-004-1 R4 did not provide non-CIP personnel with CIP access; rather it provided cyber access to two CIP-qualified individuals without first formally authorizing access. Finally, the two individuals at issue were unaware they had cyber access to the CCAs at issue and at no time attempted to access the CCAs. | To mitigate this issue, RFC_URE6: 1) removed the two individuals from the group; 2) disabled the group’s ability to access CCAs; 3) created and implemented new naming conventions to delineate between CIP and non-CIP directory service groups, reducing the likelihood that RFC_URE6 will inadvertently assign a non-CIP directory service group to a CIP-controlled access list; and 4) reviewed all directory service groups for similar situations and did not discover any additional instances of possible noncompliance.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2012010380 | CIP-008-3 | R1 | RFC_URE7 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE7 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE7 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE7 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE7 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE7: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE7 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE7 to update the Cyber Response Plan following minor changes to referenced documents.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2012010381 | CIP-008-3 | R1 | RFC_URE8 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE8 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE8 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE8 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE8 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE8: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE8 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE8 to update the Cyber Response Plan following minor changes to referenced documents.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2012010382 | CIP-008-3 | R1 | RFC_URE9 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE9 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE9 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE9 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE9 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE9: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE9 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE9 to update the Cyber Response Plan following minor changes to referenced documents.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 10 (RFC_URE10) | NCRXXXXX | RFC2012010383 | CIP-008-3 | R1 | RFC_URE10 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE10 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE10 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE10 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE10 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE10: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE10 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE10 to update the Cyber Response Plan following minor changes to referenced documents.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 11 (RFC_URE11) | NCRXXXXX | RFC2012010384 | CIP-008-3 | R1 | RFC_URE11 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE11 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE11 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE11 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE11 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE11: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE11 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE11 to update the Cyber Response Plan following minor changes to referenced documents.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 12 (RFC_URE12) | NCRXXXXX | RFC2012011286 | CIP-001-1a | R2 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE12 had an issue with CIP-001-1a R2. RFC_URE12 failed to have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. RFC_URE12 provided a safety manual procedure for emergency response, but the document’s emergency contact list did not include appropriate contacts for the Interconnection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that RFC_URE12 had a procedure in place for responding to suspected or actual sabotage events, including a list of contacts for reporting such events, although this list did not include appropriate parties in the Interconnection. The contact list contained names of various people within the RFC_URE12 organization, county sheriff, Federal Bureau of Investigation, local hospital, gas pipeline contacts, environmental agencies, and other state and federal contacts. | To mitigate this issue, RFC_URE12 updated its safety manual procedure to include telephone numbers for contacting the appropriate parties in the Interconnection concerning sabotage events.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 12 (RFC_URE12) | NCRXXXXX | RFC2012011287 | CIP-001-1a | R3 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE12 had an issue with CIP-001-1a R3. Although RFC_URE12 had sabotage response guidelines on file, RFC_URE12 could not provide evidence that changes to the guidelines were made available to operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that RFC_URE12 had developed a sabotage response guidelines. In addition, RFC_URE12 held meetings, during which possible sabotage incidents may be discussed, indicating some awareness of these guidelines by personnel. | To mitigate this issue, RFC_URE12 trained plant personnel on changes to its sabotage response procedure, including changes to the contact list for reporting sabotage events.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 13(RFC_URE13) | NCRXXXXX | RFC2012010914 | CIP-006-3c | R2; R2.2 | RFC_URE13 submitted a Self-Report stating it had an issue with CIP-006-3c R2 to ReliabilityFirst. RFC_URE13 granted a contractor authorized cyber access to a Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter (PSP) so that that contractor could restart the system if it froze and required restarting. The access did not include anything beyond restarting the system. RFC_URE13; however, failed to conduct a personnel risk assessment (PRA) for the contractor prior to granting access, as required by CIP-004-3 R3. RFC_URE13 discovered this issue within seven days of granting access and removed access that day. RFC_URE13 submitted a Self-Report to ReliabilityFirst identifying an additional occurrence of an issue with CIP-006-3c R2 related to CIP-004-3 R3. RFC_URE13 granted three contractors authorized cyber access to its physical access control system, which constitutes a Cyber Asset that authorizes and/or logs access to the PSP. RFC_URE13; however, failed to conduct a PRA for the contractors prior to granting access, as required by CIP-004-3 R3. RFC_URE13 discovered this issue within four days of granting access and removed access that day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding both occurrences, RFC_URE13's internal controls enabled RFC_URE13 to discover and remediate the issues quickly. Regarding the first occurrence, the first contractor only had access to restart the device and could not perform other functions. Had the contractor restarted the device, logging and monitoring would have remained intact. Regarding the second occurrence, the three contractors were unaware of their access rights to the physical access control system. The three contractors had access in order to support databases not related to the physical access control system. RFC_URE13 database administrators with appropriate access controlled the physical access control system and assigned work to the database administrators unrelated to the physical access control system. As a result, it was unlikely that the contractors would gain inappropriate access. | To mitigate this issue, RFC_URE13: 1) removed the restart capability from the contractor’s group, remove all four contractors from that group, allow only the Cyber Security and critical infrastructure support department to access the Cyber Assets that authorize and/or log access to the PSP; and 2) continued the migration access granting to the Cyber Security and critical infrastructure support department which will process all access requests and require training and PRAs for individuals prior to granting access.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011822 | CIP-003-2 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2 because it did not document the assignment of a senior manager with overall responsibility for leading and managing implementation of, and adherence to, Standards CIP-002 through CIP-009 (CIP senior manager). SERC_URE1 had a supervisor that had assumed the responsibility of the CIP senior manager. This supervisor annually approved SERC_URE1’s risk-based assessment methodology (RBAM) and resulting null lists of Critical Assets and Critical Cyber Assets (CCAs). Additionally, SERC_URE1’s cybersecurity policy identified the CIP senior manager by title, but failed to identify the individual by name and the date of designation. This is the only evidence that SERC_URE1 could provide in regards to the designation of the CIP senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SERC_URE1 did not identify its CIP senior manager by name, title, and date of designation, SERC_URE1’s cybersecurity policy identified its CIP senior manager by title. The supervisor acting as SERC_URE1’s CIP senior manager approved SERC_URE1’s RBAM and resulting null lists for Critical Assets and CCAs. SERC_URE1 does not own or operate any Critical Assets. | To mitigate this issue, SERC_URE1: 1) revised its CIP compliance document to identify the CIP senior manager by name, title, and date of designation; 2) revised its CIP compliance document to require that any changes to the CIP senior manager must be documented within 30 calendar days of the effective date; 3) revised its CIP compliance document to allow the CIP senior manager to delegate authority for specific actions to a named delegate or delegates provided these delegations are documented in the same manner as R2.1 and R2.2, and approved by the CIP senior manager; and 4) revised its CIP compliance document to allow the CIP senior manager or delegate(s) to authorize and document any exception from the requirements of the cybersecurity policy. SERC has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP_URE1) | NCXXXXX | SPP201000446 | CIP-002-1 | R3; R3.3 | SPP_URE1 submitted a Self-Report to SPP RE stating that it had an issue with CIP-002-1 R3.3 because it did not identify all of its Critical Cyber Assets (CCAs) associated with Critical Assets that support reliable operation of the Bulk Electric System (BES). SPP_URE1 instituted a companywide de-commissioning of all dial-up modems and routers with remote connectivity to monitoring and control devices located within its substations. Subsequently, SPP_URE1 discovered that three dial-up devices with remote connectivity to relays designated as Critical Assets were overlooked and not disabled. SPP_URE1 disabled the three devices in March 2010. The issue period was from the date the Standard became mandatory and enforceable to the date SPP_URE1 disabled the devices at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three dial-up devices were connected to relays for retrieving fault information only and did not control any of the associated relays. Furthermore, these devices were password-protected and located within locked control houses. Finally, the duration of the issue lasted only three months, and during that time, no events occurred that put the BPS at risk. | To mitigate the issue, SPP_URE1: 1) disabled the three dial-up devices; and 2) developed a three-step process to ensure that all CCAs associated with Critical Assets that support reliable operation to the BES are identified. SPP RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXX | TRE2012009764 | CIP-003-1 | R4; R4.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-003-1 R4.3 because TRE_URE1 did not include within its information protection annual review process the assessment of the incidence response plan(s) as required for CIP-003-1 R4.3. Texas RE determined that the incident response plan was part of the Critical Cyber Asset (CCA) information that TRE_URE1 protected but TRE_URE1 did not perform the assessment, document the assessment results, and implement an action plan to remediate deficiencies if any, identified during an assessment of the incidence response plan. Therefore, TRE_URE1 had an issue with CIP-003-1 R4 from the date the requirement became enforceable for TRE_URE1 through the date that all mitigating activity was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE1 stated that it performed an annual assessment of its incidence response plan. Although TRE_URE1 failed to specifically list the “incident response plan” in its annual review process document, or provide sufficient evidence of its annual assessment, TRE_URE1 stated that the incident response plan was assessed and it was protected pursuant to the rest of the protected information list. | TRE_URE1 remediated the issue with CIP-003-1 R4 by providing evidence that TRE_URE1’s information protection annual review process has been updated to include the annual assessment of the incident response plan. Texas RE verified completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXX | TRE2012009768 | CIP-005-1 | R4; R4.4 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-005-1 R4.4 because TRE_URE1 did not perform a complete cyber vulnerability assessment (CVA) for the electronic access points to the ESP. Specifically, TRE_URE1 failed to demonstrate that it had reviewed and implemented the network management community strings on all identified electronic access points. Therefore, TRE_URE1 had an issue with CIP-005-1 R4.4 from the date the requirement became enforceable for TRE_URE1, through the date that all mitigating activity was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). The risk to reliability of the BPS was mitigated because while TRE_URE1 did not complete a review of controls for network management community strings, TRE_URE1’s infrastructure is protected from penetration by various layers of protection that include: firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and electronic security perimeter and physical security perimeter access authentication. Texas RE determined that the instant issue is appropriate for FFT treatment because although TRE_URE1 has prior CIP violations, they were self-reported and occurred concurrently with the instant issue. | To mitigate this issue, TRE_URE1: 1) provided evidence that a complete CVA was performed; 2) offered supporting documentation; and 3) the CVA process was updated to remind the tester to retain all evidence of test results as a part of the CVA documentation. Texas RE has verified completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXX | TRE2013012122 | CIP-002-2 | R4 | On March 13, 2013, TRE_URE2 submitted a Self-Report to Texas RE, stating that it had an issue with CIP-002-2 R4. Specifically, TRE_URE2 did not have a senior manager or delegate sign its risk-based assessment methodology (RBAM), its list of Critical Assets, and its list of null Critical Cyber Assets (CCAs). TRE_URE2 designated one person as the senior manager. TRE_URE2’s plant manager, instead of the designated person, signed TRE_URE2’s RBAM, its list of Critical Assets, and its list of null CCAs. The plant manager had not been designated as a senior manager or delegate. TRE_URE2 designated a third person as the senior manager and the newly designated person signed and approved TRE_URE2’s RBAM, its list of Critical Assets, and its list of null CCAs. TRE_URE2 had an issue with CIP-002-2 R4 from the date the undesignated person signed the documents to the date the newly designated person signed and approved TRE_URE2's RBAM, its list of Critical Assets, and its list of null CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the plant manager signed the documents until the time the senior manager signed them TRE_URE2’s methodology did not change. Moreover, TRE_URE2 did not previously have any CCAs and does not currently have any CCAs. Texas RE determined that the instant issue is appropriate for FFT treatment because it occurred around the time one TRE_URE2 affiliated company had an issue with CIP-002-1 R4, and thus is not considered a repeat violation. Also, the circumstances of the two instances of noncompliance are different. | To mitigate this issue, TRE_URE2: 1) correctly designated a senior manager; and 2) had the correctly designated senior manager sign the RBAM, its list of Critical Assets, and its list of null CCAs. To prevent re-occurrence, TRE_URE2 assigned compliance responsibility to in-house personnel rather than an outside consultant. TRE_URE2 hired a director of reliability process and compliance to improve its compliance program. TRE_URE2 updated and refined its compliance procedures for the applicable NERC standards and approving the RBAM. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXX | TRE2013012083 | CIP-002-2 | R4 | TRE_URE3 submitted a Self-Report to Texas RE stating that it had an issue with CIP-002-2 R4. Specifically, TRE_URE3 did not have a senior manager or delegate sign its risk-based assessment methodology (RBAM), its list of Critical Assets, and its list of null CCAs. TRE_URE3 designated one person as the senior manager. TRE_URE3’s plant manager, instead of the designated person, signed TRE_URE3’s RBAM, its list of Critical Assets, and its list of null CCAs. TRE_URE3’s plant manager had not been designated as a senior manager or delegate. TRE_URE3 designated a third person as the senior manager. TRE_URE3 had an issue with CIP-002-2 R4 from the date the undesignated person signed the documents to when the newly designated person signed and approved TRE_URE3’s RBAM, its list of Critical Assets, and its list of null CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the plant manager signed the RBAM, until the time the official delegate signed it, TRE_URE3’s methodology did not change. Moreover, TRE_URE3 did not have any CCAs and does not currently have any CCAs. Texas RE determined that the instant issue is appropriate for FFT treatment because it occurred around the time one TRE_URE2 affiliated company had an issue with CIP-002-1 R4, and thus is not considered a repeat violation. Also, the circumstances of the two instances of noncompliance are different. | To mitigate this issue, TRE_URE3: 1) correctly designated a senior manager; and 2) had the correctly designated senior manager sign the RBAM, its list of Critical Assets, and its list of null CCAs. To prevent re-occurrence TRE_URE3 assigned compliance responsibility to in-house personnel rather than an outside consultant, TRE_URE3 a director of reliability process and compliance to improve its compliance program. TRE_URE3 updated and refined its compliance procedures for the applicable NERC standards and approving the RBAM. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXX | TRE201100555 | CIP-004-3 | R4; R4.1 | Following a Compliance Audit, Texas RE determined that TRE_URE4 completed quarterly reviews and maintained documentation of personnel with access to Critical Cyber Assets (CCA) and of the associated access rights for each person. However, TRE_URE4 failed to update the CCA list within seven days of any change of personnel with such access to CCA. Specifically, Texas RE determined after a review of the unescorted physical access rights list, the access control procedures, and an internal disable access order, that TRE_URE4 failed to update its CCA physical access list within seven calendar days of a contractor’s CCA access rights being terminated, as required by R4.1. TRE_URE4 had an issue with CIP-004-3 R4.1 for one day, the date the change in the contractor’s physical access rights were recorded, which was eight days after his access rights were terminated. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated by the short violation duration period and TRE_URE4 evidencing that the contractor’s badge was surrendered to management on his last day of employment. PSP access now requires dual authentication; badging and pin number authentication. | To mitigate this issue TRE_URE4 removed the former contractor from its CCA access list. PSP access now requires dual authentication: badging and pin number authentication. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXX | TRE2012011442 | CIP-007-3a | R7; R7.2 | TRE_URE5 submitted a Self-Report to Texas RE stating that it had an issue with CIP-007-3a R7.2. Specifically, on TRE_URE5 redeployed a server analyst workstation without erasing the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. Rather than wiping the drive device with the prescribed tool of choice, the device was re-imaged with a standard analyst workstation image. TRE_URE5 duly erased the data storage media. The issue duration is from the date the server was placed into service, through the date the server drive was properly erased. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: a) the Cyber Asset remained within the Physical Security Perimeter (PSP) at all times; and b) though TRE_URE5 re-imaged the system instead of securely erasing the system as required, sophisticated and difficult forensic tool and techniques would be required to retrieve any potential data left on the machine. Texas RE determined that the instant issue is appropriate for FFT treatment because none of TRE_URE5’s prior CIP-007 violations involved disposal or redeployment of Cyber Assets. | To mitigate this issue, TRE_URE5: 1) purchased software to erase the data storage media; 2) erased the data storage media; and 3) documented the change control. Texas RE has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012408 | CIP-002-3 | R4 | WECC performed a Compliance Audit of WECC_URE1’s compliance with, among other Reliability Standards, CIP-002-3 R4. According to the WECC audit team, WECC_URE1 could not show evidence of compliance with this Standard for one calendar year. During the audit, WECC_URE1 provided copies of null lists of Critical Cyber Assets (CCAs) and Critical Assets, signed and dated by a senior manager. But WECC_URE1’s risk-based assessment methodology (RBAM) had not been signed or dated. WECC_URE1 did provide evidence of compliance with the Standard for the next calendar year and provided a signed RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 had correctly developed null lists of its Critical Assets and CCAs and its senior manager had signed and dated the lists. Based on these actions, WECC_URE1 did not expose any Critical Assets or CCAs to a potential threat. As a compensating measure, WECC_URE1 incorporated an approval signature block for the CIP senior manager as part of its RBAM review and approval process, and for use in future RBAM criteria documentation. | To mitigate this issue, WECC_URE1: 1) provided copies of its RBAM and null lists of Critical Assets and CCAs signed and dated by a senior manager; and 2) incorporated an approval signature block for the CIP senior manager as part of its RBAM review and approval process, and for use in future RBAM criteria documentation.