## PUBLIC_CIP_Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Neither Admits nor Denies" or "Does Not Contest"
FRCC | FRCC_URE1 | NCRXXXXX | FRCC201000381 | Settlement Agreement | The entity self-reported that its proprietary fiber network did not reside within an identified Physical Security Perimeter using completely enclosed "six wall" border as required by CIP-006-1 R1.1. The entity did not submit any technical feasibility exceptions (TFEs) and did not deploy and document alternative measures to control physical access to such Cyber Assets. | CIP-006-1 | 1.1 | Medium | High | FRCC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the fiber was and is privately owned by FRCC_URE1 and all data traffic on the fiber belonged to FRCC_URE1. Also, FRCC_URE1 did have circuit monitoring in place to detect physical intrusion of the fiber network. | 2010-04-01 | 2010-07-22 | $14,000 (Settlement of FRCC201000381, FRCC201000396, FRCC200900296, FRCC200900134, FRCC200900135) | Self-Report 7/14/10 | 1. Installed primary encrypted tunnel. 2. Installed firewalls. 3. Submitted TFEs. | 1. 6/25/10 2. 7/22/10 3. 7/29/10 | 1/25/11 (onsite) | Neither Admits nor Denies
FRCC | FRCC_URE1 | NCRXXXXX | FRCC201000396 | Settlement Agreement | The entity failed to document the assessment of a security patch for applicability within thirty calendar days of availability of the patch. Patch applicability assessment was completed in 35 days instead of the required 30 days. | CIP-007-2a | 3.1 | Lower | Lower | FRCC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the applicable patch was delayed by 5 days and was implemented in the appropriate implementation cycle. | 2010-07-16 | 2010-07-21 | $14,000 (Settlement of FRCC201000381, FRCC201000396, FRCC200900296, FRCC200900134, FRCC200900135) | Self-Report 9/24/10 | 1. Verified all patches have been evaluated. 2. Created monthly patch evaluation report. 3. Converted monthly patch evaluation report to bi-monthly. | 1. 8/16/10 2. 9/15/10 3. 8/1/10 | 1/25/11 (onsite) | Neither Admits nor Denies
FRCC | FRCC_URE1 | NCRXXXXX | FRCC200900296 | Settlement Agreement | The entity's documents were insufficient to demonstrate that it had cyber security test procedures (for workstations, databases, and applications) that minimize the adverse effects to existing security controls within its Electronic Security Perimeter. In addition, the entity's evidence was insufficient to demonstrate that it documented all of its test results. | CIP-007-1 | 1 | Medium | Lower | FRCC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because system testing was being performed for the functional requirements which included some security controls. | 2008-07-01 | 2009-05-29 | $14,000 (Settlement of FRCC201000381, FRCC201000396, FRCC200900296, FRCC200900134, FRCC200900135) | Spot-Check 12/04/09 | FRCC_URE1 tested its hardware and software assets by running policy reports through its testing software. The test results confirmed that changes to its system configurations did not compromise existing security measures. | 2009-05-29 | 1/20/10 (onsite) | Neither Admits nor Denies
FRCC | FRCC_URE1 | NCRXXXXX | FRCC200900134 | Settlement Agreement | The entity did not maintain sufficient evidence that training was performed within 90 days for 16 employees (out of 288) and 2 contractors (out of 8 contractors). | CIP-004-1 | 2 (2.1, 2.3) | Medium | Lower | FRCC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the identified employees were long-term employees with physical only access, and the contractors were either security guards or trusted vendors who had been vetted for their employment. | 2008-07-01 | 2009-01-27 | $14,000 (Settlement of FRCC201000381, FRCC201000396, FRCC200900296, FRCC200900134, FRCC200900135) | Self-Report 1/29/09 | 1. Reviewed records and revocation of access where appropriate. 2. New procedures became effective including a 10-day freeze on granting access rights. 3. New procedures to verify records of training and background checks prior to granting Critical Cyber Asset access and to track ongoing access rights for compliance with CIP requirements were communicated and implemented. 4. Monthly reviews of CCA access privileges. 5. Three months of reviews completed. 6. Six months of reviews completed. | 1.1/27/09 2.1/29/09 3. 1/29/09 4.3/10/09 5. 6/16/09 6. 9/8/09 | 1/25/11 (onsite) | Neither Admits nor Denies
FRCC | FRCC_URE1 | NCRXXXXX | FRCC200900135 | Settlement Agreement | The entity did not maintain sufficient evidence that Personnel Risk Assessments (PRAs) were performed for 16 employees (out of 288) and 4 contractors (out of 8). | CIP-004-1 | 3 | Medium | Moderate | FRCC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the identified employees were long-term employees with physical only access, the contractors were either security guards or trusted vendors who had been vetted for their employment. In addition the security guards maintained state level Personnel Risk Assessments. | 2008-07-01 | 2009-01-27 | $14,000 (Settlement of FRCC201000381, FRCC201000396, FRCC200900296, FRCC200900134, FRCC200900135) | Self-Report 1/29/09 | 1. Reviewed records and revocation of access where appropriate. 2. New procedures became effective including a 10-day freeze on granting access rights. 3. New procedures to verify records of training and background checks prior to granting Critical Cyber Asset access and to track ongoing access rights for compliance with CIP requirements were communicated and implemented. 4. Monthly reviews of Critical Cyber Asset access privileges were implemented. 5. Three months of reviews completed. 6. Six months of reviews completed. | 1.1/27/09 2.1/29/09 3. 1/29/09 4.3/10/09 5. 6/16/09 6. 9/8/09 | 1/25/11 (onsite) | Neither Admits nor Denies
NPCC | NPCC_URE1 | NCRXXXXX | NPCC201000214 | Settlement Agreement | On October 6, 2010, NPCC_URE1 reviewed access logs associated with a particular firewall (i.e. end point) at its back-up control center for unauthorized access to the back-up control center Electronic Security Perimeter (ESP). During the process of performing the access review on 10/6/10, NPCC_URE1 discovered that a violation of CIP-005-2 R3.2 had occurred as the previous manual access review associated with the firewall in question had occurred on 3/22/10. This amounted to a time span of 197 days and is in excess of the 90 calendar days allowed by R3.2. | CIP-005-2 | 3.2 | Medium | Severe | The violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The manual historical access review performed by NPCC_URE1 on 10/6/10 did not result in the discovery of any unauthorized attempts at access in the past 197 days to the back-up control center ESP via the firewall in question. Also, the firewall in question connects to a frame relay network and does not allow access to the Internet or the NPCC_URE1 corporate network. | 2010-06-21 | 2010-10-06 | 7500 | Self-Report | 1. NPCC_URE1 discussed the responsibilities of CIP-005-2 R3.2 with the persons directly responsible for compliance with the requirement to review or otherwise review access logs for attempts at or actual unauthorized accesses at least every 90 calendar days when 24x7 alerting is not technically feasible. 2. NPCC_URE1 initiated an immediate historical review of the access logs of the firewall in question at the back-up control center for unauthorized attempts at access and unauthorized actual access. 3. NPCC_URE1 directed completion of an in-progress capital project to provide continuous (24x7) alerting associated with this and several other firewalls. 4. NPCC_URE1 reviewed with the Network Communication and Planning Department and the Critical National Infrastructure Department their specific assigned responsibilities related to Standards CIP 002 – 009. It was agreed to meet quarterly as a group to review these requirements and report on progress. | 2010-12-09 | 2011-02-10 | Neither Admits Nor Denies
NPCC | NPCC_URE2 | NCRXXXXX | NPCC201000215 | Settlement Agreement | NPCC_URE2, as Generator Operator and Generator Owner, did not make its cyber security policy readily available to contractors with access to, or responsibility for Critical Cyber Assets. | CIP-003-1 | 1.2 | Lower | Severe | NPCC determined that the violation of CIP-003-1 R1.2 posed a minimal risk and did not create a serious or substantial risk to the reliability of the bulk power system (BPS) because the contractors successfully completed NPCC_URE2's CIP training. The training included the proper use of Critical Cyber Assets; physical and electronic access controls to Critical Cyber Assets; the proper handling of Critical Cyber Asset information; action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. In addition the contractors had to have a satisfactory documented Personnel Risk Assessment prior to access being granted | 2010-01-01 | 2010-09-30 | 5000 | Self-Report | NPCC_URE2 e-mailed a copy of its cyber security policy to each contractor with remote authorized cyber access. NPCC_URE2 placed a copy of the cyber security policy at a central location of each Critical Asset within the NPCC region and explained on the Physical Security Perimeters' sign-in, sign out log the availability of the cyber security policy. NPCC_URE2 updated the contractor eligibility process to include the process step to send the contractor the cyber security policy and copy the supervisor after the contractor becomes eligible for access. The contractor becomes eligible for access once he/she successfully meets the Personnel Risk Assessment and training requirements. | 2010-09-30 | 2011-04-19 | Does Not Contest
NPCC | NPCC_URE3 | NCRXXXXX | NPCC201100250 | NOCV | On January 1, 2010, the control systems for two NPCC_URE3 generating units were added by NPCC_URE3_Parent to the NPCC_URE3 Critical Cyber Asset (CCA) list. There were no technical feasibility exception (TFE) requests made associated with the control systems of either unit. The proper assessment, documentation, and installation of patches associated with both control systems were not performed as per CIP-007-3 R3 between 1/1/10 and 12/1/10. The control systems for both units are not connected to an outside network. The isolated nature of both control systems contributed to the difficulty of installing security patch updates and malware prevention software without the potential of introducing viruses. However, NPCC_URE3 did not make any TFE requests. The technological age of the control systems and inherent vendor support issues added to the difficulties. These difficulties led to a lack of proper assessment, updates, documentation, and installation relating to R3. | CIP-007-3 | 3 | Lower | Lower | The violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) as the control systems for both units utilized non-routable protocol during the entire timeframe. At no time, were they ever connected to a network. There was no actual impact to the BPS as the operation of both units were never effected due lack of patches performed or anti-virus software installed because a connection to a network was never made. | 2010-01-01 | 2010-12-01 | 0 | Self-Report | 1. On December 1, 2010, upon the completion of an internal assessment, the control systems for both units were removed from the CCA list. 2. On December 16, 2010, NPCC_URE3_Parent hired a full-time Regional CIP Engineer whose job description is to provide CIP guidance to the plant, which will include identifying situations that require TFEs. 3. On 1/20/11, training was completed for appropriate IT personnel on patching and anti-virus requirements associated with CIP-007. | 2011-01-20 | 2011-05-06 | Admits
NPCC | NPCC_URE3 | NCRXXXXX | NPCC201100251 | NOCV | On January 1, 2010, the control systems for NPCC_URE3_Parent's two NPCC_URE3 generating units were added to the NPCC_URE3 Critical Cyber Asset (CCA) list by NPCC_URE3_Parent. There were no technical feasibility exception (TFE) requests made associated with the control systems of either unit. NPCC_URE3 is a wholly owned subsidiary of NPCC_URE3_Parent. The proper assessment, documentation, and installation of patches associated with both control systems were not performed as per CIP-007-3 R3 between 1/1/10 and 12/1/10. The control systems for both units are not connected to an outside network. The isolated nature of both control systems contributed to the difficulty of installing security patch updates and malware prevention software without the potential of introducing viruses. However, NPCC_URE3 did not make any TFE requests. The technological age of the control systems and inherent vendor support issues added to the difficulties. These difficulties led to a lack of proper assessment, updates, documentation, and installation as required by R3. | CIP-007-3 | 4 | Lower | Severe | The violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) as the control systems for both units utilized non-routable protocol during the entire timeframe. At no time, were they ever connected to a network. There was no actual impact to the BPS as the operation of both units were never effected due lack of patches performed or anti-virus software installed because a connection to a network was never made. | 2010-01-01 | 2010-12-01 | 0 | Self-Report | 1. On December 1, 2010, upon the completion of an internal assessment, the control systems for both units were removed from the CCA list. 2. NPCC_URE3_Parent hired a full-time Regional CIP Engineer whose job description is to provide CIP guidance to the plant, which will include assisting appropriate plant personnel in identifying situations that require TFEs. 3. Training was completed for appropriate plant personnel on patching and anti-virus requirements associated with CIP-007. | 2011-01-20 | 2011-05-06 | Admits
MRO | MRO_URE1 | NCRXXXXX | MRO201100248 | NOCV | During a CIP Spot-Check of MRO_URE1 conducted July 26, 2010 through August 6, 2010, MRO determined that MRO_URE1 did not have controls in place to ensure that it was notified by its energy management system (EMS) vendor when individuals were terminated from the vendor's employ. MRO_URE1 was notified on June 30, 2010 that a member of the vendor’s staff supporting the MRO_URE1 EMS system had voluntarily terminated employment and his access had been revoked. On July 6, 2010 MRO_URE1 terminated this employee’s logical access to Critical Cyber Assets and updated its list of personnel with access to Critical Cyber Assets within seven calendar days as required. MRO_URE1 then learned that the vendor’s employee had voluntarily terminated employment on May 14, 2010, and the vendor failed to notify MRO_URE1 until June 30, 2010. | CIP-004-1 | R4.2 | Lower | Moderate | MRO determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because although MRO_URE1 did not revoke the individual's access within seven days of termination of employment, the EMS vendor revoked access to its facilities and revoked the individual’s remote logical access to MRO_URE1's EMS system from the vendor’s site. In order for the vendor’s employee to gain access to MRO_URE1’s Critical Cyber Assets, the employee must have access to a secured area, along with an authorized account on a workstation specifically used for supporting the MRO_URE1 EMS system. Without access to either the secure area or the specific workstation, the vendor’s employees are not able to gain logical access to the MRO_URE1 EMS system from outside of MRO_URE1's defined Electronic Security Perimeter. | 2008-07-01 | 2010-12-16 | 0 | Spot-Check | MRO_URE1 began e-mailing its EMS vendor every Monday to verify that the list of people with logical access to the MRO_URE1 EMS had not changed in the past seven days. The EMS vendor developed and implemented a secure web-based portal through which MRO_URE1 is able to access all of the information required by CIP-004-2 R2, R3 and R4. If the vendor’s employee is no longer a part of the MRO_URE1 EMS project team, voluntarily leaves the employment of the vendor, or is removed for cause by the vendor, as soon as the vendor revokes access at its site, an automatic e-mail is generated alerting MRO_URE1 personnel to revoke the logical access to the EMS system and update the list of authorized vendor employees. This secure web-based portal became operational on December 16, 2010. MRO_URE1 accesses this secure portal on a weekly basis and compares the list of the vendor’s names with its list of vendor personnel with logical access to MRO_URE1’s EMS. | 2010-12-16 | 2011-05-12 | Admits
MRO | MRO_URE2 | NCRXXXXX | MRO201100277 | NOCV | During a CIP Spot-Check of MRO_URE2 conducted December 6, 2010 through December 16, 2010, MRO determined that MRO_URE2 failed to update its Cyber Security Incident response plan to reflect a process for updating the plan within thirty calendar days of any changes as required by Reliability Standard CIP-008-2 R1.4. MRO_URE2's Cyber Security Incident response plan stated that updating would occur within 90 days as required by version 1 of the CIP Reliability Standards. The cause of the violation was an oversight during the annual review process. | CIP-008-2 | R1 | Lower | High | MRO determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because although MRO_URE2 failed to update its Cyber Security Incident response plan to reflect the 30 calendar day requirement, MRO_URE2 had a cyber incident response plan in place that: (1) provided procedures to characterize and classify events as reportable Cyber Security Incidents; (2) addressed response actions, including roles and responsibilities of incident response teams, incident handling procedures, and communication plans; (3) provided a process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center; and had a process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. Additionally, to date, MRO_URE2 has not had a Cyber Security Incident which would have required the use of the Cyber Security Incident response plan and supporting documentation. | 2010-04-01 | 2010-12-08 | 0 | Spot-Check | MRO_URE2 updated its Cyber Security Incident response plan to reflect the 30 calendar day requirement. | 2010-12-08 | 2011-06-07 | Admits
SERC | SERC_URE1 | NCRXXXXX | SERC201000716 | NOCV | On December 7, 2010, SERC_URE1, as a Load Serving Entity, self-reported to SERC a violation of CIP-002-1 R1 for failing to document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-002-1 | 1 | Medium | Severe | SERC finds that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in the proposed CIP-002-4; 2. SERC_URE1 performed a review of its assets and determined it did not have any Critical Assets, but it failed to document the RBAM as well as the application of the RBAM as required by the Standard; and 3. SERC_URE1 is a minimal size distribution utility with a peak load of 6 MW which serves 1,095 residential customers and 80 commercial consumers and does not own any BPS facilities. SERC_URE1 is only included on the NERC Compliance Registry because the interconnected Transmission Operator requires it to own and operate an underfrequency load shedding system. | 2009-12-31 | 2011-04-19 | 0 | Self-Report | SERC_URE1 developed a procedure establishing a written RBAM that identifies Critical Assets, Critical Cyber Assets (if any), and requires the annual review of its RBAM and list of Critical Assets and Critical Cyber Asset (if any). | 2011-04-19 | 2011-05-12 | Admits
SERC | SERC_URE1 | NCRXXXXX | SERC201000717 | NOCV | On December 7, 2010, SERC_URE1, as a Load Serving Entity, self-reported to SERC a violation of CIP-003-1 R2 for failing to assign a senior manager with overall responsibility and authority for leading and managing the entity’s adherence to Standards CIP-002 through CIP-009. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-003-1 | 2 | Lower | Severe | SERC finds that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE1 has no critical assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE1 had a senior manager tasked with the responsibility of approving the risk-based methodology, the list of Critical Assets, and the list of Critical Cyber Assets for the CIP-002 self-certifications however, SERC_URE1 had not formally designated and documented the senior manager with the specificity required by the Standard. | 2008-12-31 | 2011-02-07 | 0 | Self-Report | SERC_URE1 developed a formal written document that assigned the utility director as the senior manager with the responsibility for leading and for managing SERC_URE1’s adherence to Standards CIP-002 through CIP-009. The document (1) identifies the senior manager by name, title and date of designation; (2) requires that changes to senior management are documented within 30 days; (3) allows the senior manager to delegate specific actions to named delegates; and (4) requires the senior manager to authorize and document any exception from the requirements of the cyber protection policy. | 2011-02-07 | 2011-05-12 | Admits
SERC | SERC_URE2 | NCRXXXXX | SERC201000697 | NOCV | On November 23, 2010, SERC_URE2, as a Load Serving Entity, self-reported to SERC a violation of CIP-002-1 R1 for failing to document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-002-1 | 1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4; 2. SERC_URE2 performed a review and determined that it did not have any Critical Assets but failed to document its RBAM as well as its application of the RBAM as required by the Standard; and 3. SERC_URE2 is a minimal size distribution utility of 12 MW serving 2600 residential customers and 100 small to medium commercial consumers and meets no criteria for inclusion on the Compliance Registry other than the requirement by its Transmission Operator to own and operate an automatic underfrequency load shedding (UFLS) system. | 2009-12-31 | 2011-04-13 | 0 | Self-Report | SERC_URE2 developed a procedure establishing a written RBAM that identifies Critical Assets, Critical Cyber Assets (if any), and requires the annual review of its RBAM and list of Critical Assets and Critical Cyber Assets (if any). | 2011-04-13 | 2011-05-24 | Admits
SERC | SERC_URE2 | NCRXXXXX | SERC201000699 | NOCV | On November 23, 2010, SERC_URE2, as a Load Serving Entity, self-reported to SERC a violation of CIP-003-1 R2 for failing to assign a senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-003-1 | 2 | Lower | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE2 is a minimal size distribution utility of only 12 MW and meets no criteria for inclusion on the Compliance Registry other than the requirement by its Transmission Operator to own and operate an automatic underfrequency load shedding (UFLS) system; and 2. SERC_URE2 had a senior manager tasked with the responsibility of approving the risk based methodology, the list of critical assets, and the list of critical cyber assets for the CIP-002 self-certifications; however, SERC_URE2 had not formally designated and documented the senior manager with the specificity required by the Standard. | 2008-12-31 | 2011-01-29 | 0 | Self-Report | SERC_URE2 prepared a senior manager designation form that assigned a single manager with overall responsibility and authority for leading and managing SERC_URE2's adherence to CIP-002 through CIP-009. The form (1) identifies the senior manager by name, title and date of designation; (2) requires that changes to senior management are documented within 30 days; (3) allows the senior manager to delegate specific actions to named delegates; and (4) requires the senior manager to authorize and document any exception from the requirements of the cyber protection policy. | 2011-01-29 | 2011-03-15 | Admits
SERC | SERC_URE3 | NCRXXXXX | SERC201000719 | Notice of Confirmed Violation | On December 7, 2010, SERC_URE3, as a Load Serving Entity, self-reported to SERC a violation of CIP-002-1 R1 for failing to document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-002-1 | 1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4; 2. SERC_URE3 performed a review and determined that it did not have any Critical Assets, but failed to document its RBAM as well as the application of the RBAM as required by the Standard; and 3. SERC_URE3 is a minimal size distribution utility with a peak load of 5 MW which serves 1,132 residential customers and 136 commercial consumers and is included on the NERC Compliance Registry solely because its interconnected Transmission Operator requires it to own and operate an underfrequency load shedding system. | 2009-12-31 | 2011-04-22 | 0 | Self-Report | SERC_URE3 developed a procedure establishing a written RBAM that identifies Critical Assets, Critical Cyber Assets (if any), and requires the annual review of its RBAM and list of Critical Assets and Critical Cyber Assets (if any). | 2011-04-22 | 2011-05-24 | Admits
SERC | SERC_URE3 | NCRXXXXX | SERC201000721 | NOCV | On December 7, 2010, SERC_URE3, as a Load Serving Entity, self-reported to SERC a violation of CIP-003-1 R2 for failing to assign a senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. This violation also applies to Version 2 and Version 3 of the Standard since the duration of the violation spans the enforceable dates of each version. | CIP-003-1 | 2 | Lower | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in CIP-002-4; and 2. SERC_URE3 had a senior manager tasked with the responsibility of approving the risk based methodology, the list of critical assets, and the list of critical cyber assets for the CIP-002 self-certifications; however, SERC_URE3 had not formally designated and documented the senior manager with the specificity required by the Standard. | 2008-12-31 | 2011-02-11 | 0 | Self-Report | SERC_URE3 developed a formal written document that assigned the utility director as the senior manager with the responsibility for leading and for managing SERC_URE3’s adherence to Standards CIP-002 through CIP-009. The document (1) identifies the senior manager by name, title and date of designation; (2) requires that changes to senior management are documented within 30 days; (3) allows the senior manager to delegate specific actions to named delegates; and (4) requires the senior manager to authorize and document any exception from the requirements of the cyber protection policy. | 2011-02-11 | 2011-05-06 | Admits