## PUBLIC_CIP_VIOLATIONS
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007407 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-002-2 R1.2 for a failure to include a documented evaluation criterion associated with the seven types of assets specified in R1.2 of the corporate documented risk-based assessment methodology (RBAM) used to identify Critical Assets (CAs). NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-002-2 R1.2. | CIP-002-2 | R1.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the absence of written language specifically documenting the evaluation criterion could have resulted in improper identification of CAs or some CAs not being identified at all. The risk was mitigated by the fact that NPCC_URE1 attested that it was using CA evaluation criterion in verbal discussions and reviews of the outcomes of engineering studies. Also, the addition of the evaluation criterion to the RBAM did not change the list of facilities or equipment that was previously identified as CAs. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its RBAM and added the required evaluation criteria into the document and communicated the RBAM revisions to the relevant staff; 2. Conducted a review to determine which assets should be on the CA list based on the revised RBAM; 3. Established a team to review the necessary components that need to be specifically documented as evaluation criteria; and 4. Drafted and obtained approval for the documented evaluation criterion. | 2011-04-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007408 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-003-2 R5 for a failure to develop a program that fully addressed the management of access to protected Critical Cyber Asset (CCA) information. Specifically, NPCC_URE1 neglected to document the process for gaining access (physical and logical) to protected CCA information. As a result, the list required in R5.1 was not kept, the annual review required by R5.2 was not performed, and the annual assessment required by R5.3 was not performed. NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-003-2 R5. | CIP-003-2 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because failure to manage the access to CCAs information could lead to security gaps and unauthorized individuals gaining access to this information. The risk was mitigated by the fact that the CCA information was securely stored, and only personnel with authorized physical or logical access were able to access the information. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Documented a list of managers who are responsible for authorizing access to protected information for NPCC_URE1's employees and contractors; 2. Made a revision to the procedure that documents the process for the designated managers to authorize access to protected information for NPCC_URE1's employees and contractors; 3. Provided cybersecurity training to the employees and contractors that have access to CCA information; and 4. Communicated the revision of the NPCC_URE1 procedure that documents the requirements for authorizing access to protected CCA information to all relevant personnel. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007409 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-004-2 R4 for a failure to maintain a list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). NPCC_URE1 discovered the violation during an internal review. The review revealed that NPCC_URE1's facility quarterly access reports were not consistent from quarter to quarter but did not contain an explanation of the changes. In addition, NPCC_URE1's access reports did not contain detailed electronic rights, as required by this Standard. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-004-2 R4. | CIP-004-2 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to maintain a list of personnel with access to CCAs could lead to security gaps and unauthorized individuals gaining access to CCAs. The risk was further mitigated by the fact that NPCC_URE1 had physical access control, electronic access control, and electronic alerting procedures already in place. Also, all individuals at issue had completed cybersecurity training and had a personnel risk assessment. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Performed a detailed review of individual physical access rights and individual electronic access rights; 2. Created and revised an access tracking matrix. Also, an access authorization form was created to be used by management in assigning physical and electronic access and ensure uniformity and consistency; 3. Revised the corporate document that describes how physical and electronic rights will be granted and tracked. The corporate document refers to the revised access authorization form as an appendix; and 4. Communicated to all relevant personnel the revised corporate procedure and expected actions. | 2011-09-30 | 2012-02-17 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007410 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-005-2 R1.5 for a failure to protect fully a Cyber Asset (CA) used in the access control and/or monitoring of a Electronic Security Perimeter (ESP), as required in R1.5. The CA was a remote server that monitored electronic access. NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-005-2 R1.5. | CIP-005-2 | R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to afford all required protective measures to the CAs could lead to security gaps and unauthorized individuals gaining access to the CAs and ESPs. The risk was mitigated by the fact that the devices at issue were located on a secure network logically protected by strict firewall access control lists. Further, physical access to the CAs was restricted with key card access though the Physical Security Perimeter (PSP). | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Removed from service and replaced the not fully protected remote server that monitored electronic access with a server that is within the ESP and within a defined PSP; 2. Made a revision to its procedures to include assets involved in access control and/or monitoring in its cyber program; and 3. Reviewed its risk-based assessment methodology list which resulted in the removal of the CA from the list that was the subject of this violation. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007411 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R1 for a failure to create, implement, and maintain cybersecurity test procedures to perform testing for any of its Critical Cyber Assets (CCAs), its access control and monitoring devices, or its Cyber Assets (CAs). Although changes were tested using a test environment, they were not part of a documented process, and a "before and after" snapshot was not compared after the updates were put into production. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R1. | CIP-007-2a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to have documented procedure for testing its cybersecurity devices could lead to inconsistent testing and potential vulnerabilities of NPCC_URE1's system. The risk was mitigated by the fact that actual testing via the corporate change management procedure was being performed before and after CCA changes were made even without the existence of a written CCA testing process and written guidance on CCA records retention. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Established a series of actions for testing of security controls specific to categories of CAs; 2. Documented the security test procedure for each set of category of CAs; and 3. Communicated new security category specific security test procedures to all relevant staff. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007412 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R3 for a failure to track, evaluate, test and install applicable cybersecurity software patches to its CCAs, access control monitoring devices and other non-critical Cyber Assets devices within the Electronic Security Perimeter (ESP). Security patch activity and review had taken place only for the ESP access points. This violation was discovered during an internal audit. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R3. | CIP-007-2a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to track, evaluate, test and install security patches could lead to cyber vulnerability of the devices at issue. The risk was mitigated by the fact that the devices were located within the ESP. Further, intrusion detection and security logging measures were already in place for all assets. Finally, patches of a certain type have been evaluated as part of a general practice for NPCC_URE1. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Determined which equipment within the ESP needed security patch testing and determined whether there were patches available for installation on this equipment; 2. Performed testing on the patches for installation; 3. Installed the security patches after testing was completed; 4. Updated all relevant documentation to address the requirements of this Standard; and 5. Communicated updates to all relevant staff. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007413 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R4.2 for the failure to document and implement a process for the update of anti-virus and malware prevention “signatures,” along with failing to address testing and installing the signatures. Additionally, the signature files associated with anti-virus/ malware updates were not tested prior to installation on Cyber Assets within the Electronic Security Perimeter (ESP). After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R4. | CIP-007-2a | R4.2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a possible errant signature update could potentially cause a system to behave abnormally or have serious availability issues. The risk was mitigated by the fact that NPCC_URE1 had implemented intrusion detection systems, security logging, cyber and physical access control and a defense-in-depth network design. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Determined the environment needed to test signature files prior to installation of equipment in ESPs; 2. Built the environment where anti-virus software and malware prevention updates could be tested; 3. Updated the documentation relevant to this Standard; and 4. Notified staff engaged in managing Cyber Assets within the ESP of the changes and made them aware of the requirements. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007414 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R5 for a failure to establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. Specifically, NPCC_URE1 failed to implement its own documented password policy. NPCC_URE1 did not follow its own documented password management policy, which stated that passwords should be changed every 90 days. During an internal review, NPCC_URE1 discovered that passwords do not automatically expire and have not been changed since the Standard became mandatory and enforceable. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R5. | CIP-007-2a | R5 | Lower | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1's process requiring password changes every 90 days was more strict than the NERC CIP requirement calling for a password change once a year. NPCC_URE1 changed its password within one calendar year, thereby reducing the risk to the BPS to minimal. In addition, NPCC_URE1 had a written password policy, required appropriate password complexity, and its system locked accounts out after invalid login attempts. | 90 days after this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its account management procedure to document its password management process to state that it must be done annually as required by R5; 2. Verified that all passwords associated with network equipment and Critical Cyber Assets were reset; and 3. Communicated the revisions to the password management process to relevant staff. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007417 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R1 for a failure to ensure that its physical security plan addressed at a minimum the requirements detailed in R1.1 through R1.8. NPCC_URE1 reported that the plan was not drafted to fully address the physical security practices NPCC_URE1 had implemented. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R1. | CIP-006-2 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 had the required physical security controls in place but failed to properly document these controls as required by CIP-006-2 R1. NPCC_URE1 had all Physical Security Perimeter (PSP) entry points documented and had measures to control access at these points (personnel risk assessments, cybersecurity training for the personnel with access, swipe card). Further, alarms were installed to facilitate monitoring the PSPs. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its corporate physical security procedure to address CIP-006 R1.1 through R1.8; and 2. Trained all personnel on the procedure changes. | 2011-09-22 | 2011-10-14 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007427 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R3 by not having a remote server associated with the monitoring of electronic access to Critical Assets (CAs) inside of a defined Physical Security Perimeter (PSP). After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R3. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because there were existing physical access control procedures in place at the NPCC_URE1 facility that housed the server at issue. These control procedures included: physical access control procedure at the corporate building, personnel risk assessment and cybersecurity training completed for personnel, swipe cards required to gain access to the server that resided within the PSP. Furthermore, the server was used for monitoring electronic access only, not granting or changing access, which further reduced the risk to the BPS. | when the server at issue was moved from a secure PSP at another company site and became unsecure at this point | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. The remote server that monitored electronic access was removed from service and replaced with a local server that monitors electronic access at the CA; 2. The new server is within the Electronic Security Perimeter (ESP) of the CA and within a defined PSP; and 3. All documentation relevant to this Standard was updated, and the staff engaged in managing Cyber Assets within the PSP was notified of the changes and made aware of the requirements. | 2011-11-30 | 2012-02-17 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007428 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R8 by not having a written maintenance and testing program to ensure that all physical security systems under Standard CIP-006-1 R4, R5 and R6, function properly. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R8. | CIP-006-2 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because under NPCC_URE1's vendor's recommendations, NPCC_URE1 would not have been required to perform testing and maintenance of all physical security mechanisms during the pendency of the violation. NPCC_URE1's vendor has recommended a three-year cycle of maintenance from the date of NPCC_URE1's registration. NPCC_URE1 discovered the violation and completed all mitigating activities within three years and eleven days, thereby reducing the risk to the BPS to minimal. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. The recommended maintenance and testing protocols were obtained from the security system vendor; 2. The existing physical security procedure was revised to include the maintenance and testing protocols received from the security system vendor; and 3. Communicated to relevant staff the revisions of the physical security procedure. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000367 | Settlement Agreement | RFC_URE1 self-reported to ReliabilityFirst noncompliance with CIP-006-1 R1.1. Within the Self-Report, RFC_URE1 identified 11 user interfaces listed on its Critical Cyber Asset (CCA) list that were not designated as being located in a Physical Security Perimeter (PSP) in the physical security plan. These 11 CCAs were completely enclosed in a “six-wall” border; however, RFC_URE1 did not identify this area as a PSP in its physical security plan. Therefore, ReliabilityFirst determined that RFC_URE1 failed to document in the physical security plan that all Cyber Assets within an Electronic Security Perimeter (ESP) also reside within an identified PSP, as required by CIP-006-1 R1.1. | CIP-006-1 | R1.1 | Medium | High | ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The 11 identified CCAs were in a completely enclosed “six-wall” border. In addition, the 11 CCAs were physically located on the ground floor of RFC_URE1’s control center and in an ESP. Physical access to the control center was restricted by badge card readers, monitored by cameras and logged. Cyber events on the identified user interfaces were monitored by a security information and event management software and the CCAs were monitored for unauthorized changes. Visitors to the control center were logged and escorted. Finally, physical access to these devices was restricted to only those personnel who had undergone required personnel risk assessments (PRAs) and received appropriate security training. Therefore, RFC_URE1 had other mechanisms in place to provide physical protection to Cyber Assets, particularly the 11 user interfaces. | when RFC_URE1 was required to comply with CIP-006-1 R1.1 | Mitigation Plan completion | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) relocated the 11 CCAs to a defined PSP; (b) reviewed the physical security plan; (c) implemented a process for ensuring new Cyber Assets within the ESPs are also within PSPs; and (d) trained relevant personnel on these changes. | 2010-09-30 | 2011-01-18 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000624 | Settlement Agreement | RFC_URE1 self-reported to ReliabilityFirst noncompliance with CIP-004-1 R3.2. RFC_URE1 reported that it had not completed a personnel risk assessment (PRA) for two individuals within seven years of each individual’s previous PRA. Specifically, RFC_URE1 discovered that it calculated the interval for completing the seven-year PRA based on each individual’s hire date, rather than calculating the interval based upon the prior PRA completion date. Therefore, individuals completing their PRA before their date of hire did not undergo the seven-year updated PRA on time. As a result, RFC_URE1 did not update PRAs at least every seven years after the initial PRA for two individuals. This violation involves two instances and therefore the duration of the violation spans two periods of time. | CIP-004-1 | R3.2 | Lower | Moderate | ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Both individuals had previously undergone initial PRAs and had received annual security training. Supervisors and critical area owners recertified the access possessed by both individuals quarterly. Finally, RFC_URE1 completed the PRAs for both individuals shortly after their expiration and those PRAs resulted in no negative findings. The foregoing circumstances therefore reduced the potential risk from unauthorized personnel access to Critical Cyber Assets (CCAs). | 1st instance: when a PRA was due for the first individual 2nd instance: when a PRA was due for the second individual | 1st instance: when RFC_URE1 completed the first individual's PRA 2nd instance: when RFC_URE1 completed the second individual's PRA | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) completed the seven-year PRAs for the two identified individuals; (b) completed a review of all individuals with PRAs conducted during or before 2003; (c) updated the PRA tracking system; (d) revised internal processes for tracking and maintaining PRAs; (e) provided training on the revised CIP-004 PRA processes, policies and procedures to Human Resources (HR) staff; and (f) hired an outside consultant for an independent review of HR processes related to NERC CIP Standards. | 2011-04-29 | 2012-06-26 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as an aggravating factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100747 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-004-3 R2.1. RFC_URE1 identified three individuals, all of whom were contractors, who received physical access to two of RFC_URE1’s Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs) without first completing security training. | CIP-004-3 | R2.1 | Medium | Severe | ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The three individuals had personnel risk assessments (PRAs) completed prior to RFC_URE1 granting access, with no negative findings. Video cameras were present, operational and monitored at the two PSPs in question. Furthermore, two of the identified individuals only used their physical access badges at common areas. The third individual was never on-site at RFC_URE1, and therefore, never received his physical access badge and never entered a PSP. The foregoing circumstances therefore reduced the potential risk from unauthorized personnel access to CCAs. | when physical access was granted to all three individuals | when RFC_URE1 disabled this physical access for all three individuals | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) disabled the PSP access granted to the three identified individuals; (b) modified the operating procedure for account authorization to require security training prior to granting access to CCAs; (c) evaluated contractors to whom RFC_URE1 granted physical access in order to ensure that no additional contractors received PSP access without having completed all requirements; and (d) updated RFC_URE1’s physical security documentation. | 2011-02-28 | 2011-05-06 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as an aggravating factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100780 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-007-2a R3.1. RFC_URE1 reported that it had not documented the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades for three security patches and one security upgrade. Specifically, RFC_URE1 did not timely assess three security patches for one non-Critical Cyber Asset residing in one of RFC_URE1’s identified Electronic Security Perimeters (ESPs). Once assessed in accordance with RFC_URE1’s policy, RFC_URE1 determined two of those security patches to be applicable. In addition, RFC_URE1 did not timely assess one security upgrade for a storage device residing on RFC_URE1’s servers within RFC_URE1s ESP. These servers are non-Critical Cyber Assets within the ESP. This violation involves two instances and therefore the duration of the violation spans two periods of time. | CIP-007-2a | R3.1 | Lower | Severe | ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. All relevant assessments, while not conducted within the thirty days specified by the Standard, were conducted within a very short timeframe after they were due. Both the security patches and security upgrade were applicable to non-Critical Assets. Regarding the security patches, in the event of an attack, the attacker could only impact the one identified Cyber Asset by manipulating the operating system’s memory to affect the Cyber Asset’s performance and availability. The vulnerability could not be exploited to reach other Cyber Assets within the ESP. Therefore, the function of the identified Cyber Asset reduced the risk of vulnerabilities resulting from RFC_URE1’s failure to implement its process for security patch management. Further, the security upgrade for the storage device was assigned an internal residual risk rating of “low” by RFC_URE1’s assessment team and was designed to remediate a vulnerability that could only be exploited from within the RFC_URE1 network. The term “residual risk rating” refers to a rating assigned by RFC_URE1 security and technology subject matter experts. If the patch or upgrade is designated as applicable, RFC_URE1 assigns a risk rating of “high,” “medium” or “low,” depending on the circumstances. The vendor rating and the associated criteria used to develop this rating for each patch or upgrade is used as the starting point for determining the internal risk rating for RFC_URE1. Based on the results of the discussion, the RFC_URE1 assigns an internal risk rating for each security patch or security upgrade. In addition, the vulnerabilities remediated by the security upgrade could only be exploited from within the RFC_URE1 network by individuals who had access to the servers on which the software resided. All such individuals had authorized cyber access along with the appropriate personnel risk assessments, training and security awareness as prescribed by the requirements of CIP-004. The identified Cyber Asset was only available to personnel with appropriate clearance. As a result, the foregoing circumstances reduced the risk from potential exploitation of the Cyber Asset. | 1st instance: when the first security patch was due for assessment 2nd instance: when the upgrade was due for assessment | 1st instance: when RFC_URE1 completed the assessment of all three security patches 2nd instance: when RFC_URE1 completed the upgrade assessment | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) completed a documented assessment of the three security patches and one security upgrade; (b) removed the non-Critical Cyber Asset from the ESP; and (c) established, documented, implemented and communicated a procedural control to verify that all security patches and security upgrades have been identified for assessment. | 2011-07-29 | 2012-08-20 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as a neutral factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100822 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-005-1 R1. RFC_URE1 connected a dial-up modem to a Critical Cyber Asset (CCAs) residing in an Electronic Security Perimeter (ESP). The dial-up modem permits a hardware vendor to remotely access the hardware management console of this CCA. The CCA was an enterprise storage device used by two other CCAs. The hardware management console was used to perform system administration tasks for the enterprise storage device. The dial-up modem was configured for both dial-in and dial-out capability. The dial-out capability was used to communicate component failure and system degradation of the enterprise storage device to the hardware vendor, who would replace components and address degradation. The dial-in capability was used by the hardware vendor’s support team, who would remotely perform troubleshooting activities. RFC_URE1 did not document the dial-up modem as an access point to the ESP, as required by CIP-005-1 R1.1. | CIP-005-1 | R1 | Medium | Lower | ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The identified device was specifically designed for a third-party vendor’s remote access to the ESP. ReliabilityFirst did, however, consider that RFC_URE1 was unaware of this access point. The databases stored on the identified CCA are associated with the economic dispatch of the generation resources. If either or both databases are lost, then the economic dispatching of the generation could be compromised. However, this would not impact RFC_URE1’s ability to dispatch generation to support reliability of the transmission system. The risk to the reliability of the BPS was further mitigated by the controls in place to minimize remote access through the modem. As noted above, the modem allowed a hardware vendor to gain access to the hardware management console of one storage device. In order to utilize the dial-up modem for remote access, an individual requires an account, password, and unique key. A unique key is generated for each hardware management console and is stored in a secure database at the hardware vendor’s site. There are three accounts with varying levels of access that can be used to gain remote access. The passwords for these accounts are unique to each hardware management console and are changed every twenty-four hours. Data that is not stored on any enterprise storage device is not accessible via any of these accounts. ReliabilityFirst further considered that while RFC_URE1 data residing on the identified CCA is not accessible via these accounts, two of the accounts have the ability to affect the availability of the data hosted on this CCA. | when RFC_URE1 was required to comply with CIP-005-1 R1 | when the dial-up modem was documented as an access point to the ESP | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) documented the modem as an ESP access point; (b) reconfigured the modem to remove dial-up capability; (c) confirmed that there are no dial-up accessible Cyber Assets within existing ESPs; (d) implemented a procedural control to validate new Cyber Assets being added to the ESP are not dial-up accessible; and (e) reviewed and updated the quarterly modem discovery scan process. | 2011-06-09 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100864 | Settlement Agreement | RFC_URE1 submitted a Self-Certification identifying noncompliance with CIP-007-3 R2. RFC_URE1 established and documented multiple processes to ensure this requirement is met for the different types of Cyber Assets that reside within its Electronic Security Perimeters (ESPs). However, RFC_URE1 discovered that it did not implement certain components of its process for those Cyber Assets running a RFC_URE1 installation of two operating systems and those Cyber Assets categorized as storage devices. Thus, RFC_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled. | CIP-007-2a | R2 | Medium | Severe | ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Using a thorough review process, RFC_URE1 determined that the potential for a cyber attack via the identified ports and services was low given the security controls in place at the time of the violation. In particular, all of the ports and services disabled subsequent to the review could not have been accessed from outside of the ESP. In addition, immediately after discovery of this issue, RFC_URE1 performed a review of all ports and services enabled on those Cyber Assets within RFC_URE1’s ESPs running a RFC_URE1 installation of the two identified operating systems and those Cyber Assets categorized as storage devices. Ports and services not required for normal and emergency operations were disabled. | when RFC_URE1 was required to comply with CIP-007-2a R2 | when RFC_URE1 established, documented and implemented new processes for ensuring that only those ports and services required for normal and emergency operations are enabled | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Certification | RFC_URE1 performed a comprehensive review of all Cyber Assets, and disabled all ports and services that were not needed for normal or emergency operations. In addition, RFC_URE1 updated and published new procedures that govern the ports and services of the assets in question, and implemented more robust detection mechanisms to provide visibility into the status of the entire range where ports may be allocated. Last, training on the new procedures was completed. | 2011-08-19 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as a neutral factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100865 | Settlement Agreement | RFC_URE1 submitted a Self-Certification, identifying noncompliance with CIP-007-1 R6. The following month, RFC_URE1 submitted additional information regarding this violation of CIP-007-1 R6. Specifically, RFC_URE1 utilizes a security information and event management software, to comply with CIP-007-1R6. This software stores security audit log data from systems that are properly connected and provides alerting and monitoring capabilities to help identify unauthorized activity on RFC_URE1’s devices. RFC_URE1 identified Cyber Assets within its Electronic Security Perimeters (ESPs) that were not configured to send log data to the security information and event management software. These Cyber Assets provide the infrastructure data storage used by other Cyber Assets within RFC_URE1’s ESPs. As a result of RFC_URE1’s failure to configure these devices to send log data, these Cyber Assets did not have automated tools or organizational process controls to monitor system events related to cyber security. The violation involved 7.2% of the total assets at RFC_URE1. | CIP-007-1 | R6 | Lower | Moderate | ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Although RFC_URE1 had limited visibility to security incidents that may have occurred on these identified Cyber Assets, RFC_URE1’s infrastructure had additional layers of defense that provided some security and made these Cyber Assets visible to the security information and event management software for monitoring through other means. For example, RFC_URE1’s firewalls and other network devices send data to the security information and event management software, which monitors the network activity related to these Cyber Assets and sends alerts of suspicious events. In addition, RFC_URE1’s intrusion detection systems monitor network activity for these Cyber Assets and alert on suspicious events. Therefore, RFC_URE1 had other mechanisms in place to monitor system events that are related to cyber security, thereby reducing the risk to the BPS to moderate. | when RFC_URE1 was required to comply with CIP-007-1 | when RFC_URE1 ensured that all Assets within the ESPs were correctly configured and were sending data | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Certification | RFC_URE1 initially performed a reconciliation of its ESP Cyber Assets and the security information and event management software to determine Cyber Assets that were not sending audit log data. Based upon the results of that reconciliation, RFC_URE1 then correctly configured Cyber Assets that had been identified as not sending audit log data. Moreover, RFC_URE1 had previously created procedures to ensure that audit logging is implemented for deploying new Cyber Assets into ESPs and verified that appropriate procedures were in place to ensure that audit logging would be completed prospectively. RFC_URE1 also revalidated that all Cyber Assets were reporting to the software and implemented a monthly process to reconcile the list of Cyber Assets with those being monitored. Last, RFC_URE1 reviewed its need to document Technical Feasibility Exceptions for those Cyber Assets that remained in the ESP for which audit logs cannot be sent to the software, and found none. | 2011-12-15 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1's established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as a neutral factor.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100942 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-007-1 R5. RFC_URE1 identified five Cyber Assets residing within RFC_URE1’s Electronic Security Perimeters (ESPs) for which RFC_URE1 did not enforce the password criteria specified in CIP-007-1 R5.3. The Cyber Assets were storage devices, which are appliances that contain redundant and highly available sets of disks that are portioned out to various host operating systems. Each appliance has local accounts used to manage the appliance. Each appliance contains local user accounts: 50% are system administrator accounts for RFC_URE1 staff, and 50% are default or system/service accounts. Specifically, for two default system accounts on each of the five Cyber Assets (for a total of ten accounts), RFC_URE1 did not enforce the minimum password length of six characters, as required by CIP-007-1 R5.3.1. For all accounts on each of the five identified Cyber Assets, RFC_URE1 did not require that each password consist of a combination of alpha, numeric and “special” characters, as required by CIP-007-1 R5.3.2. | CIP-007-1 | R5.3 | Lower | Moderate | ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the bulk power system was mitigated by the following factors. The appliances impacted one of RFC_URE1’s systems which governs the economic dispatch of generation resources. Reliability impacts that could have resulted from the misuse of the system would have been mitigated by an operator’s ability to utilize its manual dispatch capabilities in response to any perceived data anomalies. Moreover, RFC_URE1 reviewed all of its emergency service tickets during the period of the violation to determine whether there was an adverse impact to the availability of these systems. These types of tickets are opened when an ongoing operational issue is identified and occurs for more than 30 minutes. RFC_URE1 determined that one ticket was created for the identified system; however, upon in-depth review, it was determined that this identified issue was not related to the storage appliance. | when the devices were added to the ESP | when RFC_URE1 enforced the password composition criteria of CIP-007-3-1 R5.3 for each of the Cyber Assets residing within RFC_URE1's ESPs | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) enforced the password composition criteria of CIP-007 R5.3; (b) implemented a procedural control to verify compliance; (c) performed a compliance review of all storage devices within the ESP to verify compliance with CIP-0070 R5.3; (d) reviewed and updated documentation to include the new procedural control; and (e) communicated the new procedural control to relevant staff. | 2011-06-29 | 2012-06-26 | Neither Admits nor Denies | ReliabilityFirst considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. ReliabilityFirst also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. ReliabilityFirst considered the violation history of RFC_URE1 as a neutral factor.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000376 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-003-1 R5. SPP RE_URE1 failed to document and implement a program for managing access to protected Critical Cyber Asset (CCA) information until 17 months after the compliance enforcement date of the Standard. Although SPP RE_URE1 did have some documented procedures for managing access to CCA information, its procedures did not address all the requirements of this Standard. Specifically, SPP RE_URE1 did have documented procedures to limit access to CCAs and CCA information to those with cleared background checks and did review the access list quarterly. SPP RE_URE1’s cybersecurity policies did address information owners and made them responsible for protecting that information. It also stated that access to information must be made in accordance with job responsibilities. As part of the annual review of the cybersecurity plan documents, this information protection section would have also been reviewed. However, SPP RE_URE1 failed to maintain a list of designated personnel consistent with the requirements of R5.1, as well as failed to confirm that access privileges were correct and that they corresponded with SPP RE_URE1's needs and appropriate personnel roles and responsibilities, as required by R.5.2. In addition, SPP RE_URE1 had protective measures in place to protect CCA information from unauthorized access, but SPP RE_URE1 did not assess and document at least annually the processes for controlling access privileges to protected information, as required by R5.3. | CIP-003-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE1 did have documented procedures to identify and classify CCAs, although SPP RE_URE1 did not address all the requirements of the Standard. SPP RE_URE1 stored CCA information on a restricted site and limited access file shares. SPP RE_URE1 had some documented procedures to manage access to the CCA information, including limiting access to CCAs and CCA information to only those with cleared background checks and quarterly reviews of access lists. Moreover, SPP RE_URE1 had protective measures to protect CCA information from unauthorized access, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | when SPP RE_URE1 documented and implemented its CCA information protection program | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 documented and implemented a CCA information protection program. Additionally, SPP RE_URE1 trained affected personnel on the program. As part of the program, SPP RE_URE1 implemented steps to identify, classify and protect information associated with CCAs. SPP RE_URE1 implemented a program for its document management site security and permission management for protected information. | 2011-02-25 | 2011-03-22 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000378 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-005-1 R3. SPP RE_URE1 failed to implement and document an electronic or manual process for monitoring and logging access at access points to the Electronic Security Perimeter (ESP) twenty-four hours a day, seven days a week. Specifically, at the time of the violation, all devices defined as access points to SPP RE_URE1’s ESP were configured to log security-related events to a central logging tool. While SPP RE_URE1’s security monitoring system was incapable of alerting for attempts at or actual unauthorized accesses, SPP RE_URE1 periodically (at least monthly) manually monitored for unauthorized access attempts. However, because the logs were backed up on tapes, the logs were not easily retrievable; therefore, not all relevant historical logs were reviewed at least every ninety calendar days. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because failure to implement an electronic or manual process for monitoring and logging access at access points presented a risk of SPP RE_URE1 not being aware of unauthorized attempts and/or access into SPP RE_URE1’s ESP. SPP RE_URE1 did, however, have protective measures in place to protect Critical Cyber Assets (CCAs), including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | when SPP RE_URE1 implemented and documented its process for monitoring and logging access at access points to its ESP | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 implemented and documented an electronic process for monitoring and logging access at access points to its ESP twenty-four hours a day, seven days a week. SPP RE_URE1 also installed and tested firewalls at all access points to its ESP; the firewall configurations were hardened to strengthen the security of its servers. Additionally, SPP RE_URE1 configured the firewalls to monitor and log all access points to the ESP twenty-four hours a day, seven days a week, and verified that the monitoring system is capable of detecting and alerting attempts at or actual unauthorized access to the appropriate designated response personnel. | 2011-06-30 | 2011-11-15 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000379 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-005-1 R4. Although SPP RE_URE1 had a documented process for performing cyber vulnerability assessments (CVAs) of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), it did not have a documented process for performing CVAs of access points to the ESP, as required by CIP-005-1 R4.1. Additionally, because no baseline of its ports and services had been conducted, SPP RE_URE1 was unable to ensure that only ports and services required for operations at access points to the ESP were enabled, as required by R4.2. Further, while SPP RE_URE1 conducted CVAs, SPP RE_URE1 did not have a documented process for discovering all access points to the ESP, as required by R4.3. Lastly, although action plans to remediate vulnerabilities identified in the assessment were created, SPP RE_URE1 was unable to provide documentation that such remediation had been executed, as required by R4.5. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE1's failure to have a sufficient process for conducting CVAs of access points to the ESP could have led to unauthorized access. This risk was mitigated by the fact that although the required documented review process was not in place, SPP RE_URE1 did conduct CVAs. Additionally, the affected CAs and Critical Cyber Assets (CCAs) were within SPP RE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 performed its annual CVA of the access points to its ESP and developed an action plan to remediate the vulnerabilities found. Additionally, SPP RE_URE1 developed a comprehensive CVA process, which requires an annual review of ports and services required for operations at access points to the ESP; a review of ports and services required for operations of access points; discovery of all access points to the ESP; and a review of controls for default accounts, passwords and network management community strings. The CVA process requires documentation of the results of the assessments, remediation plans to address vulnerabilities discovered in the assessments and execution status of the plans. To prevent recurrence of the violation, SPP RE_URE1 installed firewalls at access points to the ESP to reduce the risk of vulnerabilities to CAs within the ESP. Moreover, SPP RE_URE1 installed into the firewalls an advanced inspection and prevention security services card and an intrusion protection and intrusion prevention system card to further reduce the risk of vulnerabilities. | 2011-08-31 | 2011-11-15 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000383 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R2. SPP RE_URE1 did not establish a documented process for ensuring that only those ports and services required for normal and emergency operations were enabled, as required by R2. Although SPP RE_URE1 conducted a baseline for some devices, it did not conduct a baseline of ports and services to ensure that only ports and services required for normal and emergency operations were enabled, as required by R2.1. Further, SPP RE_URE1 was unable to provide documentation that it disabled other ports and services not required for normal and emergency operations prior to production use of all Cyber Assets (CAs) inside the Electronic Security Perimeter (ESP), as required by R2.2. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because undocumented port configurations presented a risk of incorrect configurations and port vulnerability, port failure, or port inaccessibility in certain situations. Failure to ensure properly designated ports and services were disabled prior to production use of Critical Cyber Assets (CCAs) within the ESP could have led to ports or services failure and/or unauthorized access to CCAs. Failure to review baseline documents resulted in a failure to ensure their continued integrity. However, the risk posed by SPP RE_URE1’s noncompliance was lessened because the affected CAs and CCAs were within SPP RE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 implemented a documented process to ensure that only ports and services required for normal and emergency operations are enabled. SPP RE_URE1 also purchased a quality assurance system for the new software system to provide a test environment to determine a baseline for ports and services within the system’s environment. SPP RE_URE1 performed vulnerability assessments and ran port scans on workstations to develop a baseline and compare the baseline to scans after system changes. SPP RE_URE1 replaced the previous access points, which were switches, with firewalls and hardened the configuration of those firewalls to only enable the required ports and services. SPP RE_URE1 installed new software into the firewalls to further protect its CAs within the ESP. The software’s intrusion prevention capabilities significantly enhance firewall protection by blocking threats and network attacks including worms, Trojans, viruses, and attacks against operating system and application vulnerabilities. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000384 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R3. SPP RE_URE1 failed to implement a documented security patch management program for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). Additionally, although SPP RE_URE1 documented that it tracked, assessed and implemented security patches and upgrades to some of its servers within its ESP, SPP RE_URE1 was unable to provide such documentation for all servers within the ESP. Further, some of the security patches and upgrades that were tracked and evaluated were not done within thirty calendar days of their availability, as required by R3.1. Moreover, SPP RE_URE1’s documentation indicated that a few evaluated security patches were not installed and the documentation did not include compensating measures applied to mitigate risk exposure or an acceptance of risk, as required by R3.2. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to test and implement all available security patches or updates for CAs within the ESP presented a risk that out-of-date security patches could allow unauthorized electronic access and potential compromise to Critical Cyber Assets (CCAs) that support BPS reliability. However, SPP RE_URE1 did evaluate and implement some security patches and updates to some of its CAs within its ESP. Additionally, the risk posed by SPP RE_URE1’s noncompliance was lessened because the affected CAs and CCAs were within SPP RE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 implemented a documented security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches and upgrades for all CAs within its ESP. SPP RE_URE1 also replaced the previous access points (i.e., switches) to its ESP with firewalls. SPP RE_URE1 purchased and is using a quality assurance system and software to ensure testing and assessment of patches and upgrades prior to installation and to create applicable reports and assessments. SPP RE_URE1 also installed new software into the firewalls to further protect its CAs within the ESP. For instance, the software’s intrusion prevention capabilities greatly enhance firewall protection by blocking threats and network attacks including worms, Trojans, viruses, and attacks against operating system and application vulnerabilities. SPP RE_URE1 is now documenting all of its assessment of security patches and upgrades for applicability within thirty calendar days of their availability and has a documented process for situations in which patches were not installed for documenting compensating measures applied to mitigate risk exposure or an acceptance of risk. | 3/38/2011 | 2011-05-03 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000385 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R6. SPP RE_URE1 failed to implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), as required by R6.1. Additionally, not all CAs (e.g., servers, remote terminal units) within SPP RE_URE1’s ESP were capable of issuing automated or manual alerts for detected Cyber Security Incidents, as required by R6.2. | CIP-007-1 | R6; R6.1; R6.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to have processes to monitor system events related to cybersecurity presented a risk that SPP RE_URE1 would not have the ability to respond to critical security events, thereby placing Critical Cyber Assets (CCAs) at risk of being compromised. Although there was not a formal process in place, some of SPP RE_URE1’s CAs were being monitored, such as SCADA production workstations, including servers and remote terminal units. A system was used to monitor user log-on/off, success/failures and system errors for corporate servers and firewalls. It also monitored normal logs like sessions being built/torn down on the firewalls. SPP RE_URE1 also had protective measures in place to protect CAs and CCAs within its ESP, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 implemented and documented formal organizational processes and technical and procedural mechanisms for monitoring security events on all CAs within the ESP. SPP RE_URE1 worked with its energy management system (EMS)/SCADA vendor and installed a new security and compliance management automation system to monitor and alert cybersecurity events within the EMS environment twenty-four hours a day, seven days a week. SPP RE_URE1 also set up the new automated system into its quality assurance system so that testing of various configuration changes to the automated system can be made without impacting the EMS environment. All CAs within SPP RE_URE1’s ESP are now capable of issuing automated alerts for detected cybersecurity incidents. | 2011-06-30 | 2011-07-22 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000386 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R7. SPP RE_URE1 failed to establish formal methods, processes and procedures for both disposal and redeployment of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). | CIP-007-1 | R7 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because any obsolete or out-of-service CAs were stored securely within the ESP. If any CAs would have needed to be disposed of or redeployed during the violation, device drives would have been removed and set aside in a secure environment to be wiped at a later date in bulk. SPP RE_URE1 has been removing drives from its computers since at least before the Standard became mandatory and enforceable, and wiping them using software rated for use by the Department of Defense, simply as good practice. Additionally, the affected CAs were within SPP RE_URE1’s ESP and were afforded some of the measures to protect Critical Cyber Assets (CCAs), including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 developed and formalized methods, processes and procedures for disposal and redeployment of CAs within its ESP to prevent unauthorized retrieval of sensitive cybersecurity or reliability data contained on media used within its ESP. All affected personnel have been trained on all such methods, processes and procedures. | 2010-10-08 | 2011-01-13 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000387 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R8. SPP RE_URE1 had a documented process for its cyber vulnerability assessments (CVAs) of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), as required by R8.1; however, the process did not address all the requirements of the Standard. First, the documented process did not require the CVA to be performed annually, as required by R8. Additionally, although SPP RE_URE1 conducted CVAs of CAs within its ESP, SPP RE_URE1 did not have a test environment, and its documented process did not include a review and verification process to ensure that only ports and services required for operation of CAs within the ESP were enabled, as required by R8.2. SPP RE_URE1 did not conduct a baseline of ports and services to determine which ports and services needed to be enabled for operations of CAs within its ESP. Further, while reviews of controls for default accounts were conducted, SPP RE_URE1 failed to include these reviews in its documented CVA process, as required by R8.3. In addition, SPP RE_URE1 confirmed that its CVAs may not have identified all vulnerabilities of such default accounts. Although remediation plans to address discovered vulnerabilities from the assessments were created, SPP RE_URE1 was unable to produce documentation to show that it executed the remediation plans, as required by R8.4, since its documented CVA process did not include a process for doing so. | CIP-007-1 | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to perform complete CVAs may have led to a failure to identify all systems or components at risk and mitigation of any known vulnerabilities, which could have placed CAs within the ESP and the BPS at risk. Although not all of the required documented review processes were in place, SPP RE_URE1 did conduct CVAs. Additionally, the affected CAs were within SPP RE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 developed a comprehensive CVA process, including an annual policy review provision and performed a CVA using the new procedures. The policy now requires a baseline of ports and services; a review to ensure that only ports and services required for operations of CAs within the ESP are enabled; a review of controls for default accounts; documentation of the results of the CVAs; remediation plans to address vulnerabilities discovered in the assessments; and execution status of the plans. To prevent recurrence of the violation and to further reduce the risk of vulnerabilities, SPP RE_URE1 installed firewalls at access points to the ESP. SPP RE_URE1 also installed into the firewalls an advanced inspection and prevention security services card and an intrusion protection and intrusion prevention system card. SPP RE_URE1 provided documentation demonstrating adherence to its implemented CVA process. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000388 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-007-1 R9. SPP RE_URE1 failed to conduct an annual review of the documents and procedures it maintains pursuant to CIP-007. Additionally, SPP RE_URE1 failed to document changes resulting from modifications to the systems or controls within 90 days of such changes. | CIP-007-1 | R9 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to conduct the required documentation review and maintenance presented a risk that SPP RE_URE1 would not sufficiently assess vulnerabilities to Critical Cyber Assets (CCAs) and Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). However, SPP RE_URE1 did have documented and informal procedures for compliance with some of CIP-007. For example, SPP RE_URE1 conducted baseline testing of ports and services for some of its devices; documented, tracked, assessed, and implemented security patches and upgrades to some of its servers within the ESP; and had a documented process for its cyber vulnerability assessments, even though it did not address all of the requirements of the Standard. Additionally, SPP RE_URE1 had protective measures in place to protect CAs and CCAs, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 revised its cyber security policy to include a provision specifically addressing CIP-007 R9 with language noting that SPP RE_URE1 will: (1) review and update the documentation specified in CIP-007 at least annually; and (2) document any changes resulting from modifications to the systems or controls within thirty calendar days from the date of such changes. SPP RE_URE1 also developed, documented and implemented a CIP-007 systems management process manual, which requires an annual review of the manual and provides specific procedures for documenting changes resulting from modifications to its systems or controls. Additionally, SPP RE_URE1 revised its vulnerability assessment process to provide more detailed procedures for conducting, reviewing, and documenting remediation and changes made to systems or controls. Lastly, SPP RE_URE1 provided attestations from all affected personnel that they are aware of and understand the new CIP-007 R9 policies and procedures. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201000389 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that was in violation of CIP-009-1 R4. Although SPP RE_URE1 had a recovery plan, its plan did not include processes and procedures for the backup and storage of information required to successfully restore its Critical Cyber Assets (CCAs). | CIP-009-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although SPP RE_URE1 failed to implement documented procedures, in practice, it was backing up and storing information that could successfully restore all of its CCAs. For instance, SPP RE_URE1's SCADA software automatically ran backups of its CCAs, and reports of such backups were regularly reviewed to ensure the backups were running as scheduled and that no errors were reported. Further, SPP RE_URE1 did have protective measures in place to protect CCAs, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPP RE_URE1’s network is isolated without Internet connectivity. Lastly, according to SPP RE_URE1, there have been no incidents requiring recovery of CCAs from a backup. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 revised its recovery plan processes and procedures to include the backup and storage of information required to successfully restore its CCAs. All affected personnel have been trained on the new processes and procedures. | 2011-02-23 | 2011-06-29 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP201100520 | Settlement Agreement | Pursuant to a Self-Certification by SPP RE_URE1, SPP RE determined that SPP RE_URE1 was in violation of CIP-006-1 R3. SPP RE_URE1 failed to fully implement its documented procedures to monitor physical access points to its Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. Specifically, SPP RE_URE1’s physical access security policies and procedures provide for camera observation of all access points to Critical Cyber Assets (CCAs), twenty-four hours a day, seven days a week. The policies and procedures also provide that SPP RE_URE1’s security system will monitor all access points to its PSP, twenty-four hours a day, seven days a week, and is capable of issuing an alarm, as well as an alarm summary report via security system consoles, to security department personnel for unauthorized access or access attempts of any access point to the PSP. Additionally, the policies and procedures require the security department personnel to review all alarms and alarm summary reports as part of their daily duties. Although camera surveillance was being conducted and SPP RE_URE1’s security system was capable of issuing alarms and alarm reports twenty-four hours a day, seven days a week to security department personnel for unauthorized access or access attempts at access points to the PSP, such human observation and notifications would be observed and immediately investigated only when security department personnel were on-site. Security department personnel were on-site during normal business hours and outside normal business hours. Consequently, SPP RE_URE1 did not fully implement its documented physical security policies and procedures to ensure that immediate notification of unauthorized access or access attempts was given to personnel responsible for investigating and responding to such security breaches, as required by CIP-006-1 R3. | CIP-006-1 | R3; R3.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although SPP RE_URE1 failed to fully implement its procedure as required, physical access points to its PSP were being monitored on a daily basis, and there were multiple layers of security measures in place to prevent unauthorized access to the PSP. During normal business hours, SPP RE_URE1’s CCAs had two layers of protection. For instance, once inside SPP RE_URE1’s main lobby, a badge was required to gain access to any area outside the lobby, which included all doors and hallways that led to access points to the PSP. If an intruder somehow had gotten past the first layer of protection, a badge and biometrics were required to gain access to the PSP. Thus, had there been a break-in during normal business hours, SPP RE_URE1 operators, who worked throughout areas beyond the lobby and within the PSP on a daily basis, most likely would have seen the intruder and would have investigated and/or called SPP RE_URE1’s security department prompting an immediate investigation. Even if an intruder had not been seen by an operator, the break-in would have triggered an alarm alerting SPP RE_URE1’s security department of an unauthorized access or access attempt, prompting an immediate investigation. Additionally, all access points to SPP RE_URE1’s PSP were under camera observation, which was recorded twenty-four hours a day, seven days a week, and monitored during normal business hours. Consequently, any malicious activity conducted during that time period would have been seen and immediately investigated by security department personnel. Outside normal business hours, the CCAs were protected by three layers of protection. For example, a badge and biometrics were required to gain access into the facility. Once inside the facility, the same two layers of protection indicated during normal business hours were in place to gain access to any of SPP RE_URE1’s CCAs. Furthermore, if an intruder somehow had gotten through all three layers of protection at times in which SPP RE_URE1 security department personnel were on-site after hours, the break-in would have triggered an alarm alerting them of an unauthorized access or access attempt, prompting an immediate investigation. Also, the security cameras were under human observation; therefore, any malicious activity conducted during that time period would have been seen and immediately investigated by security department personnel. Lastly, during the time period of the violation, there were no known break-ins into any of SPP RE_URE1’s PSPs. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPP RE_URE1 hired additional personnel to fully implement its documented physical access policies and procedures to ensure immediate review and response to unauthorized access or access attempts at all access points to its PSP. SPP RE_URE1 also revised its physical security policies and procedures to make it more clear as to what steps are to be taken and specific contact information should an issue arise. All affected personnel were trained on the revised policies and procedures. | 2011-09-29 | 2011-11-09 | Neither Admits nor Denies | SPP RE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPP RE_URE1's ICP to be a mitigating factor in the penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (Texas RE_URE1) | NCRXXXXX | TRE201100264 | Settlement Agreement | During a Compliance Audit, Texas RE found that Texas RE_URE1 was in violation of CIP-007-1 R2 because Texas RE_URE1's annual cyber vulnerability assessment (CVA) showed multiple logical ports/services that were enabled on Cyber Assets and printers within the Electronic Security Perimeter (ESP); however, these ports/services were not required for normal or emergency operations. The ports identified represent 0.3% of all ports identified during the CVA. The majority of the ports were associated with a message application running on a workstation that no longer was used to process, aggregate, or store messages. The remainder unnecessary port was associated with a system service that Texas RE_URE1 does not need for normal or emergency operations. | CIP-007-1 | R2; R2.1 | Medium | Lower | Texas RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had risk mitigating controls, policies, and procedures in place during the pendency of the violation, as follows: (a) A search of the National Vulnerability Database for vulnerabilities related to the services using the open ports revealed no reported vulnerabilities; (b) Texas RE_URE1 utilizes firewalls to filter incoming network traffic. Logs are reviewed weekly, at which time the unusual activity would have been noted and further investigated; (c) In addition to the network-based defenses of the firewalls and intrusion protection system (IPS), Texas RE_URE1 uses other defense-in-depth measures to protect assets from both known and undiscovered vulnerabilities. Texas RE_URE1 uses a white-listing anti-virus application on all servers and workstations that prevents the execution of applications that have not been previously authorized. It also detects when modified or unauthorized libraries are in-use in memory and blocks their execution. Daily scans of system files and configurations for changes help to detect both authorized and unauthorized system modifications. Also, network traffic from Texas RE_URE1 ESPs is not routable to the internet or on the private supervisory control and data acquisition (SCADA) network. Physical access to Texas RE_URE1 ESPs is protected by secured areas with limited access to reduce the number of personnel who have the opportunity to access devices; (d) Texas RE_URE1 uses a network IPS to monitor traffic entering the ESP and traffic within the ESP. The IPS vendor develops rules to detect the exploitation through network traffic of vulnerabilities that have been reported. Where vulnerabilities have been discovered, the new rules would have been imported during Texas RE_URE1's monthly signature update; (e) For the ports associated with the message application, any exploitation of unknown vulnerabilities (which would have needed to be performed from inside a Texas RE_URE1 ESP due to firewall rules) would most likely have affected only the unused application or, in the worst case, availability of the workstation running the software. Because the workstation running the application was designated for use in system support and not for system operations, even unexpected impacts to host availability would not have affected the BPS; (f) The last unnecessary port was associated with a system service that Texas RE_URE1 does not require for normal or emergency operations. Because Texas RE_URE1 applies patches monthly beginning nine days after the patch was released, any discovered vulnerabilities in the service using that port would have been patched shortly after being publicly acknowledged. The servers which are used for processing SCADA data and controls were not utilizing this unnecessary port, nor were the workstations used for monitoring and control of Texas RE_URE1 field assets; and (g) No breaches or other intrusions into Cyber Assets within Texas RE_URE1 ESPs have been identified during the time the undocumented and unnecessary ports were open. Similarly, no breaches or other intrusions were identified during the period the printer ports may have been open. | when the Standard became mandatory and enforceable for Texas RE_URE1 | when Texas RE_URE1 disabled the last unnecessary port | $17,000 (for TRE201100264 and TRE201100265) | Compliance Audit | Texas RE_URE1 updated its documentation to indicate that Technical Feasibility Exceptions (TFEs) must be filed when ports or services cannot be disabled. Texas RE_URE1 completed its action plan for the annual CVA. Upon completion, Texas RE_URE1 identified the ports required for normal/emergency operation, as well as the open ports that were not necessary for such operations. Texas RE_URE1 disabled the unnecessary ports/services. Texas RE_URE1 amended its procedures to include both stricter controls and assessments when determining which ports/services should be enabled. Texas RE_URE1’s change control process includes performing a full port scan on a representative of each asset class impacted by the change. With the change to the process to require association of dynamic port utilization discovered during the scan with a specific, authorized process, it is more likely changes adding new ports will be discovered during the testing of the change and evaluated before implementation of the change in the production environment. Texas RE_URE1 also configured change monitoring software to scan servers and workstations for additions, deletions, or modifications of services or their properties. This practice helps to support the change management process by easily identifying how changes being tested impact services and to identify when a host in production has changed. | 2012-01-26 | 2012-06-22 | Neither Admits nor Denies | Texas RE considered the presence and the quality of Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (Texas RE_URE1) | NCRXXXXX | TRE201100265 | Settlement Agreement | During a Compliance Audit, Texas RE found that Texas RE_URE1 was in violation of CIP-007-2a R3 because seven of the security patches evaluated during the audit period, and deemed required by Texas RE_URE1, had not been implemented in the production environment within 30 calendar days. Texas RE_URE1 also had not documented compensating measures for the security patches that had not been installed. | CIP-007-2a | R3; R3.1 and R3.2 | Lower | Severe | Texas RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had risk mitigating controls, policies, and procedures in place during the pendency of the violation, as follows: (a) Texas RE_URE1 receives indirect protection from its standard defense-in-depth security measures. Firewall rules deny traffic that does not meet predefined source, destination, and port criteria. Texas RE_URE1 uses a network intrusion protection system (IPS) to inspect traffic within the Electronic Security Perimeter (ESP) and from sources external to the ESP which can detect attempted exploitation of vulnerabilities from remote sources. White-list anti-virus software installed on servers and workstations prevents the modification of existing applications and libraries and prevents the execution of files not previously approved for use. The anti-virus software also can detect execution of unauthorized or modified libraries in memory and block their execution. Daily scans of system files and configurations for changes help to detect both authorized and unauthorized system modifications; (b) Also, network traffic from Texas RE_URE1 ESPs is not routable to the internet or corporate network, so communication with Texas RE_URE1 ESPs must be performed from within the ESP or on the private supervisory control and data acquisition network. Physical access to Texas RE_URE1 ESPs is protected by secured areas with limited access to reduce the number of personnel who have the opportunity to access devices; and (c) Of the seven outstanding security patches identified by Texas RE, one was determined not to be associated with security on further evaluation. A second patch did not provide release notes, making it difficult to determine if the patch was security-related. A search of the National Vulnerability Database revealed no known vulnerabilities, indicating the patch was likely not security-related. Of the remaining five patches known to affect security, two had vulnerability-specific mitigations in place that were documented by Texas RE_URE1 as general security protections. The remaining three patches that did not have complete vulnerability-specific mitigations in place were applicable to applications installed only on workstations, limiting the scope of potential impact. | the evaluation date of the oldest required security patch | Texas RE_URE1 documented compensating measures for all outstanding security patches | $17,000 (for TRE201100264 and TRE201100265) | Compliance Audit | Texas RE_URE1 installed the patches identified during the Compliance Audit. Texas RE_URE1 also documented mitigating measures on all other security patches that were not installed. Finally, Texas RE_URE1 revised its policies/procedures to reflect that, if for any reason, existing mitigating measures cannot be found for a security patch, either the patch or relevant risk mitigation measures should be implemented promptly. | 2011-11-04 | 2012-06-07 | Neither Admits nor Denies | Texas RE considered the presence and the quality of Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102850 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R2.1. Specifically, WECC_URE1 reported that several individuals did not have Critical Infrastructure Protection (CIP) training prior to being granted access to Critical Cyber Assets (CCAs). In addition, a number of employees had not received annual CIP training within the required timeframe, in violation of R2.3. WECC_URE1 utilizes a system to monitor and track physical access to all of its facilities, including its Physical Security Perimeters (PSPs). There are two root causes that have been identified with regard to this violation. The first root cause is a lack of in-house technical expertise with regard to the reporting features of the physical access control system. The second root cause is human error. Specifically, the physical access and cyber access lists are maintained by a manual process that includes the transferring of data from a source document to the lists which has resulted in data being entered incorrectly. WECC determined that WECC_URE1 is in violation of CIP-004-1 R2.1 and R2.3 for failing to administer CIP training to individuals within ninety days of being granted access to WECC_URE1's CCAs, and for failing to ensure that its employees received annual CIP training within the required time frame. | CIP-004-1 | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and PSPs. The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty-four hours a day, seven days a week, thereby reducing the risk to the BPS. | 90 days after the WECC_URE1 compliance date for this Standard, when CIP training should have been completed for personnel with access to CCAs | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Retained a technical expert from the physical access control system vendor who developed: a) A standard physical access control system report that will be used to consistently extract the physical access data from that system; b) An exception report to report out any missing data inconsistencies in dates and other such information so that data being entered into the physical access control system can be validated and tracked; and c) Procedures for WECC_URE1 personnel to follow when adding or removing access information into the physical access control system to ensure that continuous physical access dates can be determined. 2. Removed then reinstated, as appropriate, physical access for all PSP access points for all employees and contractors to reset the physical access dates for authorized employees identified. WECC_URE1 also validated the relationship between the physical access date and the training date for all employees and contractors to ensure compliance with the CIP-004-1 R2.3; and 3. Researched industry best practices with regard to the maintenance of the physical access and cyber access lists and developed procedures around those best practices to ensure compliance with this Standard. | 2011-02-26 | 2012-04-27 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002790 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that WECC_URE1 was in violation of CIP-004-1 R3. Specifically, WECC_URE1 reported that 1.56% of the total individuals with authorized logical and/or physical access to Critical Cyber Assets (CCAs) did not have personnel risk assessments (PRAs) that were completed within 30 days of being granted access to CCAs in accordance with WECC_URE1's policy requirements. WECC determined that WECC_URE1 was in violation of CIP-004-1 R3 because it did not conduct PRAs for individuals within 30 days of granting those individuals access to WECC_URE1's CCAs. | CIP-004-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the PRAs should have been completed for the individuals in scope | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Appointed a new subject matter expert and responsible employee to maintain the master CCA access lists and to oversee compliance with CIP-004-1 R3; 2. Verified the dates of completion of PRAs for employees, vendors and contract personnel with unescorted physical and/or cyber access to a CCA and revised the quarterly master access list using source documentation from a vendor utilized to conduct background checks; and 3. Documented a new PRA process in the WECC_URE1 policy document addressing CIP 004 R3. The new process document requires that the source files containing the PRAs will be used to verify the completion and dates of PRAs rather than tracking the information contained in the source files in a spreadsheet to help avoid incorrect data and human error in entering and/or extracting the data. | 2010-07-30 | 2012-04-27 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002791 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R3. Specifically, WECC_URE1 reported that 30.7% of the total individuals having access to Critical Cyber Assets (CCAs) were not properly documented on WECC_URE1's CCAs access list. The categorical breakdown of the individuals is as follows: 1) 9.5% of the individuals either were not updated on the CCA access list or did not have their access removed within seven days of CCA access being revoked; 2) 74.5% of the individuals had incorrect dates listed on the CCA access list for access; 3) 16% of the individuals were not on the CCAs access list when they should have been because they had access to CCAs; and 4) In addition, WECC_URE1 self-certified noncompliant with CIP-004 R4 stating that additional individuals had been discovered that had access to Critical Cyber Assets but were not properly documented on the CCA access list. WECC concluded that WECC_URE1 was in violation of CIP-004-1 R4 for failing to properly document WECC_URE1's CCAs access list for 31.3% of the total individuals who had access to WECC_URE1's CCAs. | CIP-004-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Assigned different personnel to maintain the (1) physical access list and (2) cyber access list, who have more extensive auditing and tracking backgrounds; 2. Developed new processes for auditing the physical access list and cyber access list that requires the use of source files containing access requests and approvals to verify the date of any access approval and the type of access approved for any particular individual. Additionally the source documentation was used to verify when access to any PSP or CCA was granting or removed for any particular individual; 3. Removed all information pertaining to access to sites that did not need to be included on the physical access list; and 4. Discontinued use of a single master access list to reduce manual entry of dates to that single file and to the physical access list and cyber access list which reduced the risk and opportunity for human error. | 2011-12-28 | 2012-07-18 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102793 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1.5. Specifically, WECC_URE1 failed to provide multiple protections for certain of its access control and monitoring (ACM) Cyber Assets that are associated with Electronic Security Perimeters (ESPs) for WECC_URE1. The protections in scope are as follows: 1) CIP-007 R3: For an 18-month period, WECC_URE1 did not assess security patches for three electronic ACM Cyber Assets as required by its program, which was developed to comply with CIP-007 R3. Additionally, WECC_URE1 reported that one security patch and one service pack were installed into production without testing on a server with an identical operating system. The server on which the patches were tested was running an older version of the operating system. The server on which the patches were tested was running an older version of the operating system. 2) CIP-004 R3: 107 individuals who had access to electronic ACM Cyber Assets did not have personnel risk assessments (PRAs). 3) CIP-005 R2.5.3: During two consecutive quarters, quarterly master access lists were not signed as required by WECC_URE1's internal process for three ACM Cyber Assets. 4) CIP-005 R2.4: On two occasions during a three-month period, two individuals were given permission to log into an ESP device without using two-factor authentication as required by WECC_URE1's cyber security policy. The device accessed was WECC_URE1's firewall management control device. WECC Enforcement determined that WECC_URE1 is in violation of CIP-005-1 R1 for failing to afford the required protections to its ACM Cyber Assets as required by the Standard. | CIP-005-1 | R1 | Medium | High | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The Cyber Assets in scope are located in ESPs and a Physical Security Perimeter (PSP). The PSP consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Evaluated, tested and installed all missing cyber security software patches on each of the servers (CIP-007 R3). 2. Implemented a comprehensive patch management process to ensure ongoing tracking, evaluating, testing and implementation of cyber security software patches on all servers in the ESPs. This process includes regular coordination meetings to ensure ongoing compliance with CIP-007 R3. 3. CIP-004 R3: Person in scope had access removed, a PRA was performed and access was granted. 4. CIP-005 R2.5.3: Verified current access was correct, revised policy on how reviews are performed, and CIP-004 R4 and CIP-007 R5 workflow document was implemented for access verification. | 2011-07-20 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount. WECC determined that this violation constituted that same action behind the CIP-005-1 and CIP-005-2 violations, WECC201102794 and WECC201102428, contained within this Notice of Penalty. As a result, WECC did not issue a separate penalty for this violation.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002794 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2. Specifically, on two occasions during a three-month period, contrary to WECC_URE1's cyber security policy, two individuals within were permitted to log into an Electronic Security Perimeter (ESP) device for firewall management control without using two-factor authentication. Therefore, WECC determined that WECC_URE1 had not implemented strong procedural and technical controls to ensure authenticity of the accessing party, where technically feasible, at access points to the ESP where external interactive access was enabled in accordance with CIP-005-1 R2.4. When reviewing WECC_URE1's CIP-005-1 R2 violation, WECC also concluded that WECC_URE1 violated CIP-005-1 R2.5.3 because it did not sign quarterly master access lists during two consecutive quarters per its CIP-004-1 R4 review. WECC concluded that WECC_URE1 was in violation of CIP-005-1 R2.4 because it did not implement its policy regarding the use of two-factor authentication, and CIP-005-1 R2.5.3 because it did not follow its review process for authorization rights in accordance with CIP-004-1 R4. | CIP-005-1 | R2; R2.4; R2.5.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The firewall management control room is in a Physical Security Perimeter (PSP) that requires card reader access. The PSP consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. In addition, both individuals in scope had current personnel risk assessments and cyber security training, and were authorized to access this ESP device for firewall management control. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Updated its two-factor authentication service to further limit unauthorized access into the ESP and PSP devices; and 2. Implemented a process to ensure management communicates with its staff the expectations regarding policies and procedures when accessing NERC CIP covered systems and to use the formal exception process when necessary. | 2010-04-30 | 2012-04-27 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102428 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-2 R5 because it failed to update documentation within 90 days of modification and change of its network. WECC_URE1 decided to remove the server running the an application and reuse that server for another purpose because the application was no longer being used. The application and the server were turned off, and power as well as network access were removed from the server. However, WECC_URE1 did not update its Electronic Security Perimeter (ESP) architecture diagram to delete the server until five months later, which was more than 90 days after the removal of the server from the ESP. WECC determined that WECC_URE1 is in violation of CIP-005-2 R5.2 for failing to update its documentation within 90 days of a modification and change to its network. | CIP-005-2 | R5; R5.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the Cyber Asset in scope was not being used prior to being removed from the ESP. | 90 days after the date that the relevant device was removed | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 updated its information system architecture diagram to reflect the removal of the server from the ESP and Physical Security Perimeter. Additionally, WECC_URE1 made changes to its change management process document and implemented a checklist for completion of change activities. | 2011-01-04 | 2012-04-27 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002792 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because certain Cyber Assets were not inside a Physical Security Perimeter (PSP) in accordance with CIP-006-1 R1. In addition, WECC_URE1 stated that it did not follow procedures for reviewing access authorization requests and revocation of access authorization in accordance with CIP-004 R4, as required by CIP-006 R1.5. Further, WECC_URE1 also stated that it did not provide multiple protections for its physical access control system, which controls physical access to all of its PSPs, as required by R1.8. The five protections that were not provided by WECC_URE1 are as follows: 1) CIP-005-1 R2.3: WECC_URE1 stated that it did not sign quarterly master access lists during two consecutive quarters in accordance with its internal process for maintaining lists of individuals with cyber and/or physical access to Critical Cyber Assets (CCAs) and PSPs. 2) CIP-005-1 R2.4: WECC_URE1 stated that on two occasions during a three-month period, two individuals were given permission to log into a WECC_URE1 IT management Electronic Security Perimeter (ESP) device without using two-factor authentication as required by WECC_URE1's cyber security policy. The device accessed was WECC_URE1's firewall management control device. 3) CIP-004-1 R3: WECC_URE1 stated that one individual, who had access to WECC_URE1's physical access control system, did not have a personnel risk assessment (PRA). 4) CIP-007-1 R5: WECC_URE1 stated that, although its cyber security policy prohibits the use of shared accounts, WECC_URE1 allowed the use of read-only access shared accounts to view information within the system used in the physical access control and monitoring (ACM) of PSPs. | CIP-006-1 | R1; R1.5; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place. The room where the firewall management control device and the two-factor authentication server in scope reside requires card reader access. This room is within multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. Also, the supervisory control and data acquisition workstation in scope resides in the backup control center in a room that requires card reader access and that is inside an ESP. Additionally, the physical access control system device, used in the ACM of CSU's PSPs, is located inside an ESP and PSP, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Report | In accordance with its Mitigation Plan, WECC_URE1 relocated the two systems associated with firewall management access control and two-factor authentication access control to a locked server rack which is a six-wall configuration. WECC_URE1 revised its CIP-004 personnel and training process document for maintaining lists of individuals with cyber and/or physical access to CCAs and PSPs. The revised process document no longer required that quarterly master access lists be signed. WECC_URE1 updated the two-factor authentication service to further limit unauthorized access into the ESP and PSP devices. Server administration staff and information security personnel were instructed to follow process and procedures strictly when accessing NERC CIP covered systems, and to use the formal exception process when necessary. WECC_URE1 removed access rights to the physical access control system, conducted a PRA and then reset the access rights for all individuals in scope. The shared account access used by the contracted security officers was removed and individual user accounts and passwords were established for each security officer to access the physical access control system. WECC_URE1 created a repeating calendar entry for the server administration staff to log into the server once a week to manually copy the security event log to a specified location on the server. WECC_URE1 collaborated with its software provider’s technical support desk for assistance to correct the workflow anomaly that had occurred. WECC_URE1worked with technical support to permanently fix the issues with the system. The system has been monitored and tested to reestablish confidence in its ability. | 2011-12-29 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102788 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-2a R3 and R3.1. Specifically, WECC_URE1 failed to implement its patch management program and to assess patches within 30 days of availability for two electronic access control and monitoring (ACM) devices and one physical ACM device that are all within WECC_URE1's Electronic Security Perimeter (ESP). In addition, WECC_URE1 provided information that patches were not assessed on three additional devices within 30 days. The three devices had been removed from the ESP before it was determined that patches needed to be assessed, and because the three devices had already been removed from the ESP at the time of discovery, patches were not implemented as required by WECC_URE1's cyber security policy. WECC determined that WECC_URE1 is in violation of CIP-007-2a R3.1 for failing to assess its security patches within 30 days and for failing to implement the patches after performing an assessment. | CIP-007-2a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the room in which the devices in scope reside requires card reader access. This room is within multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. Also, the facility in scope has twenty-four hour a day logging and monitoring and the devices in scope reside within an ESP. | 30 days after the first patch was available | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 evaluated, tested and implemented all missing cyber security software patches. WECC_URE1 further implemented a revised cyber security patch management process to ensure the ongoing tracking, evaluating, testing and implementing of cyber security software patches. This process includes regular coordination meetings to ensure ongoing compliance with CIP-007 R3. | 2011-01-31 | 2012-06-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102795 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5. Specifically, WECC_URE1 reported that its contracted security officer personnel used read-only access shared accounts to access WECC_URE1's application which controls access to WECC_URE1's Physical Security Perimeters (PSPs), although WECC_URE1's account management policy prohibits the use of shared accounts. In this case, there were two shared read-only access accounts at locations that contained Critical Cyber Assets (CCAs). The first location was WECC_URE1's service center where several security guards had read-only shared access. The second location was at WECC_URE1's plant where several security officers had read-only shared access. At both locations, the shared read-only access accounts limited the capability of the security officers to monitor (viewing, panning, tilting, scanning, and zooming) the display of live surveillance videos at the respective locations. The read-only shared access accounts did not allow any type of modification to the CCAs' physical access data housed in WECC_URE1's physical access control system. WECC determined that WECC_URE1 is in violation of CIP-007-1 R5 for failing to implement WECC_URE1's account management policy, which prohibits the use of shared accounts. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as a compensating measure, WECC_URE1 stated that the shared accounts in scope were used by personnel who had current training and personnel risk assessments. Additionally, the shared accounts provided read-only access to the physical access control system and account usage was monitored. Further, the read-only shared access accounts did not allow any type of modification to the CCAs' physical access data housed in WECC_URE1's physical access control system. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 removed shared account access used by the contracted security officers and established individual user accounts and passwords for each security officer to access the physical access control system. | 2010-11-21 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102439 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-2a R5 for failing to establish and implement formal methods, processes, and procedures for disposal of or redeployment of Cyber Assets within the Electronic Security Perimeter (ESP). Specifically, WECC_URE1 failed to redeploy a Cyber Asset as a like-kind Cyber Asset in accordance with its policy. An application and server were turned off, and power as well as network access were removed from the server. One month later, the server was removed from the Physical Security Perimeter (PSP) and the hard drives were redeployed for use. WECC_URE1 stated that the hard drives from the server were reformatted, as required by CIP-007-2a R7.2, prior to redeployment. However, WECC_URE1's change management process document further required that the hard drives be degaussed, and another section of that same policy document required that the hard drives be redeployed in a like-kind asset within the ESP. Therefore, WECC determined that WECC_URE1 is in violation of CIP-007-2a R7.2 for failing to redeploy the Cyber Asset as a like-kind Cyber Asset in accordance with its policy. | CIP-007-2a | R7; R7.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE1's hard drives were reformatted using a deep-level format. Additionally, the hard drives were used in a secure building on the corporate network. | when the server was removed from the PSP | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 removed, degaussed and destroyed the server hard drives involved. Additionally, employees were provided training and given a NERC CIP change checklist, which includes steps for decommissioning applications and servers. The checklist was added to WECC_URE1's updated change management process document which outlines procedures for changing information technology in the organization. The process document was revised and approved. | 2011-01-11 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009023 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-004-1 R4. WECC_URE2 failed to properly maintain its Critical Cyber Asset (CCA) access list for a number of individuals (16% of the total with access) for one CCA. The CCA involved is used as a server to provide the correct time for CCAs located inside a WECC_URE2 Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). Although this CCA was properly included on the CIP-002 CCA list, it was not listed on the CIP-004 R4 access list. These employees did not have access listed for the device in scope. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE2 did maintain a physical access list of the personnel having access to the server and did maintain which users had logical access in its CIP-007 R5 users list. Additionally, the device at issue resides in an ESP and PSP with twenty-four hours a day, seven days a week logging and monitoring of physical and logical access. In addition, this device is in a separate locked cabinet within the PSP to which a smaller subset of personnel has access. Although the CCA was not listed on the CIP-004 R4 access list, the individuals who had access to the device had received the appropriate NERC CIP training. | when the Standard became mandatory and enforceable as to WECC_URE2 | when WECC_URE2 completed the quarterly review of the access list of its personnel who have such access to CCAs | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | WECC_URE2 completed the following mitigating activities: 1) Established a practice and process to reference only the CIP-002 CCA list for developing and maintaining CIP-004 access lists; 2) Reviewed the CIP-002 CCA list to ensure all applicable devices are listed on the CIP-004 access lists; 3) Reviewed and updated the CIP-004 list maintenance procedure; 4) Monitored and validated the process; and 5) Reviewed the roles and responsibilities under the CIP-004 list maintenance procedure. | 2012-03-30 | 2012-07-25 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009024 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R3. WECC_URE2 failed to assess all security patches and security upgrades within 30 days of those patches being available on several of its Critical Cyber Assets (CCAs). WECC_URE2 did perform some of the required security patch assessments and security patch upgrades on the CCAs involved, but failed to complete all of the security patch upgrades for all CCAs. The CCAs involved are located inside an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). In this instance, since the Standard became mandatory and enforceable, WECC_URE2 failed to assess security patches and upgrades for a number of CCAs within 30 days of their availability. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because failure to assess security patches for CCAs within an ESP could result in unaddressed security vulnerabilities for an extended period of time, increasing the risk of a successful cyber attack against CCAs essential to the operation of the BPS. As compensating measures, WECC_URE2 did assess security patches and security upgrades for the operating system for the devices in scope, but failed to complete all of the security patch upgrades for all Cyber Assets. In addition, the devices involved are located in an ESP and PSP and protected by firewalls, anti-virus software, and are checked daily for changes to their configuration. | when the Standard became mandatory and enforceable as to WECC_URE2 | Mitigation Plan completion | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | WECC_URE2 completed the following mitigating activities: 1) Identified roles and responsibilities related to checking and reviewing security patch releases for software applications; 2) Completed security patch evaluations; 3) Updated and reviewed WECC_URE2's CIP-007 R3 security patch management procedure; and 4) Monitored and validated its process to ensure effectiveness. | 2012-03-30 | 2012-07-27 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009025 | Settlement Agreement | WECC_URE2 self-reported a violation of EOP-001-0 R6. WECC_URE2 failed to annually review, update, and provide a copy of its emergency operations planning procedure to a neighboring Balancing Authority (BA), a neighboring TOP, and the Reliability Coordinator (RC), for a single calendar year. WECC_URE2 did provide evidence that it fulfilled the requirements of the Standard for the following calendar year. WECC determined that WECC_URE2 is in violation of EOP-001-0 R6 for failing to review, update, and provide a copy of its emergency operations planning procedure to the neighboring BA, TOP and RC for one calendar year. | EOP-001-0 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE2 developed its emergency operations planning procedure and distributed it to WECC_URE2. In addition, WECC_URE2 did fulfill the requirements of the Standard in the following calendar year. In addition, WECC_URE2 made only minor changes to its emergency response procedures the previous year. | when WECC_URE2 should have reviewed, updated and provided its emergency operations planning procedure to the neighboring BA, TOP and RC for the missing calendar year | Mitigation Plan completion | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | To mitigate the violation, WECC_URE2 reviewed and revised its procedure and distributed an updated emergency operations procedure to the neighboring BA, TOP and RC. WECC reviewed the updated emergency operations planning procedure document and determined that the revised document included procedures for distributing an emergency operations procedure on an annual basis to its neighboring BA and TOP. | 2011-10-07 | 2012-05-07 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009026 | Settlement Agreement | WECC_URE2 self-reported a violation of PRC-005-1 R2. When WECC_URE2 assumed functional compliance responsibility for compliance obligations associated with a facility. WECC_URE2 failed to test the following Protection System devices within their 48-month interval: relays (0.2%), current transformers and potential transformers (19.8%), communications devices (2.0%), and DC circuitry (2.5%). All batteries were maintained and tested within the defined interval. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 maintained and tested these devices every four years and performed quarterly inspections of the stations in which they were housed. Failures of instrument transformers would have been discovered during WECC_URE2's quarterly station inspection, which were performed on schedule. | when WECC_URE2 should have performed the maintenance and testing | present | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | To mitigate the violation, WECC_URE2 will: (1) Install test switches and complete relay testing; (2) Implement instrument transformer verification for neutral relays; (3) Complete its instrument transformer verification testing; (4) Provide a status update to WECC; and (5) Design, install and test bus lockout test switch. | 5/31/2013 (approved completion date) | TBD | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009976 | Settlement Agreement | WECC determined that WECC_URE3 had a violation of CIP-005-1 R3.2 because WECC_URE3 failed to implement controls to ensure that access points to WECC_URE3's system control center and backup control center Electronic Security Perimeters (ESPs) were configured to alert appropriate personnel to unauthorized ESP access attempts or unauthorized ESP access. Several ESP access points to ESPs were not configured in accordance with CIP-005-1 R3.2. WECC determined that WECC_URE3 was in violation of CIP-005-1 R3.2 as of the effective compliance enforcement date of the Standard. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because compensating measures were in place during the violation period. WECC_URE3 has an in-depth defense structure to ensure electronic security. This includes network segmentation within ESPs. All personnel with access to each of the three devices have completed cybersecurity training and personnel risk assessments (PRAs). All the devices are password-protected, Cyber Assets and Critical Cyber Assets are secured behind firewalls, and access is controlled, logged, and monitored. | when the Standard became mandatory and enforceable to WECC_URE3 | Mitigation Plan completion | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 completed the following mitigation activities: 1) Identified and documented all electronic access control devices which may be interactively accessed. 2) Configured every device identified in step 1 so that unauthorized access attempt events are sent as syslog events to security information and event management software. | 2012-07-11 | 2012-08-21 | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor. WECC_URE3 was cooperative throughout the process.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009938 | Settlement Agreement | WECC determined that WECC_URE3 had a violation of CIP-006-1 R3 because WECC_URE3 failed to document and implement operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. WECC determined that WECC_URE3 failed to implement controls for immediately reviewing unauthorized access attempts to several PSP access points through several PSPs at multiple locations; that WECC_URE3 did not implement technical or procedural controls for immediately reviewing unauthorized access attempts at a certain type of PSPs; that WECC_URE3 did not implement procedural or technical controls for immediately reviewing unauthorized physical access attempts at access points to PSPs at the backup control center; and, that WECC_URE3 did not monitor physical access to access points to a PSP at the system control center, during normal business hours. | CIP-006-1 | R3 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE3 had compensating measures in place during the pendency of the violation. WECC_URE3 reviews access logs weekly. Access points at the PSPs at issue are locked and monitored twenty-four hours a day, seven days a week. An access point to the PSP at the system control center is locked and monitored during normal business hours. Certain identified assets are located within cabinets identified as separate PSPs within a larger PSP. All individuals with access to Critical Cyber Assets and Cyber Assets within a PSP completed cybersecurity training and personnel risk assessments (PRAs). | the first day following Certification of Mitigation Plan Completion for a prior CIP violation | present | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 will complete the following mitigation activities: 1) WECC_URE3 will identify all physical access points to the backup control center and system control center. 2) WECC_URE3 will configure unauthorized access attempt alarms for all physical access points to the backup control center and system control center. 3) WECC_URE3 will identify the appropriate staff to notify and respond to alarms. 4) WECC_URE3 will configure a method of notifying appropriate staff of unauthorized access alarms. 5) WECC_URE3 will install a video camera to monitor the roof hatch. 6) WECC_URE3 will correct network problems to enable review of the backup control center video recorder at the system control center. 7) WECC_URE3 will train operators to review video, acknowledge alarms, respond to alarms, and document alarm response. | 12/31/2012 (approved completion date) | TBD | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE3's violation history.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009939 | Settlement Agreement | WECC determined that WECC_URE3 was in violation of CIP-006-1 R4 because WECC_URE3 failed to implement technical or procedural controls to ensure logging physical access at all access points to the Physical Security Perimeter (PSP) using a logging method listed in the Requirement or their equivalent. WECC_URE3 failed to implement controls that logged physical access for a roof hatch identified as an access point to the system control center PSP. | CIP-006-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE3 had implemented other security measures to protect the PSP. The roof hatch access point was in a garage and pad-locked from the inside. There were no Critical Cyber Assets (CCAs) in the garage. Access to CCAs within the system control center via entry through the roof hatch would require passage through two card-access restricted doors, which are logged and monitored via cameras twenty-four hours a day, seven days a week. | when the Standard became mandatory and enforceable to WECC_URE3 | Mitigation Plan completion | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 completed the following mitigation activities: 1) WECC_URE3 placed visitor log books at roof hatch, at the West entrance, between the garage overhead door and garage man door; 2) WECC_URE3 changed the physical security plan to require visitors to sign out on the appropriate log book when leaving the PSP instead of at the main entrance; 3) WECC_URE3 changed the physical security plan to require the escort to return the visitor badge to the front desk and to add a note to the main entrance log book describing from which access point the visitor exited the PSP. | 2012-06-29 | 2012-08-21 | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor. WECC_URE3 was cooperative throughout the process.