## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007853 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-002-1 R3 because it failed, on two separate occasions, to identify Cyber Assets that were essential to the reliable operation of Critical Assets and were dial-up accessible as Critical Cyber Assets (CCAs) and to include them on the list of CCAs, resulting in a violation of CIP-002 R3.3. The first occasion occurred when FRCC_URE1 found that there was a multiplexer, with a dial-up connection, located at a transmission substation that still had the phone line connected. This device should have been identified when the substation was identified as a Critical Asset. The substation multiplexer was disconnected. The multiplexer was located in the low voltage control room which is typically not included in the verification of connection and disconnection of devices at identified sites and therefore had been previously missed. The second occasion occurred when FRCC_URE1 performed Critical Asset site walk-downs to ensure transmission substations were disconnected for continued compliance. During a review of the list of Critical Asset sites to walk-down, FRCC_URE1 personnel discovered that the list provided at for the walk-down did not match the official Critical Asset list. As a result, transmission substation identified as a Critical Asset on the official Critical Asset list had dial-up connectivity for one and half years. On the same day the violation was discovered, all dial-up accessibility was removed and the violation was corrected. | CIP-002-1 | R3; R3.3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to identify CCAs could result in leaving the CCAs unprotected and vulnerable to a cyber threat and therefore, may pose a moderate risk to the operation of the BPS. In this case the entity failed to identify and document one CCA that was dial-up accessible at each of the substations. The affected two CCAs made up .012% percent of total CCAs protected by FRCC_URE1. The risk to the BPS was mitigated by the fact that the dial-up provisions limited security risk. Regarding the first incident, the dial-up device at the substation was accessible only by using a proprietary client and was password protected for authorized access only. For the second incident, the device at the substation was remotely accessible without a password but required proprietary installed client (software) and was not openly available. In addition, only authorized persons were aware of its existence and no unauthorized access was identified after review of all remote activity. Furthermore, for both incidents, the dial-up accessible devices, while connected, were used to collect data that was not real-time data and was not essential or critical to the operation of the Critical Assets or BPS reliability. The function of the devices was to collect data for a historical long-term database supporting off-site storage and/or for collecting fault recorder information. | when FRCC_URE1 failed to include the Cyber Assets on the list of Critical Assets | when dial-up access was removed | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) disconnected the substation multiplexer and labeled phone line cable; 2) disconnected transmission substation multiplexer and labeled phone line cable; and 3) performed a walk-down at all Critical Asset substations. | 2011-07-07 | 2013-03-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008470 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R1 because in multiple instances Cyber Assets used in the access control and monitoring of Electronic Security Perimeters (ESPs) were not afforded the specific protection measures required by CIP-005-1 R1.5 as described below: 1) CIP-003 R5: A group of information repositories did not have the correct individual identified as the designated personnel responsible for authorizing logical access to the protected information as required by CIP-003 R5; 2) CIP-003 R6: A hard drive of an electronic access control and monitoring (EACM) server was replaced without proper documentation in the ticketing system as required by CIP-003 R6; 3) CIP-005 R1.5: None of the CIP-005 R1.5 requirements were met for certain EACM devices; 4) CIP-007 R1: The testing procedure in place as required by CIP-007 R1 was lacking specific details on how not to adversely affect existing cybersecurity controls, resulting in incomplete test results for EACM assets; 5) CIP-007 R3: A group of patches as required by CIP-007 R3, were not assessed on a group of EACM assets for a year and a half; 6) CIP-007 R5.1.3: A group of user accounts for a group of EACMs were not reviewed annually for one year, as required by CIP-007 R5.1.3 to verify access privileges were in accordance with CIP-003 R5 and CIP-004 R4; 7) CIP-007 R5.3.3: A group of passwords for accounts on EACM assets had not been reset in over a year, as required by CIP-007 R5.3.3; 8) CIP-007 R8: The execution status for the action plans for EACMs for one year's vulnerability security assessments were not consistently documented, as required by CIP-007 R8, and in some cases were not available; and 9) CIP-009 R2: There were violations related to disaster recovery plans for two different EACMs. One disaster recovery plan was not reviewed annually for one year for an EACM asset. The other disaster recovery plan was not created for an EACM asset for one year and eight months. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failing to ensure that Cyber Assets used in the electronic access control and monitoring of the ESP are afforded protective measures puts such assets at risk to be manipulated. If successfully manipulated, unauthorized access to the ESP compromises the security of Critical Cyber Assets (CCAs) within the ESP. In this case, FRCC_URE1 failed to provide protections such as change control and testing, account control and password protection, cyber vulnerability assessment, and implementation of recovery plan. However, the risk to the reliability of the BPS was mitigated as all the devices were secured behind a protected electronic access point and FRCC_URE1 maintained the defense-in-depth protection by utilizing both physical (physical security perimeters) and logical controls (ESPs) thereby limiting any potential serious impact on any EACM reported under this violation. In addition, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the first instance of the violation occurred | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) completed a review of authentication and authorization directory service owners of all information repositories where applicable; 2) changed authentication and authorization directory service ownership to designated information repository owners and added comments to appropriate authentication and authorization directory service field denoting a change in approver also requires change within the NERC-CIP repository list and to contact the information security group for assistance; 3) created procedures to note that repository list and authentication and authorization directory service approvers will be updated by the analyst performing the change in repository owner where authentication and authorization directory service group permissions are leveraged; 4) added comments to the protected CCA information repository list description to ensure any changes to the list are also reflected in procedures & documentation; 5) reviewed NERC-CIP asset disposal & redeployment process with team responsible for completing disposals & redeployments and documented future disposal/redeployment in ticketing system; 6) initiated demilitarized zone isolation project to properly secure EACM devices and apply required controls; 7) updated testing procedure to include specific details requiring the use of this procedure change control, configuration management and cybersecurity testing; 8) assessed and applied current patches to mitigate current and previous vulnerabilities and removed unnecessary software from servers where applicable; 9) added identified user accounts to the master account list and conducted annual review of access privileges for identified user accounts; 10) changed group policy for devices integrated with authentication and authorization directory service to require password change frequency in compliance with the standard and changed passwords as required for the identified accounts; 11) implemented use of change tickets to document execution status in the Mitigation Plans for vulnerability assessments and updated procedure with instructions on how to completed; 12) completed annual review of the affected EACM device; 13) developed disaster recovery procedure for the affected EACM device; and 14) revamped disaster recovery drills to require annual reviews in advance of drill. To mitigate this violation, FRCC_URE1 will submit technically feasibility exceptions, where applicable. | 3/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008521 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation CIP-005-1 R2.2 because it failed to implement appropriate access rules at its electronic access points (EAPs) that restricted traffic to only the ports and services that were required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP). The access rules, that restrict traffic to only those ports and services that are required for operations and monitoring of Cyber Assets within two control centers' ESPs and to and from appropriate demilitarized zones (DMZ), had not been fully implemented and were not documented individually or by specified grouping. FRCC_URE1 depended on the secure Internet Protocol Security (IPSec) tunnel to limit communication between the connected ESP. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1 reduced the risk by documenting what ports and services were restricted in the implementation and did review as required. FRCC_URE1 was aware of all ports and services enabled on its access points. The documentation and restrictions; however, were not documented individually or by specified grouping of the configuration of ports and services, and the granularity of the access rules in place did not ensure that only those required ports and services were enabled. In addition, all CCAs were within ESPs and protected by restrictive firewalls with limited connectivity to outside networks. Furthermore, all logical traffic is actively monitored through the use of a Security Event and Incident Monitoring (SEIM) system, EMS/supervisory control and data acquisition logs, and an Intrusion Detection System. Thus, FRCC_URE1 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. Lastly, these access points were connected to other access points using an IPSec tunnel limiting any opportunity of external exploitations. | when the Standard became mandatory and enforceable on PEF as a "Table 1" entity | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) developed initial network architecture diagram to meet CIP compliance; 2) developed initial action plan for new network device installation; 3) provided updated action plan for new network device installation; 4) developed project plan for implementation; 5) completed implementation for a generation site; 6) completed implementation for another generation site; 7) provided update on firewall policy changes; 8) installed application clients as needed on EACM devices to minimize the amount of devices which access the ESP; 9) established new group naming standards and first update of firewall rules; 10) incorporated initial findings into new trust rule and update firewall rules; and 11) updated its firewall policy per CIP-005 R2.2; and To mitigate this violation, FRCC_URE1 will: 1) monitor then incorporate any new findings in new trust rule; 2) establish new group naming standards and updated of firewall rules; 3) incorporate initial findings into new trust rule; 4) monitor then incorporated any new findings in new trust rule; and 5) remove finally original trust rule. | 12/29/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008523 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R4.2 because it failed to document the review to verify that only ports and services required for operations at all access points were enabled as part of the cyber vulnerability assessment (CVA). While FRCC_URE1 did perform verification of all other requirements of CIP-005-1 R4, it did not include the verification that all open ports and services are required for operation and monitoring of the Cyber Assets within the Electronic Security Perimeters (ESPs) at the access points. | CIP-005-1 | R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to conduct a complete CVA of all Cyber Assets could allow any cyber vulnerabilities in such assets to go unchecked and undetected. Subsequently, if any such vulnerabilities are not corrected, they could be exploited by malicious access, thereby providing an attack vector for launching cyber attacks against Critical Cyber Assets essential to the operation of BPS. In addition, lack of discovery of unwanted ports at the access point could allow unauthorized persons to compromise access point security and limit effective monitoring of the access points for security compromises. As compensating measures, FRCC_URE1 performed an initial evaluation to determine a baseline for all the access points and reviewed ports required for normal operation. In addition, FRCC_URE1 implemented defense-in-depth utilizing both physical (physical security perimeters) and logical controls (ESPs), including performing a review for enabling only ports required for operation on all the Cyber Assets within the ESP. Furthermore, all the external ESP communications are limited to other trusted sources or trusted ESPs which are connected using Internet Protocol Security tunnels. Lastly, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the non-compliant CVA was conducted | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) updated its procedure document to require a review of the firewall policy as part of the annual CVA; 2) developed initial network architecture diagram to meet CIP compliance; 3) developed initial action plan for new network device installation; 4) provided updated action plan for new network device installation; 5) developed project plan for implementation; 6) completed installation of new device as required at generation sites; and 7) created data flow diagram to demonstrate the required ports & services on specific nodes. | 2012-08-07 | 2013-03-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008524 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-007-1 R8.2 because, while FRCC_URE1 did conduct an annual cyber vulnerability assessment (CVA), it failed to maintain sufficient evidence to demonstrate that the annual CVA included a review of all ports and services required for normal and emergency operations. For non-appliance based Cyber Assets, FRCC_URE1 conducted a review based on an in-house developed tool that compares base-line configuration to verify that only ports required for normal and emergency operation were open. For appliance-based Cyber Assets, FRCC_URE1 conducted review of configurations to determine if the ports and services were required for normal and emergency operations. Manual reviews often depend on individual knowledge and in this case lacked comprehensiveness, and FRCC_URE1 failed to document all open ports and in some cases of appliance-based devices the verification of open ports and services did not include verification of many ports and services that are enabled by default and were not required by FRCC_URE1. | CIP-007-1 | R8; R8.2; R8.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Risk to these affected devices was limited as these services were not accessible remotely and FRCC_URE1 implemented defense-in-depth utilizing both physical (physical security perimeters) and logical controls (Electronic Security Perimeters (ESPs)). Furthermore, most of the external communication is limited to other trusted sources or trusted ESPs which are connected using Internet Protocol Security tunnels. In addition, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) submitted surveys to peer utilities on solutions for performing more comprehensive scans of devices within the ESP; 2) reviewed solutions for performing more comprehensive scans of devices within the ESP; and 3) assessed production feasibility. To mitigate this violation, FRCC_URE1 will: 1) test solution(s)/tool(s); 2) configure and implement a solution identified in item 2 to meet CIP-007 R8.2; 3) document results of test scans and submit and update appropriate Technical Feasibility Exceptions for CIP-007 R2; and 4) perform CVA review for compliance with CIP-007 R8. | 11/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010779 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-002-3 R3. RFC_URE1 installed an upgraded remote terminal unit (RTU) at a substation, a Critical Asset. The individuals upgrading the RTU did not identify the substation as a Critical Asset in its database, and as a result, RFC_URE1 failed to identify the Critical Cyber Assets (CCAs) associated with the substation on its list of CCAs. | CIP-002-3 | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because unidentified CCAs increase the likelihood that a Responsible Entity will fail to afford Cyber Assets which are essential to the operation of the Critical Asset the security protections of CIP-003 through CIP-009. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE1 discovered this violation due to its internal controls when its transmission protection and controls department identified that there was a critical station connected to the network without proper protection. Within one day of discovery, RFC_URE1 disconnected the network until it could apply the proper controls, locked the interior deadbolts on all doors except for one that was padlocked from the outside, and had alerting and manual logging enabled. In addition, the substation is completely fenced with a locked gate, and the doors to the control house were locked. The network and the CCA at issue both require username and password authentication. | RFC_URE1 installed the RTU | When RFC_URE1 disconnected the RTU from the network until it enabled the proper controls | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) immediately disconnected the network until it applied the proper controls and protected all doors to the substation; 2) implemented formal Physical Security Perimeter controls at the substation; 3) reviewed internal processes and procedural controls to propose improvement; and 4) implemented the improvements as agreed upon by the business units involved. | 2013-02-28 | TBD | Agrees/Stipulates | ReliabilityFirst reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with ReliabilityFirst during the Compliance Audit and in connection with the violations. ReliabilityFirst also considered that it discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. ReliabilityFirst considered that it discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
ReliabilityFirst Corporation (ReliabilityFirst), Southwest Power Pool Regional Entity (SPP RE), and Texas Reliability Entity, Inc. (Texas RE) (collectively, the Regional Entities) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX NCRXXXXX NCRXXXXX | RFC201100932 SPP201100587 TRE201100370 | Settlement Agreement | RFC_URE1 submitted a Self-Report to the Regional Entities identifying a violation of CIP-007 R1. This violation affected Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP), which involves CIP-005-3a R1.5. RFC_URE1 submitted Self-Reports to the Regional Entities identifying a violation of CIP-005-1 R1. During a periodic review of assets within the ESP and Physical Security Perimeters, RFC_URE1 discovered devices connected to console routers that were not located within an ESP. These devices were Critical Cyber Asset (CCA) firewalls and Cyber Assets used in the access control and monitoring of ESPs. The console routers constituted access points to the ESP, but RFC_URE1 failed to identify and document these access points to the ESP. RFC_URE1 disconnected the console router connections two days after discovering the omission. RFC_URE1 discovered that it had installed Cyber Assets within an ESP without identifying them as CCAs or non-critical Cyber Assets within the ESP. RFC_URE1 had incorrectly configured the gateway router settings. The IP configurations were correct as the devices were located within the ESP, but without the correct gateway router settings, the devices could not communicate outside the ESP. The remainder of these assets were identified CCAs located within the ESP but had multiple IP addresses, only one of which was identified. RFC_URE1 identified these CCAs by performing device scans from within the ESP locally or by reviewing address tables. RFC_URE1 remediated these configurations. The Regional Entities conducted a Compliance Audit during which the Regional Entities discovered violations of CIP-005-1 R1. RFC_URE1 has intrusion detection system (IDS) devices in place, which are located outside the ESP and communicate with the switches that are located within the ESP. RFC_URE1 failed to identify these IDS devices as access points to the ESP. | CIP-005-3a | R1 | Medium | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The console routers were located within a Physical Security Perimeter and similar authentication is required to access the devices. The connection was a nonroutable asynchronous connection, decreasing the likelihood of unauthorized access. Regarding the incorrect configuration of certain CCAs, each device was located within the ESP, and certain of the devices were identified and protected as CCAs. The incorrect configuration of the gateway routers and IP addresses prevented the ability to access the devices remotely. In addition, if someone had physical access to the CCAs, a username and password to authenticate was required for logical access. These devices connected to the substation network which is protected by a firewall, access control list, and IDS. Regarding the IDS devices, the IDS passively monitors networks at RFC_URE1 for malicious activities. The IDS devices consist of a management port to manage the devices remotely and report detected events back to a central monitoring system and monitoring ports to detect malicious activities within a network which are only capable of passively receiving traffic. RFC_URE1 has controls in place to prevent traffic from traversing the IDS to enter the ESP. First, the IDS isolates the management port from the monitoring ports, and the monitoring ports allow inbound traffic only. This configuration decreases the likelihood of malicious traffic using the IDS devices to enter and exit the ESP. Second, these appliances are directly connected to mirrored ports (port mirroring is utilized to monitor network traffic by sending a copy of network packets or data traffic to a network monitoring connection on another switch port on routers within the ESP. Moreover, in certain scenarios, RFC_URE1 uses a third protection, an aggregation device to combine data together from multiple switches for analysis by the IDS, which results in fewer access points to the ESP. The input port cannot be used for output on this device, and vice versa. The input port can only receive data, and it can only receive data from specific protocols that it was designed to handle. The output port can only send data outbound, and it can only send data outbound using specific protocols that it was designed to handle. Furthermore, the devices’ protocol is configured to transmit data from inside the ESP to the IDS device outside the ESP only. | When the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) conducted a system-wide scan and assessed the existing similar devices’ configuration; 2) identified and corrected related erroneous configurations; 3) evaluated alternatives to automate the process to detect device misconfigurations; 4) evaluated other available IP configuration scan tools and developed practical improvement options; 5) increased awareness of the issue to personnel involved with configurations; 6) communicated and issued lessons learned to related staff; 7) tested and piloted preferred alternative solutions; and 8) implemented automated solution for IP configuration, scanning, and detection of device misconfiguration. | 2012-02-29 | 2012-06-01 | Agrees/Stipulates | The Regional Entities reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with the Regional Entities during the Compliance Audit and in connection with the violations. The Regional Entities also considered that they discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. The Regional Entities considered that they discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, the Regional Entities seek to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
ReliabilityFirst Corporation (ReliabilityFirst), Southwest Power Pool Regional Entity (SPP RE), and Texas Reliability Entity, Inc. (Texas RE) (collectively, the Regional Entities) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX NCRXXXXX NCRXXXXX | RFC2011001088 SPP201100669 TRE201100463 | Settlement Agreement | RFC_URE1 submitted Self-Reports to the Regional Entities identifying a violation of CIP-007-3 R1.7. During its cyber vulnerability assessment, RFC_URE1 discovered that it installed new third-party software on Critical Cyber Asset (CCA) workstations. RFC_URE1 performed testing on the software, but not in accordance with its CIP-007 R1 procedures. In addition, RFC_URE1 discovered that it made significant changes to upgrade firmware on storage area network switches and one storage array, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP), and one server, which is a CCA, without following RFC_URE1’s test procedures. Both instances occurred due to lack of awareness of test procedures by RFC_URE1 personnel. | CIP-007-3 | R1.7 | Medium | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Because the Cyber Assets at issue were located in a Physical Security Perimeter and an ESP, RFC_URE1 afforded the Cyber Assets the remainder of the requisite protections, including electronic access controls, cyber vulnerability assessments, protection through a physical security plan, protection of physical and electronic access control systems, and controlling, monitoring, and logging physical access. | When RFC_URE1 made the first change without testing in accordance with the Standard and Requirement | Mitigation Plan completion | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented controls to review changes to Cyber Assets prior to implementation; 2) revised and published the data service process documentation governing test procedures; 3) revised and published the change management process document to include content governing NERC changes; 4) revised and published the IT process documentation governing test procedures; and 5) provided awareness training to personnel responsible for maintaining the infrastructure. | 2011-11-15 | 2012-01-25 | Agrees/Stipulates | The Regional Entities reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with the Regional Entities during the Compliance Audit and in connection with the violations. The Regional Entities also considered that they discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. The Regional Entities considered that they discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, the Regional Entities seek to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009916 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R6. On September 30, 2011, RFC_URE2 discovered that its workstations, which are Cyber Assets within the Electronic Security Perimeter (ESP), can provide access to its physical access control system (PACS) without requiring a separate login to the application. Due to RFC_URE2’s lack of awareness of this access point to the PACS, it failed to implement the requirements of CIP-007-3 R6 for these workstations. Specifically, these Cyber Assets did not implement automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3 R6.1. In addition, there were no automated or manual alerts for detected cyber security incidents on these Cyber Assets, as required by CIP-007-3 R6.2. RFC_URE2 also failed to maintain logs of system events related to cyber security for these Cyber Assets, as required by CIP-007-3 R6.3. These Cyber Assets were not configured to retain logs of system events related to cyber security for 90 calendar days, as required by CIP-007-3 R6.4. As a result, RFC_URE2 failed to review logs of system events related to cyber security for these Cyber Assets, as required by CIP-007-3 R6.5. In addition, RFC_URE2 discovered that the system log file for one Critical Cyber Asset (CCA) in its ESP had stopped sending messages to the security status monitoring application. While this device was in service and operational, it was not creating or maintaining logs of system events related to cyber security, as required by CIP-007-3 R6.3. Furthermore, RFC_URE2 discovered that the security monitoring controls for switches located inside the ESP, which are designated as CCAs, were not issuing automated alerts, as required by CIP-007-3 R6.2. | CIP-007-3 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because the instant violation had the potential to affect the reliable operation of the BPS by providing the opportunity for an undetected compromise of CCAs and other system events that are related to cyber security to occur without RFC_URE2's knowledge. The risk was mitigated because, for the workstations that provide access to the PACS, RFC_URE2 had afforded the PACS all protections as specified by CIP-006-3 R2.2. These systems required authentication. Therefore authorized access would be necessary prior to gaining the ability to access the PACS outside of the PACS software. For the switches that were not generating automated alerts, RFC_URE2 was monitoring the internal switches and it had organizational processes in place to log system events. | when the Standard became mandatory and enforceable on RFC_URE2 | when RFC_URE2 completed its mitigating activities | $0 (for RFC2012009916 and RFC2012009917) | Self-Report | To mitigate the violation, RFC_URE2: 1) rebooted the server, which resulted in the restoration of system status monitoring of the device; 2) configured the switches at issue to alert of security events; 3) increased the size of local security logs on all workstations and servers and increased the size of local logs on all database servers to retain logs for at least 90 days; 4) configured the internal logging and monitoring tool to collect logs and automatically alert on failed logins for the workstations; 5) tested and validated that the workstations are appropriately logging and alerting; 6) performed a manual review data that was available to ensure that there was no unauthorized access; and 7) provided additional information demonstrating that RFC_URE2 is committed to preventing or minimizing the probability of additional occurrences of the violation. RFC_URE2 is conducting a wholesale replacement of the existing technology related to monitoring and alerting that has a more robust, centrally managed solution. | 2012-11-16 | 2013-02-11 | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE2 promptly reported the violation due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues. ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for this violation. RFC_URE2 conducts internal audits of selected Reliability Standards. Furthermore, RFC_URE2 encourages its employees to submit any issues they suspect involve compliance with the Reliability Standards. ReliabilityFirst determined that RFC_URE2's previous violation constituted a prior violation and an aggravating factor in the penalty determination. ReliabilityFirst considered that RFC_URE2 discovered the violations through a Self-Reports and applied mitigating credit. Although ReliabilityFirst considered RFC_URE2’s violation history to constitute an aggravating factor, ReliabilityFirst determined that RFC_URE2’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to RFC_URE2’s compliance history. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009917 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-005-3 R3. RFC_URE2 discovered that several of its firewall devices were not configured to alert for all methods of unauthorized administrative access attempts. Instead, they were configured only to alert on a single attack vector (an attack vector is a method or path by which an individual can gain unauthorized access to a system) for unauthorized access, while two such vectors exist. One vector is accessed through the console interactively using the command line, and the other vector is accessed through an internal web server on the firewall. | CIP-005-3 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because the instant violation had the potential to affect the reliable operation of the BPS by providing the opportunity to access RFC_URE2's Electronic Security Perimeter (ESP) while leaving no record of the intrusion. Without having monitoring processes in place at all access points, RFC_URE2 would be unable to detect and alert for unauthorized access to its ESP. Therefore, RFC_URE2 would be unable to prevent or track intrusions that could result in harm to the integrity of Critical Cyber Assets within the ESP. The risk was mitigated because the firewall devices were alerting for unauthorized access attempts. RFC_URE2 installed the monitoring tool on the web service on the firewalls, but it was not configured to alert on authorized access attempts through the other vector. | when the Standard became mandatory and enforceable on RFC_URE2 | when RFC_URE2 enabled the monitoring solution on the firewalls to alert for both types of unauthorized administrative access attempts | $0 (for RFC2012009916 and RFC2012009917) | Self-Report | To mitigate this violation, RFC_URE2: 1) configured the alerting tool to alert upon all possible administrative unauthorized access methods to firewall devices and developed; and 2) performed test cases of firewalls to ensure monitoring and alerting controls were operating as designed. | 2012-11-16 | 2013-01-23 | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE2 promptly reported the due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues. ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for this violation. RFC_URE2 conducts internal audits of selected Reliability Standards. Furthermore, RFC_URE2 encourages its employees to submit any issues they suspect involve compliance with the Reliability Standards. ReliabilityFirst determined that RFC_URE2's previous violation constituted a prior violation and an aggravating factor in the penalty determination. ReliabilityFirst considered that RFC_URE2 discovered the violations through a Self-Reports and applied mitigating credit. Although ReliabilityFirst considered RFC_URE2’s violation history to constitute an aggravating factor, ReliabilityFirst determined that RFC_URE2’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to RFC_URE2’s compliance history. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009885 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-002-1 R3, stating that SERC_URE1 failed to identify all associated Critical Cyber Assets (CCAs) essential to the operation of its Critical Assets. During the physical tour of a control center, the SERC audit team observed frequency monitoring devices that were not accounted for on SERC_URE1’s list of CCAs. The SERC audit team considered the frequency monitoring devices, which use a routable protocol to communicate with the control center, to be critical to SERC_URE1's functional operations and thus should be identified as CCAs. The frequency monitoring devices were located inside a Physical Security Perimeter (PSP) but were outside an Electronic Security Perimeter (ESP). The affected frequency monitoring devices feed the energy management system. SERC determined that SERC_URE1 was in violation of CIP-002-1 R3.2 because it failed to add the affected critical frequency monitoring devices to its list of associated CCAs essential to the operation of a Critical Asset. | CIP-002-1 | R3; R3.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The violation was limited to 4.8% of SERC_URE1's total. Although the frequency monitoring devices were located inside a declared PSP but were outside a declared ESP, the devices were separated from an ESP behind secure firewalls that were protected pursuant to CIP-005 and CIP-007. In addition, SERC_URE1 had multiple frequency sources which would allow it to switch from one frequency source to another. In an emergency situation, SERC_URE1 could access frequency sources at generating plants and substations. There were no incidents at SERC_URE1 facilities related to these CCAs. Furthermore, although SERC_URE1 failed to include the affected devices on its CCA list, SERC determined that SERC_URE1 had completed an annual review of CCA lists and updated as necessary. Additionally, data sources and network equipment associated with these frequency devices were protected within a PSP and the data sources and network equipment was subjected to performance testing of access control, monitoring, logging controls, and had no identified discrepancies. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) upgraded its control system and moved the frequency monitoring devices inside the defined ESP; 2) added the frequency monitoring devices to the CCA list; 3) updated the network drawing to include the frequency monitoring devices inside the defined ESP; and 4) updated all appropriate procedures as required and requested Technical Feasibility Exceptions for the frequency monitoring devices. Any future frequency monitoring devices added to the SERC_URE1 control system, by default, will be added to the CCA list. | 2012-05-30 | 2013-02-22 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009886 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-003-1 R6, stating that SERC_URE1 failed to document a detailed process on change control and configuration management. SERC_URE1 ’s process for change control was to fill out a change log when SERC_URE1 made any changes to Critical Cyber Assets (CCAs). SERC_URE1 ’s change log contained dates, change details, and the names of individuals who completed actions, but did not show any other evidence of controls such as change approvals, action plans for requested change, or testing of changes prior to implementation. SERC_URE1 provided no other evidence to demonstrate that there were any common program components, such as approvals, back-out procedures, and criteria for what constitutes a significant change, which are critical to proper change control and configuration management. SERC determined that SERC_URE1 was in violation of CIP-003-1 R6 because it failed to have a documented process of change control and configuration management for adding, modifying, replacing, or removing CCA hardware or software, and implement supporting configuration management activities to identify, control, and document all SERC_URE1 or vendor-related changes to hardware and software components of CCAs pursuant to the change control process. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to document and follow common change control and configuration management processes could have resulted in changes that were not approved or were deployed without the ability to recover the previous settings for the production system. In addition, SERC_URE1’s violation could have resulted in changes to the system being improperly configured, which could negatively impact other parts of the system. Furthermore, SERC_URE1’s failure to establish a change control and configuration management process could have resulted in the inability to properly test changes prior to implementing them on the production environment. However, the risk to the BPS was mitigated because SERC_URE1 had a change log in place that was used to keep track of changes to its CCAs. In addition, although SERC_URE1 was unable to provide consistent evidence of such communication, SERC_URE1 indicated that it used emails for change approvals. Furthermore, SERC_URE1 enforced the testing of changes through procedural means and conducted testing on a development system that reflects the production environment. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 added a process of change control specific to its CIP-003 procedure document for adding, modifying, replacing, and removing CCAs hardware and software. The basis of change control is the use of forms whereby personnel seeking change must seek prior approval before making any change specific to the requirements of the procedure. The forms (once approved and changes implemented) are scanned and filed appropriately. | 2012-05-29 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009887 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit scheduled. The SERC audit team reported a violation of CIP-005-1 R1, stating that SERC_URE1 had three issues with CIP-005-1 R1. First, SERC_URE1 failed to identify non-critical Cyber Assets pursuant to CIP-005 R1.4 that were included in SERC_URE1 network diagrams. Second, SERC_URE1 failed to install anti-malware on firewall access points pursuant to CIP-005 R1.5. Finally, SERC_URE1 failed to technically enforce password requirements on firewall access points pursuant to CIP-005 R1.5. After reviewing SERC_URE1’s network Electronic Security Perimeter (ESP) diagram, SERC determined that SERC_URE1 failed to identify the following as non-critical Cyber Assets, as required by CIP-005 R1.4: un-managed switches in a private network; network encryption devices used to bridge the control center Physical Security Perimeters; and microwave devices that were located between the encryption devices. SERC_URE1 was unable to provide any other documentation that identified these devices as non-critical Cyber Assets. SERC_URE1 identified CCAs but failed to identify the affected non-critical Cyber Assets. SERC_URE1 removed the network encryption devices and the un-managed switches from operation. SERC also determined that SERC_URE1 failed to install anti-malware on Electronic Access Control and Monitoring (EACM) devices, specifically: firewalls; storage device; switches; and access control server. SERC_URE1 had strong compensatory measures in place in the form of a security control monitoring application that was set up to detect security control modifications and vulnerabilities. Pursuant to Appendix 4D of the NERC Rules of Procedure, however, these devices needed to be covered under a Technical Feasibility Exception (TFE). SERC_URE1 did not file a timely TFE request for these EACM devices. Finally, SERC determined that SERC_URE1 failed to technically enforce local account password requirements, specifically the password complexity requirements, on some of the aforementioned EACM devices. SERC_URE1 attested that the device passwords met the requirements of CIP-007-1 R5 but that technical controls were not in place to enforce the password complexity requirements. SERC_URE1 had procedural controls in place that ensured that the passwords met the complexity requirements of CIP-007-1 R5. Pursuant to Appendix 4D of the NERC Rules of Procedure, however, these devices needed to be covered under a TFE. SERC_URE1 did not file a timely TFE for these EACM devices. SERC determined that SERC_URE1 was in violation of CIP-005 R1.4 and R1.5 because it failed to identify all non-critical Cyber Assets within a defined ESP and failed to afford protective measures to all Cyber Assets used in access control and monitoring, pursuant to CIP-007 R4 and CIP-007 R5. | CIP-005-1 | R1; R1.4; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to identify all non-critical Cyber Assets within the ESP could have led it to fail to implement all the necessary CIP requirements for those Cyber Assets. Such a failure could result in vulnerabilities that allow an attacker to access or compromise systems within the ESP. In addition, SERC_URE1’s failure to install anti-malware on EACM devices could have left its system unable to prevent, deter, or mitigate the introduction, exposure, or propagation of malware. Such malware could cause system failure, denial of access, or compromise the system. Furthermore, SERC_URE1 ’s failure to technically enforce strong password controls on EACM devices could have left its passwords susceptible to online and offline attacks that could allow an attacker to access or compromise systems within the ESP. Without proper account password management, it is possible to introduce unnecessary new accounts and activate old accounts that may allow an attacker to access or compromise a system. However, the risk to the BPS was mitigated because SERC_URE1 had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. SERC_URE1 also had procedural password controls in place. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 : 1) updated its control system by defining ESPs that eliminated the affected non-critical Cyber Assets from the ESPs; 2) performed, prior to the control system upgrade, a review and identified all the EACM devices that were not technically capable of using antivirus/malware prevention tools and implementing the required password protection; 3) submitted TFE Requests for the EACM devices that were not technically capable of using antivirus/malware prevention tools; 4) updated the CCA list and the network drawing; and 5) updated the appropriate change-control documentation. | 2012-11-26 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009888 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-005-1 R2, stating that SERC_URE1 failed to use a deny-by-default model for firewall traffic and failed to enable only ports and services at access points to the Electric Security Perimeter (ESP) that were required for normal and emergency operations. SERC_URE1’s electronic access control documentation indicated that each firewall (access point) shall use a deny access by default configuration, but SERC_URE1’s firewalls had this configuration for inbound traffic only. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.1 because it failed to use deny-by-default rules for outbound traffic at each firewall. SERC_URE1’s detailed cyber vulnerability assessment (CVA) results for one year indicate that there was at least one access point to the ESP that had superfluous ports and services enabled that were not required for emergency and normal operations. The detailed results also indicated that ports and service documentation was not available for several access points. SERC_URE1 was unable to provide evidence supporting the justification of all open ports and services. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.2 because it failed to allow only those ports and services that are required for normal and emergency operations. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.1 and R2.2 because it failed to use mechanisms that were configured to deny access by default and it failed to enable only ports and services that are required for normal and emergency operations. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to restrict ports and services at access points to only those required for operations could increase the attack surface into the ESP and result in access out of the ESP to low trust assets that could be leveraged or compromised. In addition, SERC_URE1’s failure to implement deny-by-default rules for outbound traffic could result in internal compromise or vulnerabilities that propagate inside the ESP without restriction. Furthermore, allowing access out of ESP to a potentially unsecure asset could allow unintended extraction of confidential information. However, the risk to the BPS was mitigated because SERC_URE1 had deny-by-default rules for inbound traffic (coming from outside the ESP). SERC_URE1 also had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs and could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) performed an analysis of the organizational processes, and the technical and procedural mechanisms for controlling electronic access to all electronic access points to the defined ESPs; 2) updated its CIP-005 procedure to better define the deny-by-default rules; 3) limited outbound traffic to only those ports and services required for operations and for monitoring Cyber Assets within the ESP; 4) removed unneeded email and network protocol ports; 5) limited access for the hosts to only those ports and services required for operations and for monitoring Cyber Assets; 6) reviewed its electronic access procedures such that each rule or set of rules was reviewed and comments were added to each existing rule or set of rules. This modified firewall rules document template will require a justification prior to implementing any change to or the modification of firewall rules; and 7) implemented a new change control process, which will add a level of protection to the firewall activity. | 2012-11-27 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009890 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-2c R1, stating that SERC_URE1 failed to ensure that all Cyber Assets within an Electronic Security Perimeter (ESP) resided within an identified Physical Security Perimeter (PSP), and failed to file a Technical Feasibility Exception (TFE) that documented the alternative measures it employed. SERC later determined that this violation extended back to Version 2a of the Standard. SERC determined that SERC_URE1 identified control centers as Critical Assets. SERC_URE1’s primary means of communication between the control centers is to use an encrypted microwave signal. SERC_URE1’s backup means of communication between the control centers is to use a dedicated T1 communication line. SERC_URE1 never considered the microwave devices and the connection between them to be Cyber Assets within an ESP and did not view them as critical. SERC determined that these microwave devices and the connection between them should be considered Cyber Assets. SERC_URE1 did not consider the backup T1 communication line to be a Cyber Asset or an access point. Instead, SERC_URE1 considered the access points to be the firewalls that the T1 communication line was connected to. On July 15, 2010, FERC approved an interpretation of CIP-006-2 R1.1. The interpretation allowed a registered entity to use alternate physical or logical measures to control physical access to Cyber Assets where a six-wall border cannot be established, provided that the registered entity submits a TFE request that details the alternate physical or logical measures that protect the Cyber Assets. SERC_URE1 deployed alternative measures by utilizing encryption devices between the control centers but failed to file a TFE with SERC that documented the alternative measures used to protect the microwave devices and the connection between them. Further, SERC_URE1 did not account for additional pieces of microwave network equipment in the communication path in its SERC_URE1’s ESP documentation (addressed in SERC2012009887). SERC determined that SERC_URE1 was in violation of CIP-006-2a R1.1 because SERC_URE1 failed to file a TFE regarding the deployed and documented alternative measures to control physical access to the Cyber Assets where a six-wall border could not be established. | CIP-006-2a | R1; R1.1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 set up the microwave devices to establish a private connection between the control centers. In addition, SERC_URE1 installed the microwave communication devices inside secure, SERC_URE1-controlled locations with barbed wire fences, cameras, a guard house, and guards. SERC_URE1 also encrypted the microwave data connection. Furthermore, SERC_URE1 had a backup T1 connection in case the microwave communication devices were unavailable. Because of these security measures, an attacker would need a security card authorized to allow physical access to the microwave communication devices in order to gain electronic access to the devices. | 7/15/10 (when SERC_URE1 failed to file a TFE) | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) upgraded its control system by defining separate ESPs at the control centers, thereby eliminating the communication paths from the previously defined ESP and eliminating the need for “alternative protective measures” and a TFE request; 2) placed firewalls at the control center ESP access points and implemented use with the control system upgrade; 3) updated the CCA list and the network drawing; and 4) updated the appropriate change control documentation. | 2012-05-30 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009891 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-1 R1 stating that SERC_URE1 failed to provide evidence that all Cyber Assets used in the access control and monitoring of its Physical Security Perimeters (PSPs) were afforded the protective measures required by CIP-006-1 R1. SERC later determined that SERC_URE1’s physical security procedures failed to adequately address other sub-requirements of CIP-006-1 R1. SERC determined that SERC_URE1 had the following five instances of noncompliance with CIP-006-1 R1: 1) In violation of R1.1, SERC_URE1’s physical security plan contained a process for logging and monitoring the PSP but did not contain a process for the identification of physical access points to the PSP. Access points through each PSP, and measures to control entry to those access points, specifically badge reader controller devices, were not identified on the PSP diagram; 2) In violation of R1.2, SERC_URE1 failed to adequately document that access control panels, which are Cyber Assets within an Electronic Security Perimeter (ESP), also reside within a PSP. SERC_URE1 utilizes Physical Access Control Systems (PACS) to provide access control, monitoring, and logging of its PSPs. SERC_URE1’s PACS devices consist of a virtual server hosted outside of the ESP on a network segregated from the corporate network, and access control panels, which connect to the corporate network. Although SERC_URE1 stated that the panels reside within a PSP, upon review of a control system IP network diagram, SERC determined that the panels are located outside of the PSP, without the protection of six-wall boundaries; 3) In violation of R1.8, SERC_URE1 failed to document testing results for significant changes made to PACS devices as required by CIP-007-1 R1.3. SERC_URE1 was unable to provide any evidence of testing of significant changes to PACS devices. SERC_URE1 has a separate violation of CIP-007-1 R1 that is being addressed in NERC Violation ID SERC2012009893; 4) In violation of R1.8, SERC_URE1’s security patching process did not address security patch management for PACS devices and SERC_URE1 did not provide any evidence of the review and testing of security patches for PACS devices as required by CIP-007-1 R3. SERC_URE1 uses a third-party to monitor for security patches and has a formal process for the testing of security patches for Critical Cyber Assets (CCAs) and Cyber Assets located in an ESP, but this process did not address security patch management for PACS devices; and 5) In violation of R1.8, SERC_URE1 failed to account for PACS devices in its asset disposal and redeployment documentation as required by CIP-007-1 R7. SERC_URE1 had a policy in place that calls for wiping devices but did not address PACS devices specifically and did not provide enough detail to properly address disposal and redeployment of virtual PACS servers. SERC_URE1 has a separate violation of CIP-007-1 R7 that is being addressed in NERC Violation ID SERC2012009895. SERC determined that SERC_URE1 was in violation of CIP-006-1 R1 because it failed to provide all Cyber Assets used in the access control and monitoring of the PSPs the protective measures required by the Standard. | CIP-006-1 | R1; R1.1.; R1.2; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to have a physical security plan that identifies physical access points to the PSP could result in missed devices that are not accounted for, managed, monitored, or not protected pursuant to CIP-006-1 R1.8. If SERC_URE1 failed to afford PACS devices or logging systems the measures listed in CIP-006-1 R1.8, unauthorized individuals could gain access to these Cyber Assets, which could result in unauthorized physical and logical access to the PSP or the suppression of PSP monitoring. This could, in turn, allow unauthorized individuals to gain access to CCAs. However, the risk to the BPS was mitigated because the access control panels were located inside a secured SERC_URE1 facility with limited physical access. In addition, SERC_URE1 monitors physical access using security guards and cameras. Furthermore, SERC_URE1 limits electronic access to authorized badge holders. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) reviewed its physical security plan and associated procedures as they relate to R1.8 and determined the need for modifications to the physical security plan regarding PACS devices; 2) drafted a table in the physical security plan that lists the location, associated PSP, and a description of the identified access point, such as doors and windows; 3) established diagramming and vector graphics application drawings as a basis for reviewing and inventorying SERC_URE1’s PSPs, access points, and control mechanisms. The procedure requires a reconciliation of the drawings and table to ensure accuracy of SERC_URE1’s process for identifying access points to the PSPs at least annually; 4) conducted a review and reconciliation of SERC_URE1’s PSPs and validated the PSPs to be accurate; and 5) updated its physical security plan to better document and ensure protection is afforded as required by R1.8. Specifically, SERC_URE1 added a table that lists all Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s), their physical location, and the PSP in which they reside. Therefore, SERC_URE1's subject matter expert will have clear knowledge of the devices applicable to this requirement. | 2012-11-26 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009892 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-1 R3, stating that SERC_URE1 failed to implement the technical controls for monitoring physical access at a single access point to a Physical Security Perimeter (PSP). During the physical tour of a control center, the SERC audit team simulated forcing open a secondary access door to the PSP and found that no alarm was generated or received. Upon further investigation, SERC_URE1 determined that the tested secondary access door was not configured to be monitored for “forced door” access attempts. SERC_URE1 provided screenshots of the device configuration before and after the SERC audit team discovered the violation. The screenshots show that the monitoring device configuration was not monitoring for forced open entries prior to the issue’s discovery. Upon discovery, SERC_URE1 immediately corrected the violation and SERC_URE1 provided evidence showing the corrected configuration after the issue was identified and corrected. SERC_URE1 also provided logs from the monitoring device in question, dated before and after the issue was corrected, which show that the device was correctly generating alarms for other security events. This failure occurred at a single PSP entrance into the control center which is manned 24 hours a day, seven days a week. SERC determined that SERC_URE1 was in violation of CIP-006 R3.1 because a single monitoring system failed to indicate when a door had been opened without authorization and consequently failed to alert SERC_URE1 personnel. | CIP-006-1 | R3; R3.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP access door utilizes a magnetic lock instead of a traditional door strike that would require hundreds of pounds of force to force open the door, unless the door was released by the physical access control system or power to the access system and backup batteries was disrupted. The control center is manned 24 hours a day, seven days a week, and the access door is an internal door that requires passing through several other security controlled doors to reach. SERC_URE1 personnel within the facility are required to display a badge with their name and picture and visitors are escorted at all times. SERC_URE1 had no other PSP access points that failed to alarm or alert. Finally, the device was correctly generating alarms for other security events. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 reconfigured the door to send alerts upon forced-door events. | 2012-03-01 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009893 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R1, stating that SERC_URE1 failed to document test results for multiple significant changes. SERC reviewed SERC_URE1’s process for testing significant changes and SERC_URE1’s change control log. SERC determined that the SERC_URE1 process for testing significant changes did not address third-party software or firmware and SERC_URE1 could not provide evidence of testing for all significant changes to existing and new Cyber Assets. SERC_URE1 delegated the testing responsibility to a third-party on a system that reflects the production environment prior to implementation on production servers, except for patches on servers that are connected to the corporate local area network (LAN). For patches on servers that are connected to the corporate LAN, the third-party tested patches on corporate servers prior to implementation on production servers. SERC determined that SERC_URE1’s process for testing significant changes did not specifically address third-party software or firmware. The SERC_URE1 change log contains records of all significant changes made to Cyber Assets located inside an Electronic Security Perimeter (ESP), but does not indicate the completed testing of such changes. SERC_URE1 claims that testing communication and requests were conducted via email and the correspondence for some tests were lost. SERC_URE1 primarily relies on the third-party to test significant changes prior to implementation on production. SERC determined that SERC_URE1 failed to provide sufficient evidence to conclude that testing was being completed consistently and successfully for all significant changes prior to implementation on the production environment. SERC determined that SERC_URE1 was in violation of CIP-007 R1 because it failed to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the ESP do not adversely affect existing cybersecurity controls. | CIP-007-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to test changes prior to implementation on a production environment could compromise the functionality of Critical Cyber Assets that reside on the production system. In addition, SERC_URE1’s failure to address all significant changes, including to third-party software and firmware, increases the probability that vulnerabilities could be introduced. SERC_URE1’s failure to maintain test results could leave SERC_URE1 unable to maintain accurate audit trails, and unable to identify significant test errors. Furthermore, SERC_URE1’s failure to document test results could leave SERC_URE1 unable to research a cybersecurity incident and unable to mitigate vulnerabilities quickly and efficiently. However, the risk to the BPS was mitigated because SERC_URE1 had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. In addition, SERC_URE1 indicated that testing communication and requests were conducted via email and the correspondence for some tests were lost. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) performed an analysis of its testing procedures for significant changes; and 2) modified its CIP-007 procedure to address the weak documentation process for recording test results. Specifically, the procedure discusses how SERC_URE1’s change control procedure creates workflow that will properly document test results associated with significant changes. SERC_URE1’s new change control process utilizes approval forms whereby personnel seeking to make any change to a Cyber Asset within the defined ESP must seek approval from their manager or the group’s director. The forms utilize three levels whereby "level three" strictly relates to significant changes and can only be approved by the manager or group’s director when accompanied by an associated test record. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009894 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R5, stating that SERC_URE1 had two issues with the Standard. The SERC audit team stated that: 1) SERC_URE1 implemented a shared account on a Cyber Asset located inside the Electronic Security Perimeter (ESP) that was not authorized, nor required and 2) SERC_URE1 failed to technically enforce password requirements on a single device in the control center. SERC later found an additional violation of CIP-007-1 R5 in which SERC_URE1 failed to remove default accounts on Cyber Assets located within an ESP. SERC reviewed SERC_URE1’s account management procedure and determined that SERC_URE1 had a policy in place for account management but it only addressed shared accounts and failed to specifically address administrator, shared, and other generic account privileges, including factory default accounts, as required by R5.2. In addition, SERC_URE1 failed to follow its established procedures after restoring a device that was located inside the ESP to an earlier date. SERC_URE1’s failure to follow its procedures resurrected an unnecessary shared account. The SERC audit team discovered this unnecessary shared account while onsite. SERC determined that SERC_URE1 violated CIP-007-1 R5.2 because it failed to address administrator, shared, and other generic account privileges, including factory default accounts, in its account management procedure, and failed to follow its account management procedure while restoring a device to an earlier date, which resurrected an unnecessary shared account. SERC_URE1 also had communication devices and servers that were not capable of technically enforcing password requirements and were not covered under a Technical Feasibility Exception (TFE). SERC determined that SERC_URE1 violated CIP-007-1 R5.3 because it had communication devices and services that were not capable of technically enforcing password requirements and did not file a TFE request documenting the compensating measures. In addition to the audit findings, SERC discovered that SERC_URE1 failed to remove default accounts on Cyber Assets located inside an ESP while reviewing SERC_URE1’s cyber vulnerability assessment (CVA) for one year (as discussed in more detail in SERC201209896). The 2010 CVA identified CCAs located within the ESP that were configured with default accounts. These devices were incorrectly identified by the third-party in the CVA as CCAs, when in fact they were non-critical Cyber Assets within an ESP, and SERC_URE1 immediately removed the default accounts upon discovery. SERC_URE1 removed these Cyber Assets from the ESP with the installation of new firewalls, which excluded the Cyber Assets from the new ESP. This violation was not self-reported by SERC_URE1 and the following year's CVA does not indicate any issues with these Cyber Assets or any default accounts. SERC determined that SERC_URE1 violated CIP-007-1 R5.2.1 because it failed to remove default accounts on Cyber Assets within an ESP. SERC determined that SERC_URE1 was in violation of CIP-007-1 R5 because it: 1) failed to implement a policy to minimize and manage the scope and acceptable use of administrator and other generic account privileges including factory default accounts; 2) had an unauthorized and unnecessary shared account on a single asset located inside an ESP without submitting a TFE; 3) had communication devices and services that were not capable of enforcing password requirements and did not file a TFE request documenting the compensating measures; and 4) had 19 the affected Cyber Assets located in an ESP that were configured with default accounts without submitting TFEs. | CIP-007-1 | R5; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to develop and implement a policy that directly addresses the acceptable use of multiple account types could result in the misuse of unaddressed account types and leave them unprotected in a manner that could lead to internal or external compromise. SERC_URE1’s failure to use proper account management could lead to the introduction of unnecessary new accounts and the activation of old accounts that could allow an attacker to access or compromise a system. In addition, SERC_URE1’s failure to use strong password controls could leave passwords susceptible to online and offline attacks that could allow an attacker to access or compromise a system. Furthermore, SERC_URE1’s failure to remove default accounts on the affected Cyber Assets located in an ESP could allow an attacker to access or compromise a system. However, the risk to the BPS was mitigated because SERC_URE1 had procedural password controls in place to ensure compliance with the CIP password requirements as a compensating measure for the lack of technical password controls. SERC_URE1 also had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) removed the shared account; 2) decommissioned the test system as required by SERC_URE1’s disposal and redeployment procedure and removed it from the defined ESP; 3) assured that a mechanism for a task review was integrated into the change control process. Therefore, a task similar to that which caused this violation must now be accompanied by a documented job description and review prior to implementing the task on applicable Cyber Assets; 4) performed a thorough review of all Cyber Assets residing in the defined ESPs to determine all applicable devices as they related to necessary TFE request(s); and 5) submitted TFE requests for the affected devices. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009895 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007 R7, stating that SERC_URE1 failed to have adequately documented formal processes and methods for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter (ESP). The process documents did not contain adequate details for the proper erasure of data storage media, and for the disposal or redeployment of Cyber Assets within the ESPs. SERC reviewed the disposal and redeployment process in place at the time of the Compliance Audit and determined that the process was used by all of SERC_URE1's registered functions for all disposal and redeployments of Cyber Assets located within an ESP. SERC determined that the process in place did not adequately address the erasure of data storage media for non-network Cyber Assets within ESPs (e.g., servers and workstations) in regards to decommissioning and redeployment. SERC_URE1’s process for the erasure of media for network Cyber Assets within ESPs (e.g., firewalls, routers, and switches) provided clear detail on how to erase the data storage media. SERC reviewed decommissioned and redeployment records provided by SERC_URE1. Despite SERC_URE1’s inadequate disposal and redeployment process, SERC determined that SERC_URE1’s disposal records were in accordance with SERC_URE1’s documented procedures and demonstrated that SERC_URE1 had properly erased the data storage media upon decommissioning and redeployment of Cyber Assets within the ESP. SERC also determined that SERC_URE1 followed its established process for the disposal and redeployment of Cyber Assets within the ESP, had adequate decommissioning and redeployment evidence, and had the ability to verbally communicate the process. SERC determined that SERC_URE1 was in violation of CIP-007-1 R7 because it did not adequately document its disposal and redeployment process for handling the erasure of data storage media when decommissioning or redeploying non-network Cyber Assets located within an ESP. | CIP-007-1 | R7 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had a written process for handling the decommissioning and redeployment of Critical Cyber Assets and Cyber Assets located inside of an ESP. SERC_URE1 also consistently erased data storage media on redeployed or decommissioned Cyber Assets and maintained records of that erasure. Furthermore, SERC_URE1 was able to verbally describe the process, methods, and tools it used to erase data storage media on redeployed or decommissioned Cyber Assets. Lastly, this was a documentation only issue. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) updated its disposal and redeployment procedure to include more formal definition of “wiping” as it applies and is related to each type or category of Cyber Assets that reside in SERC_URE1’s defined ESPs; and 2) updated its change control procedure to provide more adequate tracking of specific data concerning “who, what, when, and where” regarding each disposal or redeployment event. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009896 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R8.2, stating that SERC_URE1 failed to verify that only ports and services required for the operation of the Cyber Assets within the Electronic Security Perimeter (ESP) were enabled in one year's cyber vulnerability assessment (CVA). SERC_URE1 contracted with a third-party for three year's CVAs. SERC_URE1’s first year's CVA report recommended that SERC_URE1 review its ports and services to identify and disable ports that were not needed for emergency or normal operations. SERC_URE1’s second year's CVA report indicated that documentation on ports and services was not adequate in several instances and the third-party conducting the CVA found it impossible to determine if a particular port was actually required for operation. SERC_URE1’s third year's CVA report indicated that SERC_URE1 did not provide sufficient documentation and justification of its enabled and disabled ports and services to allow the third party conducting the CVA to complete its review of SERC_URE1’s ports and services pursuant to SERC_URE1’s established process. The third-party completed all the other sub-requirements of CIP-007-1 R8 for the third year's CVA. SERC determined that SERC_URE1 was in violation of CIP-007-1 R8.2 because it failed to complete a review to verify that only ports and services required for normal and emergency operation of the Cyber Assets within the ESP were enabled. | CIP-007-1 | R8; R8.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1's failure to meet all the requirements of CIP-007-1 R8 when conducting its three year's CVAs, specifically reviewing ports and services, could have left Cyber Assets residing within the ESP open to potential security threats and compromise for an extended period of time. However, the risk to the BPS was mitigated because SERC_URE1 completed all the other sub-requirements of CIP-007 R8 for the third year's CVA and did not discover any other vulnerabilities. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) conducted a review of its procedures for CVAs; and 2) updated its CVA procedure to include control mechanisms for ensuring that all CVA tasks are performed as required and documented in the statement of work. Specifically, SERC_URE1’s compliance staff will facilitate the process to create more oversight and ensure all aspects of the statement of work are complete; and 3) required compliance staff, after the final report was distributed, to participate in the review of the report and assist in the development of plans to mitigate any identified vulnerabilities. | 2012-12-12 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.